|  | # EPR Compliance Assessment Report |  |  |  |  |  | Report ID: 05899 |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| This form will report compliance with your permit as determined by an NRW officer |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Site | Dragon LNG |  |  |  |  | Permit Ref |  |  | AP3136UA |  |  |  |  |  |
| Operator/ Permit holder | Dragon LNG |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date | 1st October 2015 |  |  |  |  | Time in |  |  | 10:00 |  |  | Out | 14:00 |  |
| What parts of the permit were assessed | Q1 and Q2 2015 Unauthorised Releases |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Assessment | Choose an item. | EPR Activity: | Installation | X |  |  | Waste Op |  |  | Water Discharge |  |  |  |  |
| Recipient’s name/position | Paul Howells, Balachander Veerasamy |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Officer’s name | Gary Evans |  |  |  | Date issued |  |  |  |  |  | 26th October 2015 |  |  |  |

| Section 1 - Compliance Assessment Summary |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| This is based on the requirements of the permit under the Environmental Permitting Regulations. A detailed explanation and any action you may need to take are given in the “Detailed Assessment of Compliance” (section 3). This summary details where we believe any non-compliance with the permit has occurred, the relevant condition and how the non-compliance has been categorised using our Compliance Classification Scheme (CCS). CCS scores can be consolidated or suspended, where appropriate, to reflect the impact of some non-compliances more accurately. For more details of our CCS scheme, contact your local office. |  |  |  |  |  |  |  |
| Permit Conditions and Compliance Summary |  |  |  |  |  | Condition(s) breached |  |
| a) Permitted activities | 1. Specified by permit |  | A |  |  |  |  |
| b) Infrastructure | 1. Engineering for prevention & control of pollution |  | A |  |  |  |  |
|  | 2. Closure & decommissioning |  | N |  |  |  |  |
|  | 3. Site drainage engineering (clean & foul) |  | N |  |  |  |  |
|  | 4. Containment of stored materials |  | N |  |  |  |  |
|  | 5. Plant and equipment |  | N |  |  |  |  |
| c) General management | 1. Staff competency/ training |  | N |  |  |  |  |
|  | 2. Management system & operating procedures |  | N |  |  |  |  |
|  | 3. Materials acceptance |  | NA |  |  |  |  |
|  | 4. Storage handling, labelling, segregation |  | NA |  |  |  |  |
| d) Incident management | 1. Site security |  | N |  |  |  |  |
|  | 2. Accident, emergency & incident planning |  | N |  |  |  |  |
| e) Emissions | 1. Air |  | C3 |  |  | 6.1.2 (3) |  |
|  | 2. Land & Groundwater |  | NA |  |  |  |  |
|  | 3. Surface water |  | C3 |  |  | 7.1.2 (1) |  |
|  | 4. Sewer |  | NA |  |  |  |  |
|  | 5. Waste |  | NA |  |  |  |  |
| f) Amenity | 1. Odour |  | NA |  |  |  |  |
|  | 2. Noise |  | A |  |  |  |  |
|  | 3. Dust/fibres/particulates |  | NA |  |  |  |  |
|  | 4. Pests, birds & scavengers |  | NA |  |  |  |  |
|  | 5. Deposits on road |  | NA |  |  |  |  |
| g) Monitoring and records, maintenance and reporting | 1. Monitoring of emissions & environment |  | A |  |  |  |  |
|  | 2. Records of activity, site diary, journal & events |  | A |  |  |  |  |
|  | 3. Maintenance records |  | N |  |  |  |  |
|  | 4. Reporting & notification |  | N |  |  |  |  |
| h) Resource efficiency | 1. Efficient use of raw materials |  | N |  |  |  |  |
|  | 2. Energy |  | N |  |  |  |  |
| KEY: C1, C2, C3, C4 = CCS breach category ( * suspended scores are marked with an asterisk), A = Assessed or assessed in part (no evidence of non-compliance), N = Not assessed, NA = Not Applicable |  |  |  |  |  |  |  |
| Number of breaches recorded |  | 4 |  | Total compliance score (see section 5 for scoring scheme) |  |  | 12 |

If the Total No Breaches is greater than zero, then please see Section 3 for details of our proposed enforcement response

| Section 2 – Compliance Assessment Report Detail |  |
| --- | --- |
| This section contains a report of our findings and will usually include information on: |  |
| - the part(s) of the permit that were assessed (e.g. maintenance, training, combustion plant, etc) - where the type of assessment was ‘Data Review’ details of the report/results triggering the assessment - any non-compliances identified - any non-compliances with directly applicable legislation - details of any multiple non-compliances | - information on the compliance score accrued inc. details of suspended or consolidated scores. - details of advice given - any other areas of concern - all actions requested - any examples of good practice. - a reference to photos taken |

Unauthorised Releases Permit No.; Inspector; Company Report Number; Location of Emission; Report; Compliance. AP3136UA; GE; DLNG 07-04-15; A8; Nox - Two breaches occurred on 02/04/15; 12:00-06:00 and 18:00-19:00. The maximum hourly mean between 12:00:00-06:00 was 193.62 and the maximum hourly mean between 18:00-19:00 was 219.19 (Limit 86mg/nm3); CCS3 241930. AP3136UA; GE; DLNG 28-04-15; A8/SCV1; Nox - The daily averages on 05/03/15 and 06/03/15 were in breach of th emission limit value. The figures were 95.41 and 94.42 respectively against a limit of 86 mg/nm3; CCS3 241931. AP3136UA; GE; DLNG 05-05-15; E3 Firewater reservoir; pH limit - The average spot sample result of pH was 9.4 and the total estimate of the overflow for the reporting period from 1st April to 30th April was 54.32m3; CCS3 241933. AP3136UA; GE; DLNG 17-06-15; A1 - Main Stack; CO Limit - 100mg/Nm3. Measured value was 234.96mg/Nm3; CCS3 241934. Dragon LNG have notified 4 Unauthorised Releases in accordance with their permit under Schedule 5. Noise Update Dragon LNG provided an update to the existing noise management plan, which will potentially be extended to December 2015. The company have completed a number of the noise reduction measures with a planned review following the completion of the work. Since installation of the improvements, the company have only received one noise complaint which was attributed to a pressure relief valve. NRW have not received any further complaints in regards to noise from the facility, however the company need to complete the improvements and submit a review in the coming months detailing the progress made, in line with BAT. Water Discharge The company have installed numerous floating balls on the fire water pond (final discharge point) to reduce algal growth within the pond during the warmer months. The project is complete, and was completed at the end of June 2015. The main aim of the changes is to reduce the breaches of pH at the final discharge. The project has been delayed due to supply problems, however the change should be beneficial in reducing the permit breaches. Potential Emergency Flaring Operations Dragon LNG carried out essential maintenance on site during September 2015, over a 10 day period which resulted in emergency flaring. The company have reviewed a range of alternative options, however due to difficulties over gas quality control and valve configurations the flaring option is the safer option compare with any direct release of natural gas. The company will be proactive with their communication to the local residents and other interested parties (Local Authority and NRW) on the times and duration of the maintenance programme. Regulation 60 Notice LCP Variation The company have collated information in response to the Notice, however there has subsequently been a further request for information to clarify certain aspects of the operation. NRW will be subsequently reviewing the submitted data to enable a permit review in line with IED LCP requirements. Variation Application The company have submitted a variation application to install a re liquefaction plant, including some minor modifications in relation to surface water discharges.

|  | # EPR Compliance Assessment Report |  | Report ID: 05899 |  |
| --- | --- | --- | --- | --- |
| This form will report non-compliance with your permit as determined by an NRW officer |  |  |  |  |
| Site | Dragon LNG | Permit |  | AP3136UA |
| Operator/ Permit | Dragon LNG | Date |  | 26th October 2015 |

| Section 3- Enforcement Response | Only one of the boxes below should be ticked |  |
| --- | --- | --- |
| You must take immediate action to rectify any non-compliance and prevent repetition. Non-compliance with your permit conditions constitutes an offence and can result in criminal prosecutions and/or suspension or revocation of a permit. Please read the detailed assessment in Section 2 and the steps you need to take in Section 4 below. |  |  |
| Other than the provision of advice and guidance, at present we do not intend to take further enforcement action in respect of the non-compliance identified above. This does not preclude us from taking enforcement action if further relevant information comes to light or advice isn’t followed. |  | X |
| In respect of the above non-compliance you have been issued with a warning. At present we do not intend to take further enforcement action. This does not preclude us from taking additional enforcement action if further relevant information comes to light or offences continue. |  |  |
| We will now consider what enforcement action is appropriate and notify you, referencing this form. |  |  |

| Section 4- Action(s) |  |  |  |
| --- | --- | --- | --- |
| Where a non - compliance has been detected and an enforcement response has been selected above, this section summarises the steps you need to take to return to compliance and also provides timescales for this to be done. |  |  |  |
| Criteria Ref. | CCS Category | Action Required/Advised | Due Date |
| See Section 1 above |  |  |  |
| 6.1.2 | C3 | Improve operations | On going |
| 7.1.2 | C3 | Improve operations – complete installation of Cover on Fire Water Pond | Dec 2015 |

| Section 5 - Compliance notes for the Operator |  |  |  | Section 6 – General Information |
| --- | --- | --- | --- | --- |
| To ensure you correct actual or potential non-compliance we may advise on corrective actions verbally or in writing require you to take specific actions in writing issue a notice require you to review your procedures or management system change some of the conditions of your permit decide to undertake a full review of your permit |  |  |  | Data protection notice The information on this form will be processed by Natural Resources Wales (NRW) to fulfill its regulatory and monitoring functions and to maintain the relevant public register(s). NRW may also use and/or disclose it in connection with: offering/providing you with its literature/services relating to environmental matters consulting with the public, public bodies and other organisations (e.g. Health and Safety Executive, local authorities) on environmental issues carrying out statistical analysis, research and development on environmental issues providing public register information to enquirers investigating possible breaches of environmental law and taking any resulting action preventing breaches of environmental law assessing customer service satisfaction and improving its service Freedom of Information Act/Environmental Information Regulations request. NRW may pass it on to its agents/representatives to do these things on its behalf. You should ensure that any persons named on this form are informed of the contents of this data protection notice. |
| Any breach of a permit condition is an offence and we may take legal action against you. We will normally provide advice and guidance to assist you to come back into compliance either after an offence is committed or where we consider that an offence is likely to be committed. This is without prejudice to any other enforcement response that we consider may be required. Enforcement action can include the issue of a formal caution, prosecution, the service of a notice and or suspension or revocation of the permit. See our Enforcement and Civil Sanctions guidance for further information |  |  |  |  |
| This report does not relieve the site operator of the responsibility to ensure you comply with the conditions of the permit at all times and prevent pollution of the environment ensure you comply with other legislative provisions which may apply. |  |  |  |  |
| Non-compliance scores and categories |  |  |  | Disclosure of information NRW will provide a copy of this report to the public register(s). However, if you consider that any information contained in this report should not be released to the public register(s) on the grounds of commercial confidentiality, you must write to your local area office within twenty working days of receipt of this form indicating which information it concerns and why it should not be released, giving your reasons in full. |
| CCS category | Description | Score |  |  |
| C1 | A non-compliance which could have a major environmental effect | 60 |  |  |
| C2 | A non-compliance which could have a significant environmental effect | 31 |  |  |
| C3 | A non-compliance which could have a minor environmental effect | 4 |  | Customer charter What can I do if I disagree with this compliance assessment report? If you are unable to resolve the issue with your site officer, you should firstly discuss the matter with the officer’s line managers. If you wish to raise your dispute further through our official Complaints and Commendations procedure, phone our general enquiry number 0300 065 3000 (Mon to Fri 08.00–18.00) and ask for the Customer Contact team or send an email to enquiries@naturalresourceswales.gov.uk If you are still dissatisfied you can make a complaint to the Public Services Ombudsman for Wales. For advice on how to complain to the Ombudsman phone their helpline on (0845) 601 0987. |
| C4 | A non-compliance which has no potential environmental effect | 0.1 |  |  |
| Operational Risk Appraisal (Opra) - Compliance assessment findings may affect your Opra score and/or your charges. This score influences the resource we use to assess permit compliance. |  |  |  |  |