## Plant & Hours Operation
Large Combustion Plant - within scope of the LCP BREF
LCP Number | Plant type | Fuel | Proposed Operating Hours
LCP15 | 9H Combined Cycle | Natural Gas | >1500 hours
| LM2500 Combined Cycle | Natural Gas | <1500 hours
LM2500 Open Cycle
| Auxiliary Boiler | Natural Gas | As per the Environmental Permit (EPR/BJ7891IT)
Combustion Plant <50MWth - Out of Scope of the LCP BREF for Data Gathering Purposes
Plant Type | Fuel | Use
Safe Shut-down Diesel Generator: Designed for infrequent use to maintain essential supplies in the event of total site power loss. | Diesel Fuel Oil | The current Environmental Permit contains no associated emission limit values or reporting requirements. Each unit is tested routinely for reliability, with estimated run times between 20 to 50 hours per annum per unit.
LM2500 Start-up Diesel Generator: Designed to allow LM2500 start-up in black-start mode in the event of total site power loss. | Diesel Fuel Oil
Pipeline Reception Facility (PRF) Back-Up Diesel Generator: Designed to maintain essential supplies to the PRF in the event of total site power loss. | Diesel Fuel Oil
Diesel Fire-Fighting Pump For use in emergency fire-fighting situations. | Diesel Fuel Oil

## BAT Conclusions
Permit number: EPR/BJ7891IT |  | Operator: Baglan Operations Limited | Facility name: Baglan Bay Power Station (Baglan Energy Park)
This table should be read and used to make reference to your Regulation 61 submission. Reference will need to be made to BAT Conclusions for Large Combustion Plants published on the 17th August 2017 and the supporting interpretation document (date and version). You should also note the specific considerations you may need to consider when making responses to the Regulation 61 notice.
| LCP BREF BAT conclusions decision: | http://eur-lex.europa.eu/legal-content/EN/TXT/?qid=1503383091262&uri=CELEX:32017D1442
| Full LCP BREF document including BAT conclusions: | http://eippcb.jrc.ec.europa.eu/reference/BREF/LCP/JRC107769_LCP_bref2017.pdf
BAT No. | Topic | Brief Description | BAT | Applicable BAT - AEL | Specific considerations for the Regulation 61 response | Operating to BAT? | BAT-AEL derogation needed? | Provide reference to the section in the Regulation 61 Response demonstrating how compliance with BAT is met or confirmation of action that will be taken to ensure compliance with BAT by 17/08/2021
General BAT Conclusions
1 | EMS | Improve overall performance | Implement and adhere to an EMS that incorporates key features identified |  |  | Yes - compliant now |  | Please see Table 3.1 in the Report ('LCP Regulation 61 Environmental Permit Review: Baglan Bay')
2 | Efficiency | Determine net electrical efficiency and/or net total fuel utilisation and/or net mechanical efficiency | Carry out a performance test at full load. |  |  | Yes - compliant now |  | Please see Table 3.1 in the Report ('LCP Regulation 61 Environmental Permit Review: Baglan Bay')
3 | Monitoring of process parameters | Monitor key process parameters for emissions to air and water specified in the corresponding table. | Monitoring of specified process parameters. |  |  | Yes - compliant now |  | Please see Table 3.1 in the Report ('LCP Regulation 61 Environmental Permit Review: Baglan Bay')
4 | Monitoring of emissions to air | Monitor emissions to air with at least the frequency in the corresponding table and in accordance with the EN standards. | Monitor emissions to air with at least the frequency in the corresponding table and in accordance with the EN standards. |  | Information on monthly mercury (Hg), chlorine (Cl) and fluorine (F) content in fuels required if seeking to use provisions in relation to "sufficiently stable emission levels". | Yes - compliant now |  | Please see Table 3.1 in the Report ('LCP Regulation 61 Environmental Permit Review: Baglan Bay')
5 | Monitoring of emissions to water from flue-gas treatment | Monitor emissions to water with at least the frequency in the corresponding table and in accordance with the EN standards. | Monitor emissions to water with at least the frequency in the corresponding table and in accordance with the EN standards. |  |  |  |  | Not Applicable. No flue gas treatment systems are required / installed.
6 | Environmental performance | Improve general environmental performance | A variety of techniques |  |  | Yes - compliant now |  | Please see Table 3.1 in the Report ('LCP Regulation 61 Environmental Permit Review: Baglan Bay')
7 | Reduce emissions of ammonia to air | Reduction of ammonia emissions where SCR or SNCR is used. | BAT is to optimise the design and/or operation and to meet associated AELs. | Not Applicable |  |  |  | Not Applicable. No SCR / SNCR is required / installed.
8 | Prevent or reduce emissions to air | Prevent or reduce emissions to air during normal operating conditions. | Ensure, by appropriate design, operation and maintenance, that the emission abatement systems are used at optimal capacity and availability. |  |  |  |  | Not Applicable. All emissions to air are controlled at source, and no emissions abatement systems are required / installed.
9 | Environmental performance and reduce emissions to air | Inclusion of a number of elements in the quality assurance/quality control programmes for all the fuels used, as part of the EMS. | Techniques (i), (ii) and (iii). |  |  |  |  | Not Applicable. The characteristics and quality of natural gas is controlled by National Grid, through the National Gas Transmission System (and therefore at a national level). As such, the quality and characteristics of natural gas arriving at the Baglan Bay site is within agreed tolerances. As such, no specific fuel quality assurance / fuel quality control programme is required. Nevertheless, a system is in place to monitor certain characteristics of the natural gas for use in overall performance monitoring.
10 | Reduce emissions to air and/or water | Prevent or reduce emissions to air during other than normal operating conditions (OTNOC). | A variety of techniques. |  |  | Yes - compliant now |  | Please see Table 3.1 in the Report ('LCP Regulation 61 Environmental Permit Review: Baglan Bay')
11 | Monitoring of emissions to air and/or to water | Monitoring of emissions to air and/or to water during OTNOC. | Appropriately monitor emissions to air and/or to water during OTNOC. |  |  | Yes - compliant now |  | Please see Table 3.1 in the Report ('LCP Regulation 61 Environmental Permit Review: Baglan Bay')
12 | Energy efficiency | Increase the energy efficiency for units operated ≥1500 h/yr | A variety of techniques |  |  | Yes - compliant now |  | Not Applicable to the LM2500 or the Auxiliary Boiler. For informationon the 9H, please see Table 3.1 in the Report ('LCP Regulation 61 Environmental Permit Review: Baglan Bay')
13 | Reduce water usage and the volume of contaminated waste water discharged | Reduce water usage and the volume of contaminated waste water discharged | Use of one or both of the techniques specified in the associated table. |  |  |  |  | Not Applicable. For (a) water recycling: Due to the quality requirements and water balance of the plant, Baglan Bay does not include water recycling. However, Baglan Bay does implement a number of water efficiency measures to reduce water usage. For (b) dry bottom ash handling: noted to be applicable to combustion of solid fuels.
14 | Prevent contaminated of uncontaminated waste water and to reduce emissions to water | Prevent contaminated of uncontaminated waste water and to reduce emissions to water | Segregate waste water streams and to treat them separately, depending on the pollutant content. |  |  | Yes - compliant now |  | Please see Table 3.1 in the Report ('LCP Regulation 61 Environmental Permit Review: Baglan Bay')
15 | Reduce emissions to water | Reduce emissions to water from flue-gas treatment | A variety of techniques | Not Applicable |  |  |  | Not Applicable.
16 | Reduce waste sent for disposal | To reduce the quantity of waste sent for disposal | A variety of techniques |  |  | Yes - compliant now |  | Please see Table 3.1 in the Report ('LCP Regulation 61 Environmental Permit Review: Baglan Bay')
17 | Reduce noise emissions | To reduce noise emissions | A variety of techniques |  |  | Yes - compliant now |  | Please see Table 3.1 in the Report ('LCP Regulation 61 Environmental Permit Review: Baglan Bay')
Combustion of Solid Fuels (Coal and/or Lignite)
18 | Environmental performance | Improve overall performance | Techniques in associated table. |  |  |  |  | Not Applicable
19 | Efficiency | Increase efficiency | Techniques in associated table. | Not Applicable |  |  |  | Not Applicable
20 | Prevent or reduce emissions of NOx | Prevent or reduce emissions of NOx emissions to air while limiting CO and N2O emissions to air from the combustion of coal and/or lignite. | A variety of techniques and associated AELs | Not Applicable |  |  |  | Not Applicable
21 | Prevent or reduce emissions of SOx, HCl and HF | Prevent or reduce emissions of SOx, HCl and HF emissions to air from the combustion of coal and/or lignite. | A variety of techniques and associated AELs | Not Applicable |  |  |  | Not Applicable
22 | Reduce dust and particulate-bound metal emissions | Reduce emissions of dust and particulate-bound metal emissions to air from the combustion of coal and/or lignite. | A variety of techniques and associated AELs | Not Applicable |  |  |  | Not Applicable
23 | Prevent or reduce emissions of mercury | Prevent or reduce emissions of mercury emissions to air from the combustion of coal and/or lignite. | A variety of techniques and associated AELs | Not Applicable |  |  |  | Not Applicable
Combustion of Solid Fuels (Solid Biomass and/or Peat)
AEELs | Energy efficiency | BAT-associated energy efficiency levels (BAT-AEELs) | Associated AEELs. | Not Applicable |  |  |  | Not Applicable
24 | Prevent or reduce emissions of NOx | Prevent or reduce emissions of NOx emissions to air while limiting CO and N2O emissions to air from the combustion of solid biomass and/or peat. | A variety of techniques and associated AELs | Not Applicable |  |  |  | Not Applicable
25 | Prevent or reduce emissions of SOx, HCl and HF | Prevent or reduce emissions of SOx, HCl and HF emissions to air from the combustion of solid biomass and/or peat. | A variety of techniques and associated AELs | Not Applicable |  |  |  | Not Applicable
26 | Reduce dust and particulate-bound metal emissions | Reduce emissions of dust and particulate-bound metal emissions to air from the combustion of solid biomass and/or peat. | A variety of techniques and associated AELs | Not Applicable |  |  |  | Not Applicable
27 | Prevent or reduce emissions of mercury | Prevent or reduce emissions of mercury emissions to air from the combustion of solid biomass and/or peat. | A variety of techniques and associated AELs | Not Applicable |  |  |  | Not Applicable
Combustion of Liquid Fuels (HFO and/or Gas-Oil-Fired Boilers)
AEELs | Energy efficiency | BAT-associated energy efficiency levels (BAT-AEELs) | Associated AEELs. | Not Applicable |  |  |  | Not Applicable
28 | Prevent or reduce emissions of NOx | Prevent or reduce emissions of NOx emissions to air while limiting CO and N2O emissions to air from the combustion of HFO and/or gas oil in boilers. | A variety of techniques and associated AELs. | Not Applicable |  |  |  | Not Applicable
29 | Prevent or reduce emissions of SOx, HCl and HF | Prevent or reduce emissions of SOx, HCl and HF emissions to air from the combustion of HFO and/or gas oil in boilers. | A variety of techniques and associated AELs. | Not Applicable |  |  |  | Not Applicable
30 | Reduce dust and particulate-bound metal emissions | Reduce emissions of dust and particulate-bound metal emissions to air from the combustion of HFO and/or gas oil in boilers. | A variety of techniques and associated AELs. | Not Applicable |  |  |  | Not Applicable
Combustion of Liquid Fuels (HFO and/or Gas-Oil-Fired Engines)
31 | Energy efficiency | BAT-associated energy efficiency levels (BAT-AEELs) | Specified techniques and associated AEELs. | Not Applicable |  |  |  | Not Applicable
32 | Prevent or reduce emissions of NOx | Prevent or reduce emissions of NOx emissions to air from the combustion of HFO and/or gas oil in reciprocating engines. | A variety of techniques and associated AELs | Not Applicable |  |  |  | Not Applicable
33 | Prevent or reduce emissions of CO | Prevent or reduce emissions of CO and volatile organic compounds from the combustion of HFO and/or gas oil in reciprocating engines. | A variety of techniques and associated AELs | Not Applicable |  |  |  | Not Applicable
34 | Prevent or reduce emissions of SOx, HCl and HF | Prevent or reduce emissions of SOx, HCl and HF emissions to air from the combustion of HFO and/or gas oil in reciprocating engines. | A variety of techniques and associated AELs | Not Applicable |  |  |  | Not Applicable
35 | Reduce dust and particulate-bound metal emissions | Reduce emissions of dust and particulate-bound metal emissions to air from the combustion of HFO and/or gas oil in reciprocating engines. | A variety of techniques and associated AELs | Not Applicable |  |  |  | Not Applicable
Combustion of Liquid Fuels (Gas-Oil-Fired Turbines)
36 | Energy efficiency | BAT-associated energy efficiency levels (BAT-AEELs) | Specified techniques and associated AEELs. | Not Applicable |  |  |  | Not Applicable
37 | Prevent or reduce emissions of NOx | Prevent or reduce emissions of NOx emissions to air from the combustion of gas oil in gas turbines. | A variety of techniques |  |  |  |  | Not Applicable
38 | Prevent or reduce emissions of CO | Prevent or reduce emissions of CO from the combustion of gas oil in gas turbines. | A variety of techniques and associated AELs | Not Applicable |  |  |  | Not Applicable
39 | Prevent or reduce emissions of SOx and dust | Prevent or reduce emissions of SOx and dust emissions to air from the combustion of gas oil in gas turbines. | A variety of techniques and associated AELs | Not Applicable |  |  |  | Not Applicable
Combustion of Gaseous Fuels (Natural Gas)
40 | Energy efficiency | BAT-associated energy efficiency levels (BAT-AEELs) | Specified techniques and associated AEELs | For the 9H: 50 - 60% |  | Yes - compliant now | No | Not Applicable to the LM2500 or the Auxiliary Boiler. For informationon the 9H, please see Table 3.2 in the Report ('LCP Regulation 61 Environmental Permit Review: Baglan Bay')
41 | Prevent or reduce emissions of NOx | Prevent or reduce emissions of NOx emissions to air from the combustion of natural gas in boilers | A variety of techniques | For the Auxiliary Boiler: Yearly: Not Applicable Daily: 85 - 110 mg/Nm3 |  | Yes - compliant now | No | For information on the Auxiliary Boiler, please see Table 3.2 in the Report ('LCP Regulation 61 Environmental Permit Review: Baglan Bay')
42 | Prevent or reduce emissions of NOx | Prevent or reduce emissions of NOx emissions to air from the combustion of natural gas in gas turbines | A variety of techniques. Please also define effective dry low NOx load where applicable. | For the 9H: Yearly: 10 - 40 mg/Nm3 Daily: 18 - 50 mg/Nm3 | Define the load at which DLN is effective for each unit within the LCP in terms of: i. The output load (i.e. electricity, heat or power generated) (MW); and ii. This output load as a percentage of the rated thermal output of the combustion plant (%). Where dry low NOx (DLN) is utilised, you should provide information on the NOx emission profile from the load that DLN is effective through to 70% load and to 100% load. | Yes - compliant now | No | For information on the 9H, please see Table 3.2 in the Report ('LCP Regulation 61 Environmental Permit Review: Baglan Bay')
|  |  |  | For the LM2500: Not Applicable |  |  |  | For information on the LM2500, please see Table 3.2 in the Report ('LCP Regulation 61 Environmental Permit Review: Baglan Bay')
43 | Prevent or reduce emissions of NOx | Prevent or reduce emissions of NOx emissions to air from the combustion of natural gas in engines. | A variety of techniques | Not Applicable |  |  |  | Not Applicable (concerns combustion of natural gas in engines)
44 | Prevent or reduce emissions of CO | Prevent or reduce emissions of CO emissions to air from the combustion of natural gas | A variety of techniques and associated AELs | For the 9H: Indicative: <5 - 30 mg/Nm3 | Where the indicative BAT-AEL for CO cannot be achieved, a BAT justification will be required as set out in the supporting interpretational document. | Yes - compliant now | No | Not Applicable to the LM2500 or the Auxiliary Boiler. For informationon the 9H, please see Table 3.2 in the Report ('LCP Regulation 61 Environmental Permit Review: Baglan Bay')
45 | Prevent or reduce emissions of non-methane volatile organic compounds (NMVOC) and methane emissions | Prevent or reduce emissions of non-methane volatile organic compounds (NMVOC) and methane emissions to air from the combustion of natural gas in spark-ignited lean-burn gas engines | A variety of techniques and associated AELs | Not Applicable |  |  |  | Not Applicable (concerns combustion of natural gas in spark-ignitd lean-burn gas engines)
BAT Conclusions for iron and steel process gases (BAT 46 - 51), offshore platforms (BAT 52 - 54) and chemical process gases (BAT 55 - 59), co-incineration (BAT 60 - 71) and gasification (72 - 75) have not been replicated in this table. If you consider these BAT Conclusions applicable to your application please list and provide the required information and append to this table when responding to the Regulation 61 notice.
Derogation
Yes
No
Compliance
Yes - compliant now
Yes - compliant by 31/07/2021
No - will not be compliant

## Guidance
Category of question | What we require
Narrative BAT | Confirm how your operations meet each technique specified. If you have a number of different plants on site you much specify which techniques each plant will operate to. If your compliance date is in the future please specify what you will do to meet BAT by that date.
BAT AELs | For each combustion unit, confirm which AELs you consider applicable and whether you will meet them. If your compliance date is in the future please specify what you will do to meet the AEL by that date.
BAT AEELs | For each combustion unit, confirm which AEEL you consider applicable and whether the plant meets the AEEL. Include information on how this has been determined.