Permit Number: 
EPR/BV3715IL

Operator: 
SCA Hygiene Products UK Limited

Facility:

Oakenholt Paper Mill
Form Number: 
Water1 / 12/07/2013
Reporting of emissions to water (other than to sewer) and land for the period from 01.10.2014 to 31.12.2014
	Emission Point
	Substance / Parameter
	Emission Limit Value
	Reference Period
	Result [1]
	Test

Method [2]
	Sample

Date and Times [3]
	Uncertainty[4]

	W1
	Biochemical Oxygen Demand (BOD)
	50 mg/l
	24-hour flow proportional composite sample
	 25 mg/l
	In accordance with TGN M18
	21.10.2014 09:00
	LOD 1 mg/l

	
	Chemical Oxygen Demand (COD)
	No limit set
	24-hour flow proportional composite sample
	 269 mg/l
	In accordance with TGN M18
	24.12.2014 04:00
	In house

	
	Suspended Solids
	50 mg/l
	24-hour flow proportional composite sample
	48 mg/l
	In accordance with TGN M18
	15.10.2014 04:00
	In house

	
	Temperature
	25oc
	Instantaneous
	23.1oC
	Standard temperature sensor
	24.12.2014 04:00
	In house

	
	Flow
	2200 m3/day
	Instantaneous
	 1971 m3
	MCERTS self monitoring of effluent flow scheme
	28.11.2014 04:00
	In house

	
	Flow (maximum instantaneous)
	108 m3/hour
	Instantaneous
	 105.99m3/hour
	MCERTS self monitoring of effluent flow scheme
	18.10.2014 04:00
	In house

	
	PH
	5 - 9
	Instantaneous
	Min – 7.30
Max – 8.86
	In accordance with TGN M18, MCERTS approved instrumentation if available
	06.10.2014 04:00
16.11.2014 04:00
	In house

	
	Total Nitrogen
	16 mg/l
	24-hour flow proportional composite sample
	  12 mg/l 
	In accordance with TGN M18
	10.11.2014 09:00
	LOD 1 mg/l

	
	Total Phosphorus
	No limit set
	24-hour flow proportional composite sample
	  1.5 mg/l
	In accordance with TGN M18
	14.10.2014 09:00
	LOD 18 ug/l

	
	Metals Zn, As, Cu, Cr, Ni, Pb
	No limit set
	24-hour flow proportional composite sample
	Zn –   1.25 ug/l
As –   0.16 ug/l

Cu –  0.4 ug/l

Cr –  0.25 ug/l

Ni –  0.5ug/l

Pb –  0.09 ug/l
	In accordance with TGN M18
	22.12.2014 09:00
	LOD
Zn - 1.25 ug/l

As - 0.16 ug/l

Cu - 0.4 ug/l

CR - 0.25 ug/l

Ni - 0.5 ug/l

PB – 0.09 ug/l

	W2
	Suspended Solids
	100 mg/l
	Spot sample 
	  14 mg/l 
	In accordance with TGN M18
	09.12.2014 09:00
	In house

	
	PH
	5 - 9
	Spot sample 
	Min – 6.80
Max – 8.32
	MCERTS approved instrumentation
	Min – 01.12.2014 09:00
Max – 16.12.2014 09:00
	In house

	
	Hydrocarbon oil
	15 mg/l
	Spot sample 
	  0.140 mg/l
	In accordance with TGN M18
	14.10.2014 09:00
	LOD – 10 ug/l


[1] The result given is the maximum value (or the minimum value in the case of a limit that is expressed as a minimum) obtained during the reporting period, expressed in the same terms as the emission limit value. Where the emission limit value is expressed as a range, the result is given as the ‘minimum – maximum’ measured values.

[2] Where an internationally recognised standard test method is used the reference number is given. Where another method that has been formally agreed with the Environment Agency is used, then the appropriate identifier is given. In other cases the principal technique is stated, for example gas chromatography.

[3] For non-continuous measurements the date and time of the sample that produced the result is given. For continuous measurements the percentage of the process operating time covered by the result is given.   

[4] The uncertainty associated with the quoted result at the 95% confidence interval, unless otherwise stated.

Signed …Alana Corbett………………………………………………………….  

Date…28.01.2015……………………..


(Authorised to sign as representative of Operator)

Permit Number: 
EPR/BV3715IL


Operator: 
SCA Hygiene Products UK Limited


Facility:

Oakenholt Paper Mill

Form Number: 
Performance1 / 25.04.2013
Reporting of other performance indicators for the period 01.10.2014 to 31.12.2014
	Parameter
	Units

	
	

	NOx/ADT
	0.2778 kg/ADT

	CO2/ADT
	0.364 Tonnes/ADT

	BOD/ADT
	0.0998 Kg/ADT 

	Suspended Solids/ADT
	0.1436 Kg/ADT

	Total Nitrogen
	0.1187 Kg/ADT

	Total Phosphorus
	0.0082 Kg/ADT


	Operator’s comments :




Signed ……Alana Corbett……………………………………………………….  

Date…28.01.2015……………………..   


