[bookmark: _GoBack]Permit Number: 	EPR/BJ9681IX				Operator: 	SCA Hygiene Products UK Limited

Facility:		Oakenholt Paper Mill			Form Number: 	Performance 1 


Reporting of other performance indicators for the period 01/04/2018 to 30/06/2018

	Parameter
	
	Units 
	

	
	
	
	

	BOD
	0.177 Kg / Tonne
	

	Suspended solids
	0.207 Kg / Tonne
	

	Total Nitrogen
	0.176 Kg / Tonne
	

	Total Phosphorous
	0.0177 Kg / Tonne
	

	NOx 
	4.817 Tonnes
	

	CO2
	6334 Tonnes
	

	AOX
	0.00300 Kg / Tonne 
	

	Total Energy Used
	 46448.52 MWh
	

	Effluent Discharged
	167 553 m3
	

	Water input to installation
	172540Tonnes
	

	Water Discharged from installation
	 167 553 Tonnes
	



	Operator’s comments :
1m3 = 1 tonne for water input to installation
1m3 = 1 tonne for water discharge from installation 
Water discharge from installation = Effluent Discharged.
Total energy = Gas & Electricity consumption 






Signed ………MIKE KING…… …….  		Date………09/07/2018…….……	
	(Authorised to sign as representative of Operator)









Permit Number: 	EPR/BJ9681IX				Operator: 	SCA Hygiene Products UK Limited

Facility:		Oakenholt Paper Mill			Form Number: 	 Water 1 
Reporting of emissions to water (other than to sewer) and land for the period from 01/04/2018 to 30/06/2018
	Emission
Point
	Substance /
Parameter
	Emission/
Limit Value
	Reference Period
	Result [1]
	Test
Method [2]
	Sample
Date and Times [3]
	Uncertainty
[4]

	W1
	Biological Oxygen Demand (BOD)
	50 mg/l
	24-hour flow proportional composite sample
	92 mg/L
	MCERTS self-monitoring of effluent flow scheme
	26/06/2018 09:00
	1 mg / L 

	W1
	Chemical Oxygen Demand (COD)
	--
	Spot Sample
	309 mg/L
	MCERTS self-monitoring of effluent flow scheme
	12/06/2018 04:00
	10 mg / L 

	W1
	Total Suspended Solids
	100 mg/l
	24-hour flow proportional composite sample
	49 mg/L
	MCERTS self-monitoring of effluent flow scheme
	26/06/2018 09:00
	5 mg / L 

	W1
	Total Mercury and its compounds
	--
	24-hour flow proportional composite sample
	<0.01 mg/L
	MCERTS self-monitoring of effluent flow scheme
	21/05/2018 09:00
	-

	W1
	Total Cadmium and its compounds
	--
	24-hour flow proportional composite sample
	<0.1 mg/L
	BS EN ISO5961:1995
	21/05/2018 09:00
	-

	W1
	pH
	9
	Instantaneous
	MIN:7.13
MAX: 8.27
	MCERTS self-monitoring of effluent flow scheme
	MIN: 25/05/2018 04:00
MAX: 28/05/2018 04:00
	-

	W1
	Dangerous Substances Screen
	--
	24-hour flow proportional composite sample
	Please see list attached
	MCERTS self-monitoring of effluent flow scheme
	Please see attached list 
	-

	W1
	Temperature
	Maximum 40oC
	Instantaneous
	24.6°C
	MCERTS self-monitoring of effluent flow scheme
	10/04/2018 04:00
	
-


	W1
	Flow rate
	108 m3/hour
	Instantaneous
	107.6 mg/L
	MCERTS self-monitoring of effluent flow scheme
	02/04/2018 04:00
	Less than +/- 8%

	W1
	Ammonia
	16mg/l
	24-hour flow proportional composite sample
	31 mg/L 
	BS EN ISO 11732 
or
ISBN 0117516139
	26/06/2018 09:00
	0.015 mg/l

	W1
	Total Nitrogen
	--
	24-hour flow proportional composite sample
	30 mg/L
	MCERTS self-monitoring of effluent flow scheme
	26/06/2018 09:00
	1 mg/l

	W1
	Total Phosphorus
	--
	24-hour flow proportional composite sample
	3.7 mg/L
	MCERTS self-monitoring of effluent flow scheme
	26/06/2018 09:00
	1.5 mg/l

	W1
	AOx
	--
	24-hour flow proportional composite sample
	0.299 mg/L
	MCERTS self-monitoring of effluent flow scheme
	30/05/2018 09:00
	0.01 mg/l

	W1
	Pb
	--
	24-hour flow proportional composite sample
	0.68 μg/L
	MCERTS self-monitoring of effluent flow scheme
	18/04/2018 09:00
	0.09 μg/l

	W1
	Zn
	--
	24-hour flow proportional composite sample
	70 μg/L
	MCERTS self-monitoring of effluent flow scheme
	18/04/2018 09:00
	1.3 μg/l

	W1
	As
	--
	24-hour flow proportional composite sample
	2.99 μg/L
	MCERTS self-monitoring of effluent flow scheme
	21/05/2018 09:00
	0.16 μg/l

	W1
	Cu
	--
	24-hour flow proportional composite sample
	1.8 μg/L
	MCERTS self-monitoring of effluent flow scheme
	18/04/2018 09:00
	0.4 μg/l

	W1
	Cr
	--
	24-hour flow proportional composite sample
	0.63 μg/L
	MCERTS self-monitoring of effluent flow scheme
	18/04/2018 09:00
	0.25 μg/l

	W1
	Ni
	--
	24-hour flow proportional composite sample
	2.1 μg/L
	MCERTS self-monitoring of effluent flow scheme
	18/04/2018 09:00
	0.5 μg/l







[1] The result given is the maximum value (or the minimum value in the case of a limit that is expressed as a minimum) obtained during the reporting period, expressed in the same terms as the emission limit value. Where the emission limit value is expressed as a range, the result is given as the ‘minimum – maximum’ measured values.
[2] Where an internationally recognised standard test method is used the reference number is given. Where another method that has been formally agreed with Natural Resources Wales is used, then the appropriate identifier is given. In other cases the principal technique is stated, for example gas chromatography.
[3] For non-continuous measurements the date and time of the sample that produced the result is given. For continuous measurements the percentage of the process operating time covered by the result is given.   
[4] The uncertainty associated with the quoted result at the 95% confidence interval, unless otherwise stated.


Signed ……..Mike King …….  		Date………09/07/2018………….






















Essity Internal

Permit Number: 	EPR/BJ9681IX			Operator: 	SCA Hygiene Products UK Limited

Facility:		Oakenholt Paper Mill		Form Number: 	 Air 1 
Reporting of emissions to air for the period from ……………….. to …………..
	Emission
Point
	Substance /
Parameter
	Emission/
Limit Value
	Reference Period
	Result [1]
	Test
Method [2]
	Sample
Date and Times [3]
	Uncertainty
[4]

	A1
	Oxides of Nitrogen
	250 mg/m3
	Hourly average
	
	
	
	

	
	
	
	
	
	
	
	



[1] The result given is the maximum value (or the minimum value in the case of a limit that is expressed as a minimum) obtained during the reporting period, expressed in the same terms as the emission limit value. Where the emission limit value is expressed as a range, the result is given as the ‘minimum – maximum’ measured values.
[2] Where an internationally recognised standard test method is used the reference number is given. Where another method that has been formally agreed with Natural Resources Wales is used, then the appropriate identifier is given. In other cases the principal technique is stated, for example gas chromatography.
[3] For non-continuous measurements the date and time of the sample that produced the result is given. For continuous measurements the percentage of the process operating time covered by the result is given.   
[4] The uncertainty associated with the quoted result at the 95% confidence interval, unless otherwise stated.



Signed …………… ……………….  		Date……………..   	
	(Authorised to sign as representative of Operator)


