Permit Number: 	EPR/BJ9681IX				Operator: 	SCA Hygiene Products UK Limited

Facility:		Oakenholt Paper Mill			Form Number: 	Performance 1

# Reporting of other performance indicators for the period……01 / 04 / 2019 ….. to ……30 / 06 / 2019 …….…

| Parameter |  | Units |  |
| --- | --- | --- | --- |
| BOD |  | 0.110 Kg / Tonne |  |
| Suspended solids |  | 0.180 Kg / Tonne |  |
| Total Nitrogen |  | 0.0552 Kg / Tonne |  |
| Total Phosphorous |  | 0.00969 Kg / Tonne |  |
| NOx |  | 4.884 Tonnes |  |
| CO2 |  | 6404.788 Tonnes |  |
| AOX |  | 0.00335 Kg / Tonne |  |
| Total Energy Used |  | 43662.50 MWh |  |
| Effluent Discharged |  | 147763 m3 |  |
| Water input to installation |  | 160574 Tonnes |  |
| Water Discharged from installation |  | 147763 Tonnes |  |

Operator’s comments : 1m3 = 1 tonne for water input to installation 1m3 = 1 tonne for water discharge from installation Water discharge from installation = Effluent Discharged. Total energy = Gas & Electricity consumption

Signed ………Mike King………….  		Date…….08 / 07 /2019……

(Authorised to sign as representative of Operator)

Permit Number: 	EPR/BJ9681IX				Operator: 	SCA Hygiene Products UK Limited

Facility:		Oakenholt Paper Mill			Form Number: 	 Water 1

# Reporting of emissions to water (other than to sewer) and land for the period from …01 / 04 / 2019…. to …30 / 06 / 2019…...

| Emission Point | Substance / Parameter | Emission/ Limit Value | Reference Period | Result [1] | Test Method [2] | Sample Date and Times [3] | Uncertainty [4] |
| --- | --- | --- | --- | --- | --- | --- | --- |
| W1 | Biological Oxygen Demand (BOD) | 50 mg/l | 24-hour flow proportional composite sample | 33.1 mgL-1 | MCERTS self-monitoring of effluent flow scheme | 24/04/2019 04:00 | 1 mgL-1 |
| W1 | Chemical Oxygen Demand (COD) | -- | Spot Sample | 364 mgL-1 | MCERTS self-monitoring of effluent flow scheme | 24/04/2019 04:00 | 10 mgL-1 |
| W1 | Total Suspended Solids | 50 mg/l | 24-hour flow proportional composite sample | 94.1 mgL-1 | MCERTS self-monitoring of effluent flow scheme | 24/04/2019 04:00 | 5 mgL-1 |
| W1 | Total Mercury and its compounds | -- | 24-hour flow proportional composite sample |  | MCERTS self-monitoring of effluent flow scheme |  | - |
| W1 | Total Cadmium and its compounds | -- | 24-hour flow proportional composite sample |  | BS EN ISO5961:1995 |  | - |
| W1 | pH | 5-9 | Instantaneous | Maximum: 8.25 Minimum: 6.79 | MCERTS self-monitoring of effluent flow scheme | Maximum: 02/04/2019 07:00 Minimum: 28/05/2019 09:45 | - |
| W1 | Dangerous Substances Screen | -- | 24-hour flow proportional composite sample |  | MCERTS self-monitoring of effluent flow scheme |  | - |
| W1 | Temperature | Maximum 25oC | Instantaneous | 23.88°C | MCERTS self-monitoring of effluent flow scheme | 29/06/2019 15:00 | - |
| W1 | Flow rate | 108 m3/hour | Instantaneous | 102.69 m3 hr-1 | MCERTS self-monitoring of effluent flow scheme | 28/06/2019 14:30 | Less than +/- 8% |
| W1 | Ammonia | 16mg/l | 24-hour flow proportional composite sample | 9.34 mgL-1 | BS EN ISO 11732 or ISBN 0117516139 | 22/05/2019 09:00 | 0.015 mgL-1 |
| W1 | Total Nitrogen | -- | 24-hour flow proportional composite sample | 11.4 mgL-1 | MCERTS self-monitoring of effluent flow scheme | 01/05/2019 09:00 | 1 mgL-1 |
| W1 | Total Phosphorus | -- | 24-hour flow proportional composite sample | 2.32 mgL-1 | MCERTS self-monitoring of effluent flow scheme | 03/04/2019 09:00 | 1.5 mgL-1 |
| W1 | AOx | -- | 24-hour flow proportional composite sample | 0.549 mgL-1 | MCERTS self-monitoring of effluent flow scheme | 24/04/2019 09:00 | 0.01 mgL-1 |
| W1 | Pb | -- | 24-hour flow proportional composite sample | <1 μgL-1 | MCERTS self-monitoring of effluent flow scheme | 10/04/2019 09:00 | 1 μg/l |
| W1 | Zn | -- | 24-hour flow proportional composite sample | 24 μgL-1 | MCERTS self-monitoring of effluent flow scheme | 10/04/2019 09:00 | 5 μgL-1 |
| W1 | As | -- | 24-hour flow proportional composite sample | <2 μgL-1 | MCERTS self-monitoring of effluent flow scheme | 10/04/2019 09:00 | 2 μgL-1 |
| W1 | Cu | -- | 24-hour flow proportional composite sample | <1 μgL-1 | MCERTS self-monitoring of effluent flow scheme | 10/04/2019 09:00 | 1 μgL-1 |
| W1 | Cr | -- | 24-hour flow proportional composite sample | <3 μgL-1 | MCERTS self-monitoring of effluent flow scheme | 10/04/2019 09:00 | 3 μgL-1 |
| W1 | Ni | -- | 24-hour flow proportional composite sample | 1.87 μgL-1 | MCERTS self-monitoring of effluent flow scheme | 10/04/2019 09:00 | 2 μgL-1 |

- The result given is the maximum value (or the minimum value in the case of a limit that is expressed as a minimum) obtained during the reporting period, expressed in the same terms as the emission limit value. Where the emission limit value is expressed as a range, the result is given as the ‘minimum – maximum’ measured values.

- Where an internationally recognised standard test method is used the reference number is given. Where another method that has been formally agreed with Natural Resources Wales is used, then the appropriate identifier is given. In other cases the principal technique is stated, for example gas chromatography.

- For non-continuous measurements the date and time of the sample that produced the result is given. For continuous measurements the percentage of the process operating time covered by the result is given.

- The uncertainty associated with the quoted result at the 95% confidence interval, unless otherwise stated.

Signed …Mike King….….  		Date…… 08 / 07 / 2019 ….