Schedule 5 - Notification 

These pages outline the information that the operator must provide. 

Units of measurement used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission. Where appropriate, a comparison should be made of actual emissions and authorised emission limits.

If any information is considered commercially confidential, it should be separated from non-confidential information, supplied on a separate sheet and accompanied by an application for commercial confidentiality under the provisions of the EP Regulations.

Part A 
	Permit Number
	BV3715IL

	Name of operator
	SCA Hygiene UK Ltd

	Location of Facility
	Chester Road, Oakenholt, Flintshire, CH6 5PU

	Time and date of the detection 
	28 May 2015


	(a) Notification requirements for any malfunction, breakdown or failure of equipment or techniques, accident, or emission of a substance not controlled by an emission limit which has caused, is causing or may cause significant pollution

	To be notified within 24 hours of detection

	Date and time of the event
	28 May 2015

	Reference or description of the location of the event 
	Final Effluent (at W1) temperature out of consent due to heat exchanger blockage.

	Description of where any release into the environment took place
	W1 emission point

	Substances(s) potentially released
	Final effluent with an elevated temperature (over 25oC permit limit)

	Best estimate of the quantity or rate of  release of substances
	Effluent drifting in and out of consent (only marginally over permit limit at around 26oC)

	Measures taken, or intended to be taken, to stop any emission
	Restriction of flows through heat exchanger to try and keep temperature within consent as far as possible

	Description of the failure or accident.
	Cooling tower heat exchanger blockage


	(b) Notification requirements for the breach of a limit

	To be notified within 24 hours of detection unless otherwise specified below

	Emission point reference/ source
	W1 

	Parameter(s)
	<25oC

	Limit
	<25oC

	Measured value and uncertainty
	N/A

	Date and time of monitoring
	28 May 2015

	Measures taken, or intended to be taken, to stop the emission
	Restriction of flows through heat exchanger to try and keep temperature within consent as far as possible


	Time periods for notification following detection of a breach of a limit

	Parameter
	Notification period

	
	

	
	

	
	


	(c) Notification requirements for the detection of any significant adverse environmental effect

	To be notified within 24 hours of detection

	Description of where the effect on the environment was detected
	None anticipated.  High flow overspill from the reservoir.  Final effluent is being blended with the overspill.

	Substances(s) detected
	

	Concentrations of substances detected
	

	Date of monitoring/sampling
	


