Schedule 5 - Notification 

These pages outline the information that the operator must provide. 

Units of measurement used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission. Where appropriate, a comparison should be made of actual emissions and authorised emission limits.

If any information is considered commercially confidential, it should be separated from non-confidential information, supplied on a separate sheet and accompanied by an application for commercial confidentiality under the provisions of the EP Regulations.

Part B - to be submitted as soon as practicable
	Any more accurate information on the matters for notification under Part A.
	During some electrical work the blowers to the Bio Tower (on the Effluent Treatment Plant) were inadvertently shut down.  The electrician recognised this and went to the control room to restart them.  What he was unaware of was that an additional local action was required to start the blower.
Because the alarms were all local to the blowers nobody was alerted.

The air remained off for a number of hours resulting in elevated readings around the ETP.

Suspended solids – 174ppm (limit 50ppm)
COD – 594mg/l (no limit)

BOD 270mg/l (limit 50mg/l)



	Measures taken, or intended to be taken, to prevent a recurrence of the incident
	We have now installed remote alarms in the control rooms and around the paper machines.

	Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment which has been or may be caused by the emission
	

	The dates of any unauthorised emissions from the facility in the preceding 24 months.
	21.07.2013, 27.07.2013, 22.10.2013, 10.02.2014, 07.04.2014, 02.02.2015, 27.02.2015, 28.05.2015, 01.06.2015


	Name*
	Alana Corbett

	Post
	Quality / Environmental Leader

	Signature
	

	Date
	28 July 2015


* authorised to sign on behalf of the operator

