Schedule 5 - Notification 

These pages outline the information that the operator must provide. 

Units of measurement used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission. Where appropriate, a comparison should be made of actual emissions and authorised emission limits.

If any information is considered commercially confidential, it should be separated from non-confidential information, supplied on a separate sheet and accompanied by an application for commercial confidentiality under the provisions of the EP Regulations.

Part A 
	Permit Number
	BV3715IL

	Name of operator
	SCA Hygiene UK Ltd

	Location of Facility
	Chester Road, Oakenholt, Flintshire, CH6 5PU

	Time and date of the detection 
	26 January 2016


	(a) Notification requirements for any malfunction, breakdown or failure of equipment or techniques, accident, or emission of a substance not controlled by an emission limit which has caused, is causing or may cause significant pollution

	To be notified within 24 hours of detection

	Date and time of the event
	26 January 2016

	Reference or description of the location of the event 
	External test results for:

Suspended solids showed a result of 120ppm.
BOD for this period showed a result of  80mg/l

Total Nitrogen for this period showed a result of 43mg/l

	Description of where any release into the environment took place
	None

	Substances(s) potentially released
	None

	Best estimate of the quantity or rate of  release of substances
	None

	Measures taken, or intended to be taken, to stop any emission
	ETP automatically goes into recirculation and dilution water added to system

	Description of the failure or accident.
	Potential to release out of consent suspended solids


	(b) Notification requirements for the breach of a limit

	To be notified within 24 hours of detection unless otherwise specified below

	Emission point reference/ source
	W1

	Parameter(s)
	Suspended solids  - BOD  - Total N

	Limit
	50ppm  - 50mg/l – 16mg/l

	Measured value and uncertainty
	120ppm (5ppm) – 80mg/l (1mg/l) – 43mg/l (1mg/l)

	Date and time of monitoring
	26 January 2016 (external samples)

	Measures taken, or intended to be taken, to stop the emission
	ETP put into recirculation and dilution water added to system


	Time periods for notification following detection of a breach of a limit

	Parameter
	Notification period

	
	

	
	

	
	


	(c) Notification requirements for the detection of any significant adverse environmental effect

	To be notified within 24 hours of detection

	Description of where the effect on the environment was detected
	None known / anticipated

	Substances(s) detected
	

	Concentrations of substances detected
	

	Date of monitoring/sampling
	


