Schedule 5 - Notification 

These pages outline the information that the operator must provide. 

Units of measurement used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission. Where appropriate, a comparison should be made of actual emissions and authorised emission limits.

If any information is considered commercially confidential, it should be separated from non-confidential information, supplied on a separate sheet and accompanied by an application for commercial confidentiality under the provisions of the EP Regulations.

Part A 
	Permit Number
	BV3715IL

	Name of operator
	SCA Hygiene UK Ltd

	Location of Facility
	Chester Road, Oakenholt, Flintshire, CH6 5PU

	Time and date of the detection 
	07 January 2016


	(a) Notification requirements for any malfunction, breakdown or failure of equipment or techniques, accident, or emission of a substance not controlled by an emission limit which has caused, is causing or may cause significant pollution

	To be notified within 24 hours of detection

	Date and time of the event
	07 January 2016

	Reference or description of the location of the event 
	Suspended solids test result showed 82ppm against the permit limit of 50ppm

	Description of where any release into the environment took place
	None

	Substances(s) potentially released
	None

	Best estimate of the quantity or rate of  release of substances
	None

	Measures taken, or intended to be taken, to stop any emission
	ETP put into recirculation and dilution water added to system

	Description of the failure or accident.
	Potential to release out of consent suspended solids


	(b) Notification requirements for the breach of a limit

	To be notified within 24 hours of detection unless otherwise specified below

	Emission point reference/ source
	W1

	Parameter(s)
	Suspended solids

	Limit
	50ppm

	Measured value and uncertainty
	82ppm

	Date and time of monitoring
	07 January 2016 (24 hour sample)

	Measures taken, or intended to be taken, to stop the emission
	ETP put into recirculation and dilution water added to system until results came within permit limit


	Time periods for notification following detection of a breach of a limit

	Parameter
	Notification period

	
	

	
	

	
	


	(c) Notification requirements for the detection of any significant adverse environmental effect

	To be notified within 24 hours of detection

	Description of where the effect on the environment was detected
	None known or anticipated

	Substances(s) detected
	

	Concentrations of substances detected
	

	Date of monitoring/sampling
	


Part B - to be submitted as soon as practicable
	Any more accurate information on the matters for notification under Part A.
	PM1 experienced difficulties on start up after the holiday period which resulted in excess fibre being dumped into the system.

04-01-16 PM2 had a fibre spill from the broke chest which entered the system.

PST had been turned off over holiday period.

	Measures taken, or intended to be taken, to prevent a recurrence of the incident
	More focus during shutdown periods and during start up

	Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment which has been or may be caused by the emission
	No emission to environment

	The dates of any unauthorised emissions from the facility in the preceding 24 months.
	10.02.14, 07.04.14, 02.02.2015, 27.02.2015, 28.05.2015, 01.06.2015, 27.07.15, 03.08.15


	Name*
	Mike King

	Post
	Safety Specialist / Environmental Leader

	Signature
	

	Date
	30/08/16


* authorised to sign on behalf of the operator

