Schedule 5 - Notification 

These pages outline the information that the operator must provide. 

Units of measurement used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission. Where appropriate, a comparison should be made of actual emissions and authorised emission limits.

If any information is considered commercially confidential, it should be separated from non-confidential information, supplied on a separate sheet and accompanied by an application for commercial confidentiality under the provisions of the EP Regulations.

Part A 
	Permit Number
	BV3715IL

	Name of operator
	SCA Hygiene UK Ltd

	Location of Facility
	Chester Road, Oakenholt, Flintshire, CH6 5PU

	Time and date of the detection 
	27 Feb 2015


	(a) Notification requirements for any malfunction, breakdown or failure of equipment or techniques, accident, or emission of a substance not controlled by an emission limit which has caused, is causing or may cause significant pollution

	To be notified within 24 hours of detection

	Date and time of the event
	27 Feb 2015

	Reference or description of the location of the event 
	Fire PM2  

	Description of where any release into the environment took place
	Smoke to air

	Substances(s) potentially released
	Smoke to Air.  All water used to extinguish was contained on site and recycled through the Effluent Treatment Plant

	Best estimate of the quantity or rate of  release of substances
	Smoke to air

	Measures taken, or intended to be taken, to stop any emission
	Extinguished by internal site fire team - Fire brigade attended site check roof space / thermal imaging

	Description of the failure or accident.
	Fire


	(b) Notification requirements for the breach of a limit

	To be notified within 24 hours of detection unless otherwise specified below

	Emission point reference/ source
	Air

	Parameter(s)
	N/A

	Limit
	N/A

	Measured value and uncertainty
	N/A

	Date and time of monitoring
	27.02.2015 (approx. 08:00)

	Measures taken, or intended to be taken, to stop the emission
	Extinguished by internal site fire team - Fire brigade attended site check roof space / thermal imaging


	Time periods for notification following detection of a breach of a limit

	Parameter
	Notification period

	
	

	
	

	
	


	(c) Notification requirements for the detection of any significant adverse environmental effect

	To be notified within 24 hours of detection

	Description of where the effect on the environment was detected
	None known / anticipated

	Substances(s) detected
	

	Concentrations of substances detected
	

	Date of monitoring/sampling
	


