Schedule 5 - Notification 

These pages outline the information that the operator must provide. 

Units of measurement used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission. Where appropriate, a comparison should be made of actual emissions and authorised emission limits.

If any information is considered commercially confidential, it should be separated from non-confidential information, supplied on a separate sheet and accompanied by an application for commercial confidentiality under the provisions of the EP Regulations.

Part A 
	Permit Number
	BG9681IX

	Name of operator
	SCA Hygiene UK Ltd

	Location of Facility
	Chester Road, Oakenholt, Flintshire, CH6 5PU

	Time and date of the detection 
	July 8th 2016 – 08.30


	(a) Notification requirements for any activity that gives rise to an incident or accident which significantly affects or may significantly affect the environment

	To be notified immediately

	Date and time of the event
	July 8th 2016 – 08.30

	Reference or description of the location of the event 
	This report is to support our notification by telephone of a near miss with the potential of release to estuary. During this week we have experienced two high results for suspended solids (83 & 59ppm).

	Description of where any release into the environment took place
	PM2 machine hall

	Substances(s) potentially released
	Dye

	Best estimate of the quantity or rate of release of substances
	Best estimate would be 20 litres.

	Measures taken, or intended to be taken, to stop any emission
	· ETP was put into recirculation in order to contain, treat and further dilute the contents.

· Both paper machines were closed whilst resolution was sought.

· MSDS checked.

· Advice sought from manufacturer.

· Testing carried out on Ph. / COD and suspended solids (all results were within limits)

· Monitoring frequency increased to six hourly

	Description of the failure or accident.
	Potential to release to estuary.


	(b) Notification requirements for the breach of a permit condition

	To be notified immediately

	Emission point reference/ source
	IBC

	Parameter(s)
	Suspended solids

	Limit
	50ppm

	Measured value and uncertainty
	Not known.

	Date and time of monitoring
	July 8th 2016

	Measures taken, or intended to be taken, to stop the emission
	Site closed and ETP was put into recirculation whilst we carried out tests. 


	Time periods for notification following detection of a breach of a limit

	Parameter
	Notification period

	
	

	
	

	
	


	(c) In the event of a breach of permit condition which poses an immediate danger to human health or threatens to cause an immediate significant adverse effect on the environment.

	To be notified immediately

	Description of where the effect on the environment was detected
	None known or anticipated

	Substances(s) detected
	None

	Concentrations of substances detected
	None

	Date of monitoring/sampling
	July 8th 2016 and ongoing throughout a two-week period


Part B - to be submitted as soon as practicable
	Any more accurate information on the matters for notification under Part A.
	IBC was found to be leaking during change over. This was not leaking during transportation, as it was checked before being moved into position. This was only seen when returning from transporting empty IBC, and preparing to position new IBC.

	Measures taken, or intended to be taken, to prevent a recurrence of the incident
	· Incident reported on SHE system, and communicated to all staff.

· Spills awareness carried out as a monthly training topic. 
· Further awareness training planned for Goal Deployment day in October

	Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment which has been or may be caused by the emission
	Increased monitoring over a four-week period

	The dates of any unauthorised emissions from the facility in the preceding 24 months.
	27/7/15, 3/8/15, 7/1/16, 17/3/16,15/4/16, 16/5/16


	Name*
	Mike King

	Post
	Safety Specialist & Environment Leader

	Signature
	

	Date
	01/09/2016


* authorised to sign on behalf of the operator

