## Input Page
PROFORMA FOR DETERMINING ENERGY EFFICIENCY USING R1
Site name | North Wales Deeside Site | Permit reference | [6 empty] | Choose an option
What data has been used in the application? → |  | Design data | [6 empty] | Design data
Details of who to contact if we have any queries regarding this form | [8 empty] | Operational Data
Indicative R1 factor (subject to confirmation) | 0.88172 | Quantity in reporting year | Units | Uc | Properties (Average over reporting year) | Units | Note which parameters that have been estimated | Reference to Supporting information | Commissioning Data
1. Gross electricity meter (Electricity produced at turbine) |  | 150400 | MWh |  |  |  |  | Water-Steam PFD
2. Electricity exported - Net input/output meter |  | 132800 | MWh |  |  |  | Guaranteed parasitic load of 2.2MW. | Water-Steam PFD
3. Electricity imported - Net input/output meter |  | 380 | MWh |  |  |  | 0.5MW for 760hr/year | Assumed
4. Other fuel inputs
| 4.1 Light fuel oil | 217620 | litres |  | 0.93 | kg/l | Fuel consumption for startups/shutdowns and abnormal operation | Assumed by EPC
[5 empty] | 42800 | kJ/kg
| 4.2 Natural gas |  | Nm3 |  | 34200 | kJ/Nm3
| 4.3 LPG |  | Nm3 |  |  | kg/Nm3
kJ/kg
| 4.4 Other fuels similar to light fuel oil |  | litres |  |  | kg/l
kJ/kg
5. Primary combustion air (as supplied to furnace) |  | 858176000 | Nm3 |  | 180 | °C |  | Air flue gas PFD
[5 empty] | 1.287 | kg/Nm3
[5 empty] | 156.55 | kJ/kg
6. Secondary combustion air (as supplied to furnace) |  | 151952000 | Nm3 |  | 180 | °C |  | Air flue gas PFD (secondary and tertiary air)
[5 empty] | 1.287 | kg/Nm3
[5 empty] | 156.55 | kJ/kg
7. Recycled flue gas (as supplied to furnace) |  | 59592000 | Nm3 |  | 200 | °C |  | Air flue gas PFD
[5 empty] | 1.248 | kg/Nm3
[5 empty] | 176.75 | kJ/kg
8. Heat exported outside R1 boundary
| 8.1 steam exported |  | tonnes |  |  | °C
kPa
kJ/kg
| condensate returned |  | tonnes |  |  | °C
kPa
kJ/kg
| 8.2 hot water exported |  | tonnes |  |  | °C
kPa
kJ/kg
| hot water returned |  | tonnes |  |  | °C
kPa
kJ/kg
9. Internal steam use
| 9.1 for soot blowing (no backflow) | 36400 | tonnes |  | 410 | °C |  | Sootblowing datasheet
[5 empty] | 62000 | kPa
[5 empty] | 3196 | kJ/kg
| 9.2 for steam driven devices | 0 | tonnes |  |  | °C
kPa
kJ/kg
| backflow as steam | 0 | tonnes |  |  | °C
kPa
kJ/kg
| 9.3 for trace heating | 0 | tonnes |  |  | °C
kPa
kJ/kg
| backflow as condensate | 0 | tonnes |  |  | °C
kPa
kJ/kg
| 9.4 for re-heating flue gas | 0 | tonnes |  |  | °C
kPa
kJ/kg
| backflow as condensate | 0 | tonnes |  |  | °C
kPa
kJ/kg
| 9.5 for concentration processes | 0 | tonnes |  |  | °C
kPa
kJ/kg
| backflow as condensate | 0 | tonnes |  |  | °C
kPa
kJ/kg
| 9.6 for building, equipment, tank heating | 0 | tonnes |  |  | °C
kPa
kJ/kg
| backflow as condensate | 0 | tonnes |  |  | °C
kPa
kJ/kg
| 9.7 for deaeration and demineralisation | 0 | tonnes |  |  | °C
kPa
kJ/kg
| backflow as condensate | 0 | tonnes |  |  | °C
kPa
kJ/kg
| 9.8 other internal applications, in line with commission guidance, to be specified | 0 | tonnes |  |  | °C
kPa
kJ/kg
| backflow as condensate | 0 | tonnes |  |  | °C
kPa
kJ/kg
| 9.9 other internal applications, in line with commission guidance, to be specified | 0 | tonnes |  |  | °C
kPa
kJ/kg
| backflow as condensate | 0 | tonnes |  |  | °C
kPa
kJ/kg
10. Use of condensing energy from steam in flue gas |  | 0 | GJ
11. Superheated steam at boiler outlet |  | 667760 | tonnes |  | 407 | °C |  | Water-Steam PFD
[5 empty] | 6000 | kPa
[5 empty] | 3185 | kJ/kg
12. Boiler feedwater |  | 667760 | tonnes |  | 130 | °C |  | Water-Steam PFD
[5 empty] | 8150 | kPa
[5 empty] | 552 | kJ/kg
13. Boiler efficiency |  | 88% | ± | 1.5% |  |  |  | Water-Steam PFD
Instructions for completing this spreadsheet
1. | Ensure that you have completed the first three rows of the application form
2. | This form should be accompanied by supporting information for the figures quoted. Where this information is in the permit application, reference to the relevant sections of the application can be made.
A Sankey diagram (or equivalent) reflecting the boundaries of the installation used as well as any references to physical properties is the absolute minimum that should be provided for an application based on design information
3. | We have colour coded the cells in this spreadsheet to assist you in completing this form, an explanation of the colour codes is provided below. The colour will disappear when data has been entered.
Blue cells require data that is essential for the R1 calculation, where information on uncertainty of the data is available it would be useful (but not mandatory) for this to be included for these parameters.
Beige Cells indicate that any data entered will be used in the R1 calculation. They have been used where there is a choice of inputs but not all plants will have data for all the input options.
Where you are entering data into beige cells you need to make sure that you enter data into all the beige cells associated with the input as they are all needed for carrying out the calculation.
Yellow cells have been used to provide flexibility to include fuels or energy uses not identified elsewhere. Supporting information to explain why the standard fields were not appropriate or adequate will need to be provided where these cells are used
Data entered in uncoloured cells are not used when calculating the R1 energy efficiency factor but can be completed to provide a more complete data set.
4. | If you believe that any of the information that you have submitted in this application form is commercially confidential please identify the confidential information and the grounds on which you believe it to be confidential in your covering letter
LIT 5753
EAD/0812/xls/v2.3
Note on E5: Uncertainty expressed as a percentage
Note on F5: For applications based on design data this should be the anticipated values based on normal operation
Note on F10: Source: 1. Rose and Cooper Seventh Edition 1977 – The British National Committee and World Energy Conference
Note on F11: Source: 1. Rose and Cooper Seventh Edition 1977 – The British National Committee and World Energy Conference
Note on F12: Source: http://chp.decc.gov.uk/cms/fuel-calorific-value
Note on F20: Calculated as per section 6.3.3 of the FDBR guideline using a specific heat of 1.01 and based on a reference temperature of 25 degree centigrade
Note on F23: Calculated as per section 6.3.3 of the FDBR guideline using a specific heat of 1.01 and based on a reference temperature of 25 degree centigrade
Note on F26: Calculated as per section 6.3.3 of the FDBR guideline using a specific heat of 1.01 and based on a reference temperature of 25 degree centigrade
Note on E100: Estimated error taken from FDBR guideline (range 1-1.5%)

## Summary calculation
Ep (detailed) | 1535711.84
Ef + Ei | 12218.9465
Ew + Ef | 1781302.7931
R1 | 0.88172

## Ep
|  | Quantity in reporting year |  | Uc | Average during operation over year |  | Uc |  |  | Uc |  |  | Uncertainty
Gross electricity meter (Electricity produced at turbine) |  | 150400 | MWh
Electricity exported - Net input/output meter |  | 132800 | MWh
Heat exported outside R1 boundary |  | 0 | GJ
| steam exported | 0 | tonnes |  | 0 | K |  | 0 | kPa |  | 0 | kJ/kg
| condensate returned | 0 | tonnes |  | 0 | K |  | 0 | kPa |  | 0 | kJ/kg
| hot water exported | 0 | tonnes |  | 0 | K |  | 0 | kPa |  | 0 | kJ/kg
| hot water returned | 0 | tonnes |  | 0 | K |  | 0 | kPa |  | 0 | kJ/kg
Internal steam use |  | 116334.4 | GJ
| for soot blowing (no backflow) | 36400 | tonnes |  |  | K |  |  | kPa |  | 3196 | kJ/kg
| for steam driven devices | 0 | tonnes |  |  | K |  |  | kPa |  | 0 | kJ/kg
| backflow as steam | 0 | tonnes |  |  | K |  |  | kPa |  | 0 | kJ/kg
| for trace heating | 0 | tonnes |  |  | K |  |  | kPa |  | 0 | kJ/kg
| backflow as condensate | 0 | tonnes |  |  | K |  |  | kPa |  | 0 | kJ/kg
| for re-heating flue gas | 0 | tonnes |  |  | K |  |  | kPa |  | 0 | kJ/kg
| backflow as condensate | 0 | tonnes |  |  | K |  |  | kPa |  | 0 | kJ/kg
| for concentration processes | 0 | tonnes |  |  | K |  |  | kPa |  | 0 | kJ/kg
| backflow as condensate | 0 | tonnes |  |  | K |  |  | kPa |  | 0 | kJ/kg
| for building, equipment, tank heating | 0 | tonnes |  |  | K |  |  | kPa |  | 0 | kJ/kg
| backflow as condensate | 0 | tonnes |  |  | K |  |  | kPa |  | 0 | kJ/kg
| other internal applications to be specified | 0 | tonnes |  |  | K |  |  | kPa |  | 0 | kJ/kg
| backflow as condensate | 0 | tonnes |  |  | K |  |  | kPa |  | 0 | kJ/kg
| other internal applications to be specified | 0 | tonnes |  |  | K |  |  | kPa |  | 0 | kJ/kg
| backflow as condensate | 0 | tonnes |  |  | K |  |  | kPa |  | 0 | kJ/kg
| other internal applications to be specified | 0 | tonnes |  |  | K |  |  | kPa |  | 0 | kJ/kg
| backflow as condensate | 0 | tonnes |  |  | K |  |  | kPa |  | 0 | kJ/kg
Use of condensing energy from steam in flue gas |  | 0 | GJ
Backflows of condensate |  |  | GJ
| Condensate after cooling |  | tonnes |  |  | K |  |  | kPa |  |  | kJ/kg
| Boiler feedwater |  | tonnes |  |  | K |  |  | kPa |  |  | kJ/kg
Ep |  | 1535711.84
Note on E1: Uncertainty expressed as a percentage
Note on H1: Uncertainty expressed as a percentage
Note on K1: Uncertainty expressed as a percentage

## Ef+Ei
| Quantity in reporting year |  | Uc
Electricity imported - Net input/output meter | 380 | MWh
Other fuel inputs | 8662.1465 | GJ
Light fuel oil | 217620 | litres |  | 0.93 | kg/l | 42800 | kJ/kg
Natural gas | 0 | Nm3 |  | 34200 | kJ/Nm3
LPG | 0 | Nm3 |  | 0 | kg/Nm3 | 0 | kJ/kg
Other fuels similar to light fuel oil | 0 | litres |  | 0 | kg/l | 0 | kJ/kg
Ef + Ei | 12218.9465 | GJ
Note on D1: Uncertainty expressed as a percentage

## Ew+Ef
| Quantity in reporting year |  | Uc | Average during operation over year |  | Uc |  |  | Uc |  |  | Uc
Superheated steam at boiler outlet | 667760 | tonnes |  | 407 | K |  | 6000 | kPa |  | 3185 | kJ/kg
Boiler feedwater | 667760 | tonnes |  | 130 | K |  | 8150 | kPa |  | 552 | kJ/kg
Primary combustion air (heated) | 858176000 | Nm3 |  | 180 | K |  | 1.287 | kg/Nm3 |  | 156.55 | kJ/kg | #REF!
Secondary combustion air (heated) | 151952000 | Nm3 |  | 180 | K |  | 1.287 | kg/Nm3 |  | 156.55 | kJ/kg | #REF!
Recirculated flue gas | 59592000 | Nm3 |  | 200 | K |  | 1.248 | kg/Nm3 |  | 176.75 | kJ/kg
Energy of steam | 2126815.6 | GJ per annum
Energy of feedwater | 368603.52 | GJ per annum
Energy of combustion air | 216665.4796 | GJ per annum
Boiler Efficiency | 88% | ± | 1.5%
Ew+Ef | 1781302.7931 | GJ per annum
Note on D1: Uncertainty expressed as a percentage
Note on G1: Uncertainty expressed as a percentage
Note on J1: Uncertainty expressed as a percentage
Note on M1: Uncertainty expressed as a percentage
Note on H10: Estimate with no pre-heating
Note on K10: Estimate with preheating
Note on D11: Estimated error taken from FDBR guideline (range 1-1.5%)

## Version Control
Version | Created by | Changes made | Date
1 | CDM | Original to be used as a guide | 2011-08-19
2.1 | CDM | Colour coding essential cells and introducing the notes at the bottom | 2011-10-31
2.2 | CDM | Removed section 10, added FGR and included indicative properties | 2011-12-31
2.3 | CDM | Added title, and modified sections 5,6 and 7 so that they did not return negative values | 2012-09-09