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Introductory note

This introductory note does not form a part of the Permit

The following Permit is issued under Regulation 10 of the Pollution Prevention and Control (England and Wales) Regulations 2000 (S.I.2000 No.1973), as amended, (“the PPC Regulations”) to operate an installation carrying out activities covered by the description in Section 2.3 Part A(1) (a)  in Part 1 to Schedule 1 of the PPC Regulations, to the extent authorised by the Permit: 
['Section 2.3 A(1)(a) – The surface treatment of metals and plastics exceeding 30m3. “]

Aspects of the operation of the installation which are not regulated by conditions of the Permit are subject to the condition implied by Regulation 12(10) of the PPC Regulations, i.e. the Operator shall use the best available techniques for preventing or, where that is not practicable, reducing emissions from the installation.

Techniques include both the technology used and the way in which the installation is designed, built, maintained, operated and decommissioned.

In some sections of the Permit conditions require the Operator to use Best Available Techniques (BAT), in each of the aspects of the management of the installation, to prevent and where that is not practicable to reduce emissions.  The conditions do not explain what is BAT.  In determining BAT, the Operator should pay particular attention to relevant sections of the IPPC Sector guidance, appropriate Horizontal guidance and other relevant guidance.

A non-technical description of the installation is given in the Application, but the main features of the installation are as follows.  
The Trostre Site is run within the Corus Packaging Plus business unit, providing cold rolled and coated steel to various customers. The main works area of the site covers approximately 80 hectares, and is located on a wide, flat coastal plain.  The raw material for the Trostre works consists of rolled steel coils, transported from other Corus sites. Coils are received by rail or by road into the Pickle line receipt bay. They enter the receipt bay on a railway locomotive, and are offloaded by crane, before being relocated to a specific area for storage prior to scheduling. When scheduled for pickling, coil is transported by crane to the entry end of the pickle line. The purpose of the pickling process is to remove all scale from the coil using sulphuric acid, and prepare it for further processing at the cold reduction mill. The process is continuous, and coil size is optimised to maximise efficiency at the five stand cold reduction mill. The purpose of the five stand CRM is to reduce the thickness of the coil to a given size. The unit is made up of five roll stands, each with a pair of work rolls and back-up rolls. Final gauge of material leaving the five stand CRM is between 0.12 and 0.6mm.

After cold reduction, lubricant from the CRM process is removed using an electrolytic cleaning method, using caustic solution. Following cleaning, the single reduced coil is then sent for batch or continuous annealing, depending on the product being made. After annealing, the material is temper rolled to give customer required surface finish and mechanical properties. The installation also processes double-reduced coil, which is sent through the double reduction mill [DRM]. The DRM is a three-stand reduction mill, with a similar configuration to the temper mill. The major volume product of the works is tinplate. There are two tin coating lines at Trostre, using thin rolled coil produced elsewhere within the works. The tinplating process involves cleaning, pickling, and electrolytic deposition of tin to the required coating weight. The installation also produces electrolytically chrome-coated steel, a substitute for tinplate in some applications. The process operates on the same principle as tinplate, except that the coating electrolyte contains chromic acid – this product is manufactured on a dedicated line at Trostre. Effluent arising at the installation is treated at a designated effluent treatment plant, owned by the Operator, but operated under contract by Violia Water Ltd. A discharge from this ETP is made to the Loughor estuary via a dedicated effluent discharge point. The installation also contains waste handling, recovery and disposal operations. Electricity is provided via the national grid, whereas heat to drive the process is provided by a dedicated boiler house
Note that the Permit requires the submission of certain information to the Agency (see Sections 4 and 5).  In addition, the Agency has the power to seek further information at any time under regulation 28 to the PPC Regulations provided that it acts reasonably.

	Other  PPC Permits relating to this installation

	Permit holder
	Permit Number
	Date of Issue

	None
	
	


	Superseded Licences/Authorisations/Consents relating to this installation

	Holder
	Reference Number
	Date of Issue

	Corus Packaging  - Water Quality Consent
	BE0038201
	31/07/19785

	Corus Packaging – Section 1.3(A) [Aggregated combustion over 50 MWTh] of Schedule 1 to SI 472:1991
	AF7789/BQ3380
	AF7789 – 1/12/92

BQ3380 – 11/02/02


Other activities may take place on the site of this installation which are not regulated under this Permit or any other PPC Permit referred to in the Table above.  These activities include :-
Supply of mixed gases [Hydrogen / Nitrogen] from on-site BOC gas delivery plant.

	Other existing Licences/Authorisations/Registrations relating to this site

	Holder
	Reference Number
	Date of issue

	None 
	
	


Public Registers 

Considerable information relating to Permits including the Application is available on public registers in accordance with the requirements of the PPC Regulations.  Certain information may be withheld from public registers where it is commercially confidential or contrary to national security. 

Variations to the Permit

This Permit may be varied in the future (by the Agency serving a Variation Notice on the Operator).  If the Operator itself wants any of the Conditions of the Permit to be changed, it must submit a formal Application.  The Status Log within the Introductory Note to any such Variation Notice will include summary details of this Permit, variations issued up to that point in time and state whether a consolidated version of the Permit has been issued.

Surrender of the Permit

Before this Permit can be wholly or partially surrendered, an Application to surrender the Permit has to be made by the Operator.  For the application to be successful, the Operator must be able to demonstrate to the Agency that there is no pollution risk and that no further steps are required to return the site to a satisfactory state. 

Transfer of the Permit or part of the Permit

Before the Permit can be wholly or partially transferred to another person, an Application to transfer the Permit has to be made jointly by the existing and proposed holders.  A transfer will be allowed unless the Agency considers that the proposed holder will not be the person who will have control over the operation of the installation or will not comply with the conditions of the transferred Permit.  If, however, the Permit authorises the carrying out of a specified waste management activity, the transfer will only be allowed if the proposed holder is also considered to be "a fit and proper person" as required by the PPC Regulations.

Talking to us

Please quote the Permit Number if you contact the Agency about this Permit.

To give a Notification under Condition 5.1.1, the Operator should use the Incident Hotline telephone number (0800 80 70 60) or any other number notified in writing to the Operator by the Agency for that purpose.

Status Log

	Detail
	Date
	Response Date

	Application BX9471IU
	Received 29/07/04
	Duly Made 29/07/04

	Response to request for information – Submission of amended Application Site Report
	Sent 22/10/04
	Submission received 28/01/05

	Response to request for information – submission of site plans
	Sent 16/02/05
	Submission received 17/2/05

	Permit determined
	24/03/05
	

	
	
	

	
	
	


End of Introductory Note.



	Permit


Pollution Prevention and Control 

Regulations 2000

Permit

Permit number 

BX9471IU

The Environment Agency (the Agency) in exercise of its powers under Regulation 10 of the Pollution Prevention and Control (England and Wales) Regulations (SI 2000 No 1973), hereby authorises

Corus UK Ltd  ("the Operator"),

whose Registered Office (or principal place of business) is

Corus UK Ltd

30 Millbank

London 

SW1P 4WY

Company registration number 2280000
to operate an Installation at

Corus Packaging Plus

Trostre Works

Trostre

Llanelli

Carms 

SA14 9SD

to the extent authorised by and subject to the conditions of this Permit.

	Signed
	Date

	
	


S McFarlane

Authorised to sign on behalf of the Agency

Conditions 

1 General

1.1
Permitted Activities

1.1.1
The Operator is authorised to carry out the activities and the associated activities specified in Table 1.1.1.

	Table 1.1.1
	
	

	Activity listed in Schedule 1 of the PPC Regulations / Associated Activity
	Description of specified activity
	Limits of specified activity 

	Section 2.3 Part A(1)(a) – Surface treatment of metals and plastics exceeding 30m3
	Pickling of metal strip and cleaning of metal strip on the Pickling Line, Continuous Annealing Line, Continuous Annealing Process Line, Cleaning Line, No.4 Electrolytic Chromium Coated Steel Line and the No.5 and 6 Electrolytic Tinning Lines.
	Pickling Line, the Continuous Annealing Line, the Continuous Annealing Process Line, the Cleaning Line, the No.4 Electrolytic Chromium Coated Steel Line and the No.5 and 6 Electrolytic Tinning Line tanks only.

	Section 1.1 Part A(1)(a) – Burning any fuel in an appliance with a rated thermal input of 50 Megawatts or more.
	Natural gas combustion in the Continuous Annealing Line, Continuous Annealing Process Line, and the Batch Annealing Line. Natural gas combustion with back-up fuel of heavy fuel oil in the Boiler House.
	Continuous Annealing Line furnaces, Continuous Annealing Process Line furnaces, Batch Annealing Line furnaces and the Boiler Plant House boilers only.

	Section 2.2 Part A(1)(b) – Melting, including making alloys of non-ferrous metals, including recovered products [refining, foundry casting etc] where –

(i) the plant has a melting capacity of more than 4 tonnes/day for lead or cadmium, or 20 tonnes/day for all other metals; and

(ii) any furnace, bath or other holding vessel used in the plant for the melting has a design holding capacity of 5 tonnes or more
	Annealing processes in the Continuous Annealing Line, the Continuous Annealing Process Line and the Batch Annealing Line.
	The Continuous Annealing Line furnaces, the Continuous Annealing Process Line furnaces and the Batch Annealing Line furnaces only.

	Directly Associated Activity 
	Treatment and disposal of non-hazardous wastes by physico-chemical methods.
	Effluent Treatment Plant only

	Directly Associated Activity 
	Cold rolling of steel strip
	Cold rolling / reversing mills only

	Directly Associated Activity 
	Discharge of treated effluent
	Discharge to Loughor Estuary from point W1 only

	Directly Associated Activity
	Collection, segregation, temporary storage and temporary storage pending off-site disposal of waste.
	Dedicated waste handling, storage and disposal areas within installation boundary


1.2
Site 

1.2.1
The activities authorised under condition 1.1.1 shall not extend beyond the Site, being the land shown edged in green on the Site Plan at Schedule 5 to this Permit.

1.3
Overarching Management Condition

1.3.1
Without prejudice to the other conditions of this Permit, the Operator shall implement and maintain a management system, organisational structure and allocate resources that are sufficient to achieve compliance with the limits and conditions of this Permit.

1.4
Improvement Programme

1.4.1
The Operator shall complete the improvements specified in Table 1.4.1 by the date specified in that table, and shall send written notification of the date of completion of each requirement to the Agency within 14 days of the completion of each such requirement.

	Table 1.4.1: Improvement programme

	Reference
	Requirement
	Date

	IC1
	Undertake an assessment of existing leakage detection and control measures. If this identifies any improvements needed to meet BAT, provide the Agency with a timetable detailing the proposed completion date for these works.
	30/09/05

	IC2
	Undertake an assessment into the feasibility of substituting the chromium VI electrolyte within the Electrolytic Chromium Coated Steel Line [Line 4] for a less toxic alternative. If this is not possible due to the nature of the process, undertake an assessment into the reduction in usage of this electrolyte via the use of porous pot methods. Provide a written report to the Agency on this assessment, to include a timetable for undertaking any recommendations necessary to meet BAT.
	31/12/05

	IC3
	Undertake an assessment into the future use of ion-exchange technology within Lines 4 [Electrolytic Chromium Coated Steel Plating] and 5 and 6 [Electrolytic Tinning Lines.] If any improvements are identified which are necessary to meet BAT, provide the Agency with a report into this assessment, containing a timetable detailing the proposed completion date for these works.
	31/03/06

	IC4
	Undertake an assessment into the recycling or recovery of spent pickling liquors from Lines 4, 5 and 6. This shall include the use of these liquors within the Effluent Treatment Plant for neutralisation purposes. If any improvements are identified which are necessary to meet BAT, provide the Agency with a timetable detailing the proposed completion date for these works.
	30/09/05

	IC5
	Assess compliance with the Oil Storage Regulations 2001. Submit a report detailing the results of this assessment. If any required works are identified which are needed to secure compliance, then include a timetable of proposed works in the report to the Agency. 
	31/09/05

	IC6
	Assess the current NOx emissions from the existing Boiler Plant against the cost [and predicted NOx reductions] of retrofitting new low NOx burners to the existing plant.
	31/12/05

	IC7
	Undertake an assessment to establish the efficiency of the Effluent Treatment Plant and ancillary plant and equipment. If the assessment identifies any improvements necessary to ensure that the operation of the ETP is optimised, provide the Agency with a timetable detailing the proposed completion date for these improvements.
	31/12/05


	IC8
	Undertake an assessment on the current usage of phenolsulphonic acid within the installation. This shall include a study into the feasibility of substituting this material for an alternative having a lower environmental impact. If the assessment does not identify an alternative to the use of this material, recommendations for reducing the usage of this material, and the concentration of phenols in the final effluent shall be made. Any recommendations or proposed improvements necessary to meet BAT should be provided to the Agency in the form of a written report, containing a timetable detailing the proposed completion date for these improvements.
	31/12/05

	IC9
	Undertake an assessment into the possibility of re-using treated effluent within the process, in order to minimise water usage. If this assessment identifies any improvements necessary to secure BAT, provide the Agency with a timetable detailing the proposed completion date for these improvements.
	31/12/05

	IC10
	Undertake an assessment of the noise impact of the installation in accordance with the following requirements :-

i.) Provide a 1/3 octave frequency spectra for identified key items of plant and equipment having a significant external noise impact at a given distance. 

ii.) Measure the ambient noise levels [expressed as dB(A), LA90] at suitable noise-sensitive receptors (in prior agreement with the Agency) with the plant operating. 

iii.) Measure the specific noise levels [expressed as dB(A), LAeq]  at suitable noise-sensitive receptors (in prior agreement with the Agency), with the plant operating. 

iv.) Using the measurements obtained from iii.) and iv) above, compare these to the background noise levels provided in support of the PPC Application. Measurements and comparison are to be made in accordance with the relevant parts of BS 4142 :1997 ‘Method for rating industrial noise affecting mixed residential and industrial areas’.  The definitions of terms used above, together with details of the information to be reported can also be found in BS4142:1997. 

v.) Report the results of the above comparison as a difference between rating level and background level, as outlined in BS4142:1997. Using this comparison, identify whether or not the operation of the installation represents BAT as regards noise impact on the adjacent noise sensitive receptors. 

If the operation of the installation does not represent BAT, provide the Agency with suitable proposals to ensure that noise from the installation is attenuated at the noise sensitive receptors in order to meet BAT.
	31/06/06

	IC11
	The Operator shall provide a report in writing to the Agency detailing the monitoring method used to determine effluent flow at W1. This report shall also demonstrate whether the flow meter used for continuous monitoring of flow at W1 meets the requirements given in the MCERTs document ‘Continuous water monitoring equipment part 3: Performance Standards for water flow meters version 1, February 2003’.  The report shall include an assessment of the flow meters performance with the criteria given in the standard, and where these are not met, proposals and time scales required to achieve the standard. The monitoring method shall be agreed in writing, along with any proposals and associated time-scales.
	30/06/05

	IC12
	The Operator shall assess the current method for effluent flow with the requirements given in the MCERTs standard ‘Minimum requirements for the self-monitoring of effluent flow’ version 2, Aug 2004.  A written report shall be provided to the Agency detailing how this is to be achieved and shall include timescales for implementation.
	30/12/06

	IC13
	Undertake an assessment into the feasibility of installing a real-time detector for the analysis of chromium levels in the incoming flume to the Effluent Treatment Plant, and report on the findings to the Agency in writing. If a method is found which represents BAT, provide the Agency with a timetable for undertaking the necessary works to include this method within the normal operation of the installation.
	30/09/05

	IC14
	Undertake an assessment to establish the relationship between releases of phenolsulphonic acid and total phenols from release point W1, having regard to Table 2.10.1 of this permit. This assessment shall indicate the release profile of total phenols.
	31/12/06

	IC15
	The Operator will submit a report on any proposed future significant increase in production and therefore emissions from the installation [in particular release points A6 and A7.] This shall have regard to the standards set out within Agency guidance TGN IPPC S2.04, and include an environmental impact assessment using Agency guidance TGN IPPC H1 or equivalent.
	31/12/05


1.4.2
Where the Operator fails to comply with any requirement by the date specified in Table 1.4.1 the Operator shall send written notification of such failure to the Agency within 14 days of such date.

1.5
Minor Operational Changes

1.5.1
The Operator shall seek the Agency’s written agreement to any minor operational changes under condition 2.1.1 of this Permit by sending to the Agency: written notice of the details of the proposed change including an assessment of its possible effects (including waste production) on risks to the environment from the Permitted Installation; any relevant supporting assessments and drawings; and the proposed implementation date.
1.5.2
Any such change shall not be implemented until agreed in writing by the Agency.  As from the agreed implementation date, the Operator shall operate the Permitted Installation in accordance with that change, and relevant provisions in the Application shall be deemed to be amended.

1.5.3
When the qualification “unless otherwise agreed in writing” is used elsewhere in this Permit, the Operator shall seek such agreement by sending to the Agency written notice of the details of the proposed method(s) or techniques.

1.5.4
Any such method(s) or techniques shall not be implemented until agreed in writing by the Agency.  As from the agreed implementation date, the Operator shall operate the Permitted Installation using that method or technique, and relevant provisions in the Application (and the Site Protection and Monitoring Programme, as the case may be) shall be deemed to be amended.

1.6
Pre-Operational Conditions

1.6.1
There are no pre-operational conditions 

1.7
Off-site Conditions

1.7.1
There are no off-site conditions

2 Operating conditions

2.1
In-Process Controls

2.1.1
The Permitted Installation shall, subject to the conditions of this Permit, be operated using the techniques and in the manner described in the documentation specified in Table 2.1.1, or as otherwise agreed in writing by the Agency in accordance with conditions 1.5.1 and 1.5.2 of this Permit.

	
	Table 2.1.1: Operating techniques

	Description
	Parts
	Date Received

	Application
	1.Proposed activities and abatement

Sections 2.1.1 to 2.2.5 in application document and associated diagrams and plans.
	29/07/04

	
	2. Management techniques

Sections 2.3.1 to 2.3.17 in application document.
	29/07/04

	
	3. Monitoring

Sections 2.10.1 to 2.10.7 in application document.
	29/07/04


2.1.2
The Permitted Installation shall, subject to the other conditions of this Permit, be operated using the techniques and in the manner described in the Site Protection and Monitoring Programme submitted under condition 4.1.7 of this Permit (as amended from time to time under this condition), or as otherwise agreed in writing by the Agency.
2.2
Emissions 

2.2.1
Emissions to Air, (including heat, but excluding Odour, Noise or Vibration) from Specified Points 

2.2.1.1
This Part 2.2.1 of this Permit shall not apply to releases of odour, noise or vibration.

2.2.1.2
Emissions to air from the emission points in Table 2.2.1 shall only arise from the source(s) specified in that Table.

	Table 2.2.1 : Emission points to air

	Emission point reference or description
	Source
	Location of emission point

	A1
	Scalemaster Stack
	Point A1 on site plan[1]

	A2
	Acid fume Stack
	Point A2 on site plan[1]

	A3
	Main fume exhaust, 5 Stand CRM
	Point A3 on site plan[1]

	A4
	Auxiliary fume exhaust, 5 Stand CRM
	Point A4 on site plan[1]

	A5
	Caustic fume exhaust, Continuous Annealing Product Line
	Point A5 on site plan[1]

	A6
	Furnace stack, Continuous Annealing Product Line
	Point A6 on site plan[1]

	A7
	Furnace stack, Continuous Annealing Line
	Point A7 on site plan[1]

	A8
	Batch annealing stack [East]
	Point A8 on site plan[1]

	A9
	Batch annealing stack [West]
	Point A9 on site plan[1]

	A10
	Temper Mill stack
	Point A10 on site plan[1]

	A11
	Main fume exhaust, Double Reduction Mill
	Point A11 on site plan[1]

	A12
	ETL5  process stack
	Point A12 on site plan[1]

	A13
	ECCS 4 process stack
	Point A13 on site plan[1]

	A14
	Caustic fume exhaust
	Point A14 on site plan[1]

	A15
	Cleaning Line Stack
	Point A15 on site plan[1]

	A16
	Boiler House East Stack
	Point A16 on site plan[1]

	A17
	Boiler House West Stack
	Point A17 on site plan[1]

	A18
	Cooling Tower
	Point A18 on site plan[1]

	A19
	ETL6 process stack
	Point A19 on site plan[1]

	A20
	ETL6 pre-treatment process stack
	Point A20 on site plan[1]

	A21
	ECCS North Wall Vent
	Point A21 on site plan[1]

	A22
	ETL6 Chem-treat process stack/ECCS 4 chromium stack.
	Point A22 on site plan[1]

	A23
	ECCS 4/pickler recirculation stack
	Point A23 on site plan[1]


[1] Site plan referred to is Plan Ref: T87124, dated 27-02-0, included in Section 2.2.1 of the Application.

2.2.1.3
The limits for emissions to air for the parameter(s) and emission point(s) set out in Table 2.2.2 shall not be exceeded. 

	Table 2.2.2 : Emission limits to air and monitoring 

	Emission point reference
	Parameter 
	Limit (including Reference Period)[1]
	Monitoring frequency
	Monitoring method

	A6
	Oxides of nitrogen as NO2
	275 mg/m3 as an hourly average
	Quarterly
	ISO 10849

	A7
	Oxides of nitrogen as NO2
	275 mg/m3 as an hourly average
	Quarterly
	ISO 10849

	A16
	Sulphur dioxide [Quarterly average] [2]
	1250 mg/m3 as an hourly average
	Quarterly
	ISO 7935:1992

	
	Sulphur dioxide [Maximum] [2]
	1700 mg/m3 as an hourly average
	Quarterly
	ISO 7935:1992

	
	Oxides of nitrogen[3]  as NO2
	450 mg/m3 as an hourly average
	Quarterly
	ISO 10849

	
	Particulates
	100 mg/m3 as an hourly average
	Quarterly
	BS EN 13284-1:2002

	A17
	Sulphur dioxide [Quarterly average] [2]
	1500 mg/m3 as an hourly average
	Quarterly
	ISO 7935:1992

	
	Sulphur dioxide [Maximum] [2]
	1700 mg/m3 as an hourly average
	Quarterly
	ISO 7935:1992

	
	Oxides of nitrogen[3] as NO2
	450 mg/m3 as an hourly average
	Quarterly
	ISO 10849

	
	Particulates
	100 mg/m3 as an hourly average
	Quarterly
	BS EN 13284-1:2002


Note 1: See Section 6 for reference conditions

Note 2: refers to limits for firing on heavy fuel oil only

Note 3: refers to limits for firing on natural gas only

2.2.1.4
No condition applies. 

2.2.2
Emissions to water (other than groundwater), including heat, from specified points 

2.2.2.1 This Part 2.2.2 of this Permit shall not apply to releases of odour, noise or vibration or to releases to groundwater.

2.2.2.2
Conditions 2.2.2.3 - 2.2.2.6 shall not apply to emissions to sewer.

2.2.2.3
Emissions to water from the emission point(s) specified in Table 2.2.4 shall only arise from the source(s) specified in that Table

	Table 2.2.4: Emission point to water

	Emission Point Reference or description
	Source
	Receiving Water

	W1 on plan ref. D67037 in application
	Process effluent discharge from effluent treatment plant
	Loughor Estuary at NGR SS 5237 9827

	W2 on plan ref. D67037 in application
	Uncontaminated surface water, East storm water drain
	River Loughor at NGR SS5266 9905

	W3 on plan ref. D67037 in application
	Uncontaminated surface water, West storm water drain
	River Loughor at NGR SS5262 9906


2.2.2.4
The limits for the emissions to water for the parameter(s) and emission point(s) set out in Table 2.2.5 shall not be exceeded. 

2.2.2.5
Where a substance is specified in Table 2.2.5 but no limit is set for it, the concentration of such substance in emissions to water from the relevant emission point shall be no greater than the background concentration

	Table 2.2.5 : Emission limits to water and monitoring

	Emission point reference
	Parameter
	Limit (including Reference Period)
	Monitoring frequency
	Monitoring method[2]

	W1
	Flow
	190 litres/second, as daily average.
	Continuous, reported monthly
	To commence on completion of IC11

	
	Temperature[1]
	35oC, continuous as daily average.
	Continuous, reported monthly
	None specified

	
	pH
	5-10, continuous as daily average.
	Daily average, reported monthly
	BS6068-2.50:1995,ISO 10523:1984 

	
	Suspended Solids
	100mg/l
	3 x daily
	BS EN 872:1996, BS 6068-2.54:1996 

	
	Oil and grease
	15mg/l
	3 x daily
	SCA Blue Book 77.  ISBN 0117517283

	
	Phenolsulphonic Acid
	100mg/l
	3 x daily
	To be agreed in further discussion with Agency.

	
	Dissolved iron
	60mg/l
	3 x daily
	BS ISO 17294-2:2003 BS6068-2.89:2003

	
	Total chromium
	1mg/l
	3 x daily
	BS ISO 17294-2:2003 BS6068-2.89:2003

	
	Mercury
	0.005mg/l
	Monthly
	Compliance based on  mass balance calculation (see condition 6.11)

	
	Cadmium
	0.01mg/l
	Monthly
	Compliance based on  mass balance calculation (see condition 6.11)


Note 1: The operator shall submit a method for temperature monitoring that shall be agreed with the Agency

Note 2: The stated methods will apply from 01/01/06. Prior to this time, existing methods [as previously used to monitor these parameters under Authorisation Ref: AF7789/BQ3380] will be used.  Other EN, ISO, BS or SCA Blue Book methods may be used as agreed in writing with the Agency. 

2.2.2.6
Total emissions to water in any year of a substance listed in Table 2.2.6 shall not exceed the relevant limit in that Table

	Table 2.2.6 Annual emission limits

	Substance
	Limit – kg (Compliance based on mass balance calculation)[1]

	Mercury
	40

	 Cadmium
	40



Note 1 – See condition 6.1.1

Emissions to sewer

2.2.2.7
There are no specific controls imposed on emissions to sewer in this Part of the Permit.
2.2.2.8
No condition applies.

2.2.2.9
No condition applies.
2.2.2.10 No condition applies.

2.2.3
Emissions to groundwater 

2.2.3.1
No emission from the Permitted Installation shall give rise to the introduction into groundwater of any substance in List I  (as defined in the Groundwater Regulations 1998 (S.I. 1998 No. 2746)).

2.2.3.2
No emission from within the Permitted Installation shall give rise to the introduction into groundwater of any substance in List II (as defined in the Groundwater Regulations 1998 (S.I. 1998 No. 2746)) so as to cause pollution (as defined in the Groundwater Regulations 1998 (S.I. 1998 No. 2746)).

2.2.3.3
For substances other than those in List I or II (as defined in the Groundwater Regulations 1998 (SI 1998 No.2746)), the Operator shall use BAT to prevent or where that is not practicable to reduce emissions to groundwater from the Permitted Installation provided always that the techniques used by the Operator shall be no less effective than those described in the Application.

2.2.4
Fugitive emissions of substances to air 

2.2.4.1
The Operator shall use BAT so as to prevent or where that is not practicable to reduce fugitive emissions of substances to air from the Permitted Installation in particular from:

· storage areas

· buildings

· pipes, valves and other transfer systems

· open surfaces
provided always that the techniques used by the Operator shall be no less effective than those described in the Application, where relevant.

2.2.5
Fugitive emissions of substances to water and sewer

2.2.5.1
Subject to condition 2.2.5.2 below, the Operator shall use BAT so as to prevent or where that is not practicable to reduce fugitive emissions of substances to water (other than Groundwater) and sewer from the Permitted Installation in particular from:

· all structures under or over ground

· surfacing

· bunding

· storage areas

provided always that the techniques used by the Operator shall be no less effective than those described in the Application, where relevant.

2.2.5.2
There shall be no release to water that would cause a breach of an EQS established by the UK Government to implement the Dangerous Substances Directive 76/464/EEC.

2.2.6
Odour

2.2.6.1
The Operator shall use BAT so as to prevent or where that is not practicable to reduce odorous emissions from the Permitted Installation, in particular by:

· limiting the use of odorous materials 

· restricting odorous activities

· controlling the storage conditions of odorous materials

· controlling processing parameters to minimise the generation of odour

· optimising the performance of abatement systems 

· timely monitoring, inspection and maintenance

· employing, where appropriate, an approved odour management plan

provided always that the techniques used by the Operator shall be no less effective than those described in the Application, where relevant.

2.2.6.2 No condition applies.

2.2.6.3 No condition applies.
2.2.7
Emissions to Land

2.2.7.1
This Part 2.2.7 of this Permit shall not apply to emissions to groundwater.

2.2.7.2 No emission from the Permitted installation shall be made to land. 

2.2.7.3 No condition applies.

2.3
Management 

2.3.1
A copy of this Permit and those parts of the application referred to in this Permit shall be available, at all times, for reference by all staff carrying out work subject to the requirements of the Permit.

Training

2.3.2
The Permitted Installation shall be supervised by staff who are suitably trained and fully conversant with the requirements of this Permit. 

2.3.3
All staff shall be fully conversant with those aspects of the Permit conditions which are relevant to their duties and shall be provided with adequate professional technical development and training and written operating instructions to enable them to carry out their duties.

2.3.4
The Operator shall maintain a record of the skills and training requirements for all staff whose tasks in relation to the Permitted Installation may have an impact on the environment and shall keep records of all relevant training.

Maintenance
2.3.5
All plant and equipment used in operating the Permitted Installation, the failure of which could lead to an adverse impact on the environment, shall be maintained in good operating condition.

2.3.6
The Operator shall maintain a record of relevant plant and equipment covered by condition 2.3.5 and for such plant and equipment:
2.3.6.1
a written or electronic maintenance programme; and
2.3.6.2
records of its maintenance.

Incidents and Complaints
2.3.7
The Operator shall maintain and implement written procedures for:

2.3.7.1
taking prompt remedial action, investigating and reporting actual or potential non-compliance with operating procedures or emission limits and if such event occur;
2.3.7.2
investigating incidents, (including any malfunction, breakdown or failure of plant, equipment or techniques, down time, any short term and long term remedial measures and near misses) and prompt implementation of appropriate actions; and
2.3.7.3
ensuring that detailed records are made of all such actions and investigations. 
2.3.8 The Operator shall record and investigate complaints concerning the Permitted Installation’s effects or alleged effects on the environment.  The record shall give the date and nature of complaint, time of complaint, name of complainant (if given), a summary of any investigation and the results of such investigation and any actions taken.

2.3.9 No condition applies.

2.4
Efficient use of raw materials

2.4.1
The Operator shall - 

2.4.1.1
maintain the raw materials table or description submitted in response to Section 2.4 of the Application and in particular consider on a periodic basis whether there are suitable alternative materials to reduce environmental impact; 

2.4.1.2
carry out periodic waste minimisation audits and water use efficiency audits.  If such an audit has not been carried out in the 2 years prior to the issue of this Permit, then the first such audit shall take place within 2 years of its issue.  The methodology used and an action plan for increasing the efficiency of the use of raw materials or water shall be submitted to the Agency within 2 months of completion of each such audit and a review of the audit and a description of progress made against the action plan shall be submitted to the Agency at least every 4 years thereafter; and

2.4.1.3
ensure that incoming water use is directly measured and recorded.
2.5
Waste Storage and Handling

2.5.1 The Operator shall design, maintain and operate all facilities for the storage and handling of waste on the Permitted installation such that there are no releases to water or land during normal operation and that emissions to air and the risk of accidental release to water or land are minimised.

2.5.2 The Operator shall use BAT so as to prevent or where that is not practicable to reduce emissions of litter from the Permitted Installation provided always that the techniques used by the Operator shall be no less effective than those described in the Application, where relevant.
2.6 Waste recovery or disposal

2.6.1 Waste produced at the Permitted Installation shall be: 

2.6.1.1 recovered  to no lesser extent than described in  the Application; and 
2.6.1.2 where not recovered,  disposed of while avoiding or reducing any impacts on the environment provided always that this is not done in any way that would have a greater effect on the environment than that  described in  the Application.
2.6.2 The Operator shall maintain the waste recovery or disposal table or description submitted in response to Section 2.6 of the Application and in particular review the available options for waste recovery and disposal for the purposes of complying with condition 2.6.1 above. 

2.6.3 The Operator shall maintain and implement a system which ensures that a record is made of the quantity, composition, origin, destination (including whether this is a recovery or disposal operation) and where relevant removal date of any waste that is produced at the Permitted Installation.

2.6.4 No condition applies.

2.7
Energy Efficiency

2.7.1
The Operator shall produce a report on the energy consumed at the Permitted Installation over the previous calendar year, by 31 January each year, providing the information required by condition 4.1.2.

2.7.2
The Operator shall maintain and update annually an energy management system which shall include, in particular, the monitoring of energy flows and targeting of areas for improving energy efficiency.

2.7.3
The Operator shall design, maintain and operate the Permitted Installation so as to secure energy efficiency, taking into account relevant guidance including the Agency’s Energy Efficiency Horizontal Guidance Note as from time to time amended. Energy efficiency shall be secured in particular by:

· ensuring that the appropriate operating and maintenance systems are in place;

· ensuring that all plant is adequately insulated to minimise energy loss or gain;

· ensuring that all appropriate containment methods, (e.g. seals and self-closing doors) are employed and maintained to minimise energy loss;

· employing appropriate basic controls, such as simple sensors and timers, to avoid unnecessary discharge of heated water or air; 

· where building services constitute more than 5% of the total energy consumption of the installation, identifying and employing the appropriate energy efficiency techniques for building services, having regard in particular to the Building services part of the Agency’s Energy Efficiency Horizontal Guidance Note H2; and

maintaining and implementing an energy efficiency plan which identifies energy saving techniques that are applicable to the activities and their associated environmental benefit and prioritises them, having regard to the appraisal method in the Agency’s Energy Efficiency Horizontal Guidance Note H2.

2.8
Accident prevention and control

2.8.1
The Operator shall maintain and implement when necessary the accident management plan submitted or described in response to Section 2.8 of the Application.  The plan shall be reviewed at least every 2 years or as soon as practicable after an accident, whichever is the earlier, and the Agency notified of the results of the review within 2 months of its completion.

2.9
Noise and Vibration

2.9.1
The Operator shall use BAT so as to prevent or where that is not practicable to reduce emissions of noise and vibration from the Permitted Installation, in particular by: 

· equipment maintenance, eg. of fans, pumps, motors, conveyors and mobile plant;

· use and maintenance of appropriate attenuation, eg. silencers, barriers, enclosures;

· timing and location of noisy activities and vehicle movements; 

· periodic checking of noise emissions, either qualitatively or quantitatively; and

· maintenance of building fabric,
provided always that the techniques used by the Operator shall be no less effective than those described in the Application, where relevant.
2.10
On-site Monitoring 

2.10.1
The Operator shall maintain and implement an emissions monitoring programme which ensures that emissions are monitored from the specified points, for the parameters listed in and to the frequencies and methods described in Tables 2.2.2 and  2.2.5, unless otherwise agreed in writing, and that the results of such monitoring are assessed.  The programme shall ensure that monitoring is carried out under an appropriate range of operating conditions.

2.10.2 The Operator shall carry out environmental or other specified substance monitoring to the frequencies and methods described in Table 2.10.1

	Table 2.10.1 : Other monitoring requirements 

	Emission point reference 
	Substance or parameter
	Monitoring frequency
	Monitoring method
	Other specifications

	W1
	Total Phenol
	Monthly [or as agreed in writing]
	SCA Blue Book 50. ISBN 0117516171
	Sampling to commence on 1/09/2005, and to be undertaken with reference to IC14


2.10.3
No condition applies.  

2.10.4
No condition applies.
2.10.5
The Operator shall notify the Agency at least 14 days in advance of undertaking monitoring and/ or spot sampling, where such notification has been requested in writing by the Agency.

2.10.6
The Operator shall maintain records of all monitoring taken or carried out (this includes records of the taking and analysis of samples instrument measurements (periodic and continual), calibrations, examinations, tests and surveys) and any assessment or evaluation made on the basis of such data.

2.10.7
Monitoring equipment, techniques, personnel and organisations employed for the emissions monitoring programme in condition 2.10.1 of this Permit shall have either MCERTS certification or MCERTS accreditation (as appropriate) unless otherwise agreed in writing.

2.10.8
There shall be provided:

2.10.8.1
safe and permanent means of access to enable sampling/monitoring to be carried out in relation to the emission points specified in Schedule 2 to this Permit, unless otherwise specified in that Schedule; and

2.10.8.2
safe means of access to other sampling/monitoring points when required by the Agency.

2.10.9 The Operator shall carry out the on-going monitoring identified in the Site Protection and Monitoring Programme submitted under condition 4.1.7, unless otherwise agreed in writing by the Agency.

2.10.10 No condition applies.

2.11
Closure and Decommissioning

2.11.1
The Operator shall maintain and operate the Permitted Installation so as to prevent or minimise any pollution risk, including the generation of waste, on closure and decommissioning in particular by:- 

2.11.1.1
attention to the design of new plant or equipment;

2.11.1.2
the maintenance of a record of any events which have, or might have, impacted on the condition of the site along with any further investigation or remediation work carried out; and

2.11.1.3
the maintenance of a site closure plan to demonstrate that the installation can be decommissioned avoiding any pollution risk and returning the site of operation to a satisfactory state.

2.11.2
Notwithstanding condition 2.11.1 of this Permit, the Operator shall carry out a full review of the Site Closure Plan at least every 4 years.

2.11.3
The site closure plan shall be implemented on final cessation or decommissioning of the Permitted activities or part thereof.
2.11.4
The Operator shall give at least 30 days written notice to the Agency before implementing the site closure plan.
2.12
Multiple Operator installations

2.12.1
This is not a multi-Operator installation

2.13
Transfer to effluent treatment plant

2.13.1
No transfers to effluent treatment plant are controlled under this part of this Permit.

3 Records

3.1
The Operator shall ensure that all records required to be made by this Permit and any other records made by it in relation to the operation of the Permitted Installation shall:-

3.1.1
be made available for inspection by the Agency at any reasonable time;

3.1.2
be supplied to the Agency on demand and without charge;

3.1.3
be legible;

3.1.4
be made as soon as reasonably practicable;

3.1.5
indicate any amendments which have been made and shall include the original record wherever possible; 

3.1.6
be retained at the Permitted Installation, or other location agreed by the Agency in writing, for a minimum period of 4 years from the date when the records were made, unless otherwise agreed in writing; and 

3.1.7
where they concern the condition of the site of the Installation or are related to the implementation of the Site Protection and Monitoring Programme, be kept at the Permitted Installation, or other location agreed by the Agency in writing, until all parts of the Permit have been surrendered.

4 Reporting

4.1.1
All reports and written and or oral notifications required by this Permit and notifications required by Regulation 16 of the PPC Regulations shall be made or sent to the Agency using the contact details notified in writing to the Operator by the Agency.

4.1.2
The Operator shall, unless otherwise agreed in writing, submit reports of the monitoring and assessment carried out in accordance with the conditions of this permit, as follows:-

4.1.2.1
in respect of the parameters and emission points specified in Table S2 to Schedule 2;

4.1.2.2
for the reporting periods specified in Table S2 to Schedule 2 and using the forms specified in Table S3 to Schedule 3;

4.1.2.3
giving the information from such results and assessments as may be required by the forms specified in those Tables; and

4.1.2.4
to the Agency within 28 days of the end of the reporting period.

4.1.3
The Operator shall submit to the Agency a report on the performance of the Permitted Installation over the previous year, by 31 January each year, providing the information listed in Tables S4.1 and S4.2 of Schedule 4, assessed at any frequency specified therein, and using the form specified in Table S3 to Schedule 3.

4.1.4
The Operator shall review fugitive emissions, having regard to the application of Best Available Techniques, on an annual basis, or such other period as shall be agreed in writing by the Agency, and a summary report on this review shall be sent to the Agency detailing such releases and the measures taken to reduce them within 3 months of the end of such period.

4.1.5
Where the Operator has a formal environmental management system applying to the Permitted Installation which encompasses annual improvement targets the Operator shall, not later than 31 January in each year, provide a summary report of the previous year’s progress against such targets.

4.1.6
The Operator shall, within 6 months of receipt of written notice from the Agency, submit to the Agency a report assessing whether all appropriate preventive measures continue to be taken against pollution, in particular through the application of the best available techniques, at the installation. The report shall consider any relevant published technical guidance current at the time of the notice which is either supplied with or referred to in the notice, and shall assess the costs and benefits of applying techniques described in that guidance, or otherwise identified by the Operator, that may provide environmental improvement.

4.1.7
The Operator shall, within two months of the date of this permit, submit a detailed Site Protection and Monitoring Programme, in accordance with and using the appropriate template format given in the Land Protection Guidance. The Operator shall implement and maintain the Site Protection and Monitoring Programme (SPMP) submitted under this condition, and shall undertake regular reviews of it at a minimum frequency of every 2 years.  The results of such reviews and any changes made to the SPMP shall be reported to the Agency within 1 month of the review or change.
5 Notifications

5.1.1
The Operator shall notify the Agency without delay of:-

5.1.1.1
the detection of an emission of any substance which exceeds any limit or criterion in this Permit specified in relation to the substance;

5.1.1.2
the detection of any fugitive emission which has caused, is causing or may cause significant pollution;

5.1.1.3
the detection of any malfunction, breakdown or failure of plant or techniques which has caused, is causing or has the potential to cause significant pollution; and

5.1.1.4
any accident which has caused, is causing or has the potential to cause significant pollution.

5.1.2
The Operator shall submit written confirmation to the Agency of any notification under condition 5.1.1, by sending:-

5.1.2.1
the information listed in Part A of Schedule 1 to this Permit within 24 hours of such notification; and

5.1.2.2
the more detailed information listed in Part B of that Schedule as soon as practicable thereafter;

and such information shall be in accordance with that Schedule.

5.1.3
The Operator shall give written notification as soon as practicable prior to any of the following:-

5.1.3.1
permanent cessation of the operation of part or all of the Permitted Installation;

5.1.3.2
cessation of operation of part or all of the Permitted Installation for a period likely to exceed 1 year; and

5.1.3.3
resumption of the operation of part or all of the Permitted Installation after a cessation notified under condition 5.1.3.2.

5.1.4
The Operator shall notify the Agency, as soon as reasonably practicable, of any information concerning the state of the Site which adds to that provided to the Agency as part of the Application or to that in the Site Protection and Monitoring Programme submitted under condition 4.1.7 of this Permit.

5.1.5
The Operator shall notify the following matters to the Agency in writing within 14 days of their occurrence:- 

5.1.5.1
where the Operator is a registered company:-

· any change in the Operator’s trading name, registered name or registered office address;

· any change to particulars of the Operator’s ultimate holding company (including details of an ultimate holding company where an Operator has become a subsidiary)

· any steps taken with a view to the Operator going into administration, entering into a company voluntary arrangement or being wound up;

5.1.5.2
where the Operator is a corporate body other than a registered company:

· any change in the Operator’s name or address;

· any steps taken with a view to the dissolution of the Operator.

5.1.5.3
In any other case: -

· the death of any of the named Operators (where the Operator consists of more than one named individual);

· any change in the Operator’s name(s) or address(es);

· any steps taken with a view to the Operator, or any one of them, going into bankruptcy, entering into a composition or arrangement with creditors, or, in the case them being in a partnership, dissolving the partnership;

5.1.6
Where the Operator has entered into a Climate Change Agreement with the Government, the Operator shall notify the Agency within one month of:-

5.1.6.1
a decision by the Secretary of State not to re-certify that Agreement.

5.1.6.2
a decision by either the Operator or the Secretary of State to terminate that agreement.

5.1.6.3
any subsequent decision by the Secretary of State to re-certify such an Agreement.

5.1.7
Where the Operator has entered into a Direct Participant Agreement in the Emissions Trading Scheme which covers emissions relating to the energy consumption of the activities, the Operator shall notify the Agency within one month of:-

5.1.7.1
a decision by the Operator to withdraw from or the Secretary of State to terminate that agreement.

5.1.7.2
a failure to comply with an annual target under that Agreement at the end of the trading compliance period.

5.1.8
The Operator shall notify the Agency in writing, of any known or planned introduction or material emission from the permitted installation to sewer, that may increase the concentration of any "dangerous substance", as defined in List I and List II of the Dangerous Substances Directive, 76/464/EEC, and its daughter directives.

6 Interpretation

6.1.1
In this Permit, the following expressions shall have the following meanings:-

“Application” means the application for this Permit, together with any response to a notice served under Schedule 4 to the PPC Regulations and any operational change agreed under the conditions of this Permit. 
"background concentration” means such concentration of that substance as is present in: 
· water supplied to the site; or
· where more than 50% of the water used at the site is directly abstracted from ground or surface water on site, the abstracted water;  or 

· where the Permitted Installation uses no significant amount of supplied or abstracted water, the precipitation on to the site.
“BAT”  means best available techniques means the most effective and advanced stage of development of activities and their methods of operation which indicates the practical suitability of particular techniques to prevent and where that is not practicable to reduce emissions and the impact on the environment as a whole.  For these purposes:  “available techniques” means “those techniques which have been developed on a scale which allows implementation in the relevant industrial sector, under economically and technically viable conditions, taking into consideration the cost and advantages, whether or not the techniques are used or produced inside the United Kingdom, as long as they are reasonably accessible to the operator”; “best” means “in relation to techniques, the most effective in achieving a high general level of protection of the environment as a whole” and “techniques” “includes both the technology used and the way in which the installation is designed, built, maintained, operated and decommissioned.” . In addition, Schedule 2 of the PPC Regulations has effect in relation to the determination of BAT.

‘Compliance based on Mass Balance Calculation’ means that for the purposes of demonstrating compliance or non-compliance with a specified limit the release shall be calculated. Annual mass releases for mercury and cadmium shall be calculated from the maximum potential concentration of the metal present as contamination multiplied by the volume of the chemicals used on site during the Year. An allowance may be deducted for any proportion of the chemicals used that can be demonstrated not to have reached the emission point. The concentration of mercury and cadmium shall be calculated from the annual mass release and the volume of effluent discharged during the Year.

“Fugitive emission” means an emission to air or water (including sewer) from the Permitted Installation which is not controlled by an emission or background concentration limit under conditions 2.2.1.3, 2.2.2.4, 2.2.2.5, 2.2.2.8 or 2.2.2.9 of this Permit.

“Groundwater” means all water which is below the surface of the ground in the saturation zone and in direct contact with the ground or subsoil.

"Land Protection Guidance" means the version of the Agency guidance note  "H7 - Guidance on the Protection of Land under the PPC Regime: Application Site Report and Site Protection and Monitoring Programme",  including its appended templates for data reporting, which is current at the time of issue of the Permit. 

“LAeq,T” means the equivalent continuous A-weighted sound pressure level in dB determined over time period, T.

“LA90, T” means the A-weighted sound pressure level in dB exceeded for 90% of the time period, T.

“LAFmax” means the maximum A weighted sound level measurement in dB measured with a fast time weighting.

“MCERTS” means the Environment Agency’s Monitoring Certification Scheme.

“Monitoring” includes the taking and analysis of samples, instrumental measurements (periodic and continual), calibrations, examinations, tests and surveys.

“Permitted Installation” means the activities and the limits to those activities described in Table 1.1.1 of this Permit.

“PPC Regulations” means the Pollution, Prevention and Control (England and Wales) Regulations SI 2000 No.1973 (as amended) and words and expressions defined in the PPC Regulations shall have the same meanings when used in this Permit save to the extent they are specifically defined in this Permit.
“Sewer” means sewer within the meaning of section 219(1) of the Water Industry Act 1991. 
“Staff”  includes employees, directors or other officers of the Operator, and any other person under the Operator’s direct or indirect control, including contractors. 

"Year"  means calendar year ending 31 December.

6.1.2
Where a minimum limit is set for any emission parameter, for example pH, reference to exceeding the limit shall mean that the parameter shall not be less than that limit.  

6.1.3
Unless otherwise stated, any references in this Permit to concentrations of substances in emissions into air means:-

6.1.3.1
in relation to gases from combustion processes, the concentration in dry air at a temperature of 273K, at a pressure of 101.3 kPa and with an oxygen content of 3% dry for liquid and gaseous fuels, 6% dry for solid fuels; and/or

6.1.3.2
in relation to gases from non-combustion sources, the concentration at a temperature of 273K and at a pressure of 101.3 kPa, with no correction for water vapour content

6.1.4
Where any condition of this Permit refers to the whole or parts of different documents, in the event of any conflict between the wording of such documents, the wording of the  document(s) with the most recent date shall prevail to the extent of such conflict. 

Schedule 1 - Notification of abnormal emissions

This page outlines the information that the Operator must provide to satisfy conditions 5.1.1 and 5.1.2 of this Permit. 

Units of measurement used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission. Where appropriate, a comparison should be made of actual emissions and authorised emission limits.

If any information is considered commercially confidential, it should be separated from non-confidential information, supplied on a separate sheet and accompanied by an application for commercial confidentiality under the provisions of the PPC Regulations.

Part A 
	Permit Number
	

	Name of Operator
	

	Location of Installation
	

	Location of the emission
	

	Time and date of the emission
	


	Substance(s) emitted
	Media
	Best estimate of the quantity or the rate of emission
	Time during which the emission took place

	
	
	
	

	
	
	
	


	Measures taken, or intended to be taken, to stop the emission
	


Part B
	Any more accurate information on the matters for notification under Part A.
	

	Measures taken, or intended to be taken, to prevent a recurrence of the incident
	

	Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment or harm which has been or may be caused by the emission
	

	The dates of any unauthorised emissions from the installation in the preceding 24 months.
	


	Name*
	

	Post
	

	Signature
	

	Date
	


* authorised to sign on behalf of Corus UK Ltd

Schedule 2 - Reporting of monitoring data

Parameters for which reports shall be made, in accordance with conditions 4.1.2 and 4.1.3 of this Permit, are listed below.

	Table S2: Reporting of monitoring data

	Parameter
	Emission point
	Reporting period
	Period begins
	Method

	Sulphur dioxide, mg m-3 
	A16, A17
	Quarterly
	01/04/2005
	ISO 7935:1992 1]

	Oxides of nitrogen, mg m-3
	A6, A7, A16, A17
	Quarterly
	01/04/2005
	ISO 10849 1]

	Particulates, mg m-3
	A16, A17
	Quarterly
	01/04/2005
	BS EN 13284-1:2002 1]

	Flow, litres/second [daily average of continuous measurement]
	W1
	Monthly
	01/04/2005
	To commence on completion of IC11

	pH, units [daily spot measurements]
	W1
	Monthly
	01/04/2005
	BS6068-2.50:1995,ISO 10523:1984

	Temperature, oC [daily average of continuous measurement]
	W1
	Monthly
	01/04/2005
	None specified

	Suspended solids, mg l-1
	W1
	3 x daily
	01/04/2005
	BS EN 872:1996, BS 6068-2.54:1996 [2]

	Oil and grease, mg l-1
	W1
	3 x daily
	01/04/2005
	SCA Blue Book 77.  ISBN 0117517283 [2]

	Total phenols, mg l-1
	W1
	3 x daily
	01/04/2005
	SCA Blue Book 50. ISBN 0117516171[2]

	Dissolved iron, mg l-1
	W1
	3 x daily
	01/04/2005
	BS ISO 17294-2:2003 BS6068-2.89:2003 [2]

	Total chromium, mg l-1
	W1
	3 x daily
	01/04/2005
	BS ISO 17294-2:2003 BS6068-2.89:2003 [2]

	Mercury, mg l-1
	W1
	Annual
	01/04/2005
	Compliance based on  mass balance calculation (see condition 6.1.1)

	Cadmium, mg l-1
	W1
	Annual 
	01/04/2005
	Compliance based on  mass balance calculation (see condition 6.1.1)

	Waste disposal and/or recovery, tonnes.
	Installation
	Quarterly
	01/04/2005
	By estimation

	Water usage, m3
	Installation
	Quarterly
	01/04/2005
	By estimation

	Energy usage, MW
	Installation
	Quarterly
	01/04/2005
	By estimation


Note 1: Access points for sampling may be fixed rather than permanent if they comply with the requirements of Agency Technical Guidance Note M1.

Note 2: The stated methods will apply from 01/01/06. Prior to this time, existing methods [as used previously to monitor these parameters under Authorisation Ref: AF7789/BQ3380] will be used.  Other EN, ISO, BS or SCA Blue Book methods may be used as agreed in writing with the Agency. 

Schedule 3 - Forms to be used 

	Table S3: Reporting Forms
	
	

	Media / parameter
	Form Number
	Date of Form

	Air
	A1
	24/03/05

	Water (excluding sewer)
	W1
	24/03/05

	Energy
	E1
	24/03/05

	Waste Return
	R1
	24/03/05

	Water usage
	WU1
	24/03/05

	Mass Release to water
	MR1
	24/03/05

	Performance Indicator
	PI1
	24/03/05


Schedule 4 - Reporting of performance data

Data required to be recorded and reported by Condition 4.1.3.  The data should be assessed at the frequency given and reported annually to the Agency.

	Table S4.1: Annual Production/Treatment

	Product
	Production, tonnes

	Tin-plated steel coil
	

	Electrically coated chrome coil
	


	Table S4.2: Performance parameters

	Parameter
	
	Frequency of assessment
	Performance indicator 

	Potable water use
	
	Annually
	m3 used per tonne of product produced

	Energy Use
	
	Annually
	KWh used per tonne of product produced

	Waste Disposed
	
	Annually
	Tonnes produced used per tonne of product produced


Schedule 5 - Site Plan


END OF PERMIT
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