Permit Number: 
EA/EPR/BK3638IF/V002

Operator: 
Hydro Aluminium Limited

Facility:
Wrexham Aluminium Works
Form Number: 
Water1
Reporting of emissions to water (other than to sewer) and land for the period from 01/10/2015 to 31/12/2015
	Emission Point
	Substance / Parameter
	Emission Limit Value
	Reference Period
	Result 
	Test Method 
	Sample Date and Times 
	Uncertainty

	W1
	BOD
	10 mg/l
	Single sample
	Not measured (Note 1)
	
	
	

	W1
	Suspended Solids
	35 mg/l
	Single sample
	23.28
	TM022: Method 2540D, AWWA/APHA, 20th ed, 1999 / BS2690 Part 120 1981; BS EN 872
	17/12/2015, 09:15
	±3%

	W1
	pH
	6 – 9
	Single sample
	7.82
	TM256:determination of pH in water using the GLpH Meter
	17/12/2015, 09:15
	±0.02%

	W1
	COD
	125 mg/l
	Single sample
	18.87
	TM107: ISO6060:1989
	17/12/2015, 09:15
	±1.2%

	W1
	Ammoniacal Nitrogen
	5 mg /l
	Single sample
	<0.2
	TM099: BS2690 Part 7, 1968 / BS6068 Part 2.11, 1984
	17/12/2015, 09:15
	±3.8%

	W1
	Aluminium
	0.5 mg/l
	Single sample
	0.06
	TM152: Method 3125B, AWWA/APHA, 20th ed, 1999
	17/12/2015, 09:15
	±3.8%

	W1
	Total Hydrocarbon Oil
	2 mg/l
	Single sample
	0.63
	TM172: Analysis of petroleum hydrocarbons in environmental media
	17/12/2015, 09:15
	±10.5%

	W1
	Temperature
	25 oC
	Single sample
	18
	Mercury thermometer
	17/12/2015, 09:15
	Not known

	W1
	Flow
	N/A
	-
	-
	Not measured – agreed that water emission volumes can be calculated from cooling water bleed-off and casting pit emptying (CAR I/110329/BK3638).
	-
	-


Signed ……Joel Priest……………………………………………………….  

Date ……………05/01/2016………..

(Authorised to sign as representative of Operator)

Results have been corrected as per condition 3.1.4.
Note 1: Sample was taken when pit water was discharged, however due to the testing laboratory’s Christmas schedule the sample exceeded the holding time for BOD measurement before analysis could be completed in accordance with standard methods, hence a “nil return” for this parameter for this reporting period.
