Permit Number: 
EA/EPR/BK3638IF/V002



Operator: 

Hydro Aluminium Deeside

Facility:

Wrexham Aluminium Processing

Form Number: 
 Air1a 
Reporting of emissions to air for the quarter from 01/04/18 to 30/06/18
	Emission

Point
	Substance /

Parameter
	Emission Limit Value
	Month 1

Maximum Daily average value
	Month 2

Maximum Daily average value
	Month 3

Maximum Daily average value

	A1
	Particulate Matter
	10 mg/m3 

(daily average) 
	0.59
	2.55
	7.76

	A12
	Particulate Matter 
	10 mg/m3 

(daily average)
	0.28
	0.22
	0.21

	A13
	Particulate Matter
	10 mg/m3 

(daily average)
	0.35
	0.38
	0.32


	Emission

Point
	Substance /

Parameter
	Emission Limit Value
	Month 1

Average of daily average values
	Month 2

Average of daily average values
	Month 3

Average of daily average values

	A1
	Particulate Matter
	5 mg/m3

(monthly average)
	0.26
	0.82
	2.84

	A12
	Particulate Matter 
	5 mg/m3

(monthly average)
	0.19
	0.20
	0.20

	A13
	Particulate Matter
	-
	0.21
	0.26
	0.16


Signed ………Joel Priest………………………………………….  

Date……25/07/18……

(Authorised to sign as representative of Operator)

NOTE: While below the current permit limit, results were higher than usual in May-June for Bag Plants 1 & 2. This was traced to leaking filter bags in bag plant 2, which were subsequently removed from use. Average levels in July have returned to more typical levels of <1.0 mg/m3.

Results have been corrected as per condition 3.1.4
