# Natural Resources Wales permitting decisions

# Bespoke permit

We have decided to grant the permit for HMS Cambria operated by Reserve Forces & Cadets Association (Wales).

The application number is PAN-004955

The permit number is BB3296ZM

The discharge is for secondary treated sewage effluent: domestic in nature with a maximum daily volume of 14.6 cubic metres. The effluent is treated via package treatment plant before discharging to Roath Dock. The discharge arises from HMS Cambria Naval training facility.

Permit AN0033407 currently active on the site is to be surrendered upon issue of this permit with all works decommissioned.

We consider in reaching that decision we have taken into account all relevant considerations and legal requirements and that the permit will ensure that the appropriate level of environmental protection is provided.

Purpose of this document

This decision document:

- explains how the application has been determined

- provides a record of the decision-making process

- shows how all relevant factors have been taken into account

- justifies the specific conditions in the permit other than those in our generic permit template.

Unless the decision document specifies otherwise we have accepted the applicant’s proposals.

Structure of this document

- Annex 1 the decision checklist

- Annex 2 the consultation responses

.

# Annex 1: decision checklist

This checklist should be read in conjunction with the Duly Making checklist.

| ### Aspect | ### Justification / Detail | Criteria met |
| --- | --- | --- |
|  |  | Yes |
| Consultation |  |  |  |
| Scope of consultation | The consultation requirements were identified and implemented. The decision was taken in accordance with RGN 6 High Profile Sites, our Public Participation Statement and our Working Together Agreements. |  |
| ### Responses to consultation and web publicising | The consultation responses (Annex 2) were taken into account in the decision. There were no responses to web publicising. The decision was taken in accordance with our guidance. |  |
| Operator |  |  |  |
| Control of the facility | We are satisfied that the applicant (now the operator) is the person who will have control over the operation of the facility after the grant of the permit. The decision was taken in accordance with EPR RGN 1 Understanding the meaning of operator. |  |
| European Directives |  |  |  |
| Applicable directives | All applicable European directives have been considered in the determination of the application. |  |
| The site |  |  |  |
| Extent of the site of the facility | The operator has provided a plan which we consider is satisfactory, showing the extent of the site of the facility including discharge points. A plan is included in the permit and the operator is required to carry on the permitted activities within the site boundary. |  |
| Biodiversity, Heritage, Landscape and Nature Conservation and a designated site under the CRoW Act. | The application is within the relevant distance criteria of a site of heritage, landscape or nature conservation, and/or protected species or habitat . A full assessment of the application and its potential to affect the sites has been carried out as part of the permitting process. We consider that the application will not affect the features of the site. |  |
| Habitat Regulation Assessment for a designated site under the EU Habitats Directive | No FORM 1 completed: HRA is not required because there is no conceivable impact pathway to any Natura 2000/Ramsar site. The discharge is direct to a sealed dock. Water levels in the dock are managed by abstraction from the surrounding rivers with limited outflow to Cardiff Bay and in to the designated site of Severn Estuary. The discharge being of good quality; meeting that of British Standards 12566 as a minimum, combined with high rate of dispersal and dilution within the dock and Cardiff Bay, the discharge will be insignificant when it reaches the designated site in the Severn Estuary. Therefore it can be concluded there is no conceivable impact pathway from the discharge to the protected site of Seven Estuary, and with a high degree of confidence we can conclude there will be no likely significant impacts. Additionally, the Local NRM conservation officer is in agreement stating ‘there will be no likely significant impacts on the relevant statutory designated sites (Severn Estuary SAC, SSSI, RAMSAR) as a result of the proposed arrangements. |  |
| Environmental Risk Assessment and operating techniques |  |  |  |
| Environmental risk | We have carried out a risk assessment on behalf of the operator. The operator considers this risk assessment is satisfactory. The assessment shows that, applying the conservative criteria in our guidance on Environmental Risk Assessment all emissions may be categorised as environmentally insignificant. |  |
| Operating techniques | We have reviewed the techniques used by the operator and compared these with the relevant guidance notes. Measures proposed by the applicant conform to requirements set out in EPR 7.01. The proposed techniques / emission levels for priorities for control are in line with the benchmark levels contained in the TGN and we consider them to represent appropriate techniques for the facility. |  |
| The permit conditions |  |  |  |
| Emission limits | We have decided that emission limits should be set for the parameters listed in the permit. It is considered that the numeric limits described below will prevent significant deterioration of receiving waters. We have imposed numeric limits because either a relevant environmental quality or operational standard requires this. - ATU-BOD as O2 - 20 mg/l - Suspended solids (measured after drying at 105o C) - 30 mg/l - Ammoniacal nitrogen (expressed as N) - 20 mg/l These limits have been set to ensure the discharge quality does not negatively impact the quality of the water within the Roath Dock and to continue to meet British Standard requirement of BS 12566. |  |
| Considerations of foul sewer | We agree with the operators justification for not connecting to foul sewer. |  |
| Operator Competence |  |  |  |
| Environment Management System | There is no known reason to consider that the operator will not have the management systems to enable it to comply with the permit conditions. The decision was taken in accordance with RGN 5 on Operator Competence. |  |
| Sustainable Management of Natural Resources (SMNR) |  |  |
| Considerations of SMNR - Compliance with our General Purpose | We are satisfied that this decision is compatible with our general purpose of pursuing the sustainable management of natural resources in relation to Wales and applying the principles of sustainable management of natural resources” |  |

# Annex 2: Consultation responses

Summary of responses to consultation and the way in which we have taken these into account in the determination process.  (Newspaper advertising is only carried out for certain application types, in line with our guidance.)

Response received from

Associated British Ports

Brief summary of issues raised

No issues were raised, reference mace to quality of effluent to be discharged and compliance with relevant British Standards.

Summary of actions taken or show how this has been covered

No action to be taken