SCHEDULE 1
Confirmation of condition 5.1.1 notifications,

 in accordance with condition 5.1.2

	PART A – To be completed and sent within 24 hours of verbal notification to the EA

	Name of Operator and Permit Number
	UPM-Kymmene (UK) Limited, Shotton Paper. Authorisation BT 4885

	Location of Installation
	Weighbridge Rd, Shotton Deeside

	Date information provided
	05/06/2015

	Name(s) of the prescribed substance(s), which might cause harm.
	CO

	Time, date and location of emission.
	02:00 hours   
05/06/2015

Emission to atmosphere 

	Best estimate of the quantity of the substance(s) released or the rate of release, and the time during which the release took place.
	134.2 mg/m3, 30 minute average at 02:00 hours

	Environmental medium into which the emission took place.
	Air

	Measures taken, or intended to be taken, to stop the emission.
	Incident happened at the end of a sootblow. Boiler control reduced CO levels to minimum but spike was too high to bring average down in time.


	PART B – To be completed and sent to the EA as soon as practicable

	Any more accurate information on the matters notified under Part A.
	

	Measures taken, or intended to be taken to prevent a recurrence of the incident.
	

	Measures taken of intended to be taken, to rectify any environmental damage which has been or may be caused by the release.
	

	The dates of any Part A notifications within the previous 24 months.
	


COPIES TO:

Peter Walmsley,

John Sanderson,

