SCHEDULE 1
Confirmation of condition 5.1.1 notifications,

 in accordance with condition 5.1.2

	PART A – To be completed and sent within 24 hours of verbal notification to the EA

	Name of Operator and Permit Number
	UPM-Kymmene (UK) Limited, Shotton Paper. Authorisation BT 4885

	Location of Installation
	Weighbridge Rd, Shotton Deeside

	Date information provided
	05/06/2015

	Name(s) of the prescribed substance(s), which might cause harm.
	CO

	Time, date and location of emission.
	02:00 hours   
05/06/2015

Emission to atmosphere 

	Best estimate of the quantity of the substance(s) released or the rate of release, and the time during which the release took place.
	134.2 mg/m3, 30 minute average at 02:00 hours

	Environmental medium into which the emission took place.
	Air

	Measures taken, or intended to be taken, to stop the emission.
	Incident happened at the end of a sootblow. Boiler control reduced CO levels to minimum but spike was too high to bring average down in time.


	PART B – To be completed and sent to the EA as soon as practicable

	Any more accurate information on the matters notified under Part A.
	As a consequence of the sootblow there is less HP steam available for power generation this results in the steam turbine output to be reduced. The Boiler output steam flow target is 33 kg/s
See attached trends which indicate that at the end of the sootblow the steam flow suddenly increased to 36.0 kg/s therefore causing the steam turbine to also increase.

All other parameters have been checked and there have been no other abnormalities found.
The combustion control system was as usual active at the time, again with no abnormalities found.

It is likely therefore that the CO non conformance is as a result of a number of parameters occurring at the same time resulting in an increased steam output from which the combustion control system could not react with sufficient speed.



	Measures taken, or intended to be taken to prevent a recurrence of the incident.
	Review of the combustion control system

	Measures taken of intended to be taken, to rectify any environmental damage which has been or may be caused by the release.
	Continue monitoring

	The dates of any Part A notifications within the previous 24 months.
	None
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