[bookmark: _GoBack]Schedule 5 - Notification

These pages outline the information that the operator must provide.

Units of measurement used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission. Where appropriate, a comparison should be made of actual emissions and authorised emission limits.
If any information is considered commercially confidential, it should be separated  from non-confidential information, supplied on a separate sheet and accompanied by an application for commercial confidentiality under the provisions of the EP Regulations.

Part A
	Permit Number
	BT4885

	Name of operator
	UPM-Kymmene UK Ltd

	Location of Facility
	Weighbridge Rd, Shotton, Deeside, Flintshire. CH5 2LL

	Time and date of the detection
	



	(a) Notification requirements for any malfunction, breakdown or failure  of equipment or techniques, accident, or emission of a substance not controlled by an emission limit which  has caused, is
causing or may cause significant pollution

	To be notified within 24 hours of detection

	Date and time of the event
	 01.07.2015  03:30-04:00hrs

	Reference or description of the

location of the event
	Boiler 7 stack. Continuous emissions monitoring system.  

	Description of where any release into the environment took place
	 Boiler 7 stack to atmosphere. 

	Substances(s) potentially
released
	 CO

	Best estimate  of the quantity  or
rate of  release of substances
	 124.1mg/m3  (30min average)

	Measures taken, or intended to be taken, to stop any emission
	Boiler output temporarily reduced. Conditions stabilized.  

	Description of the failure or
accident.
	Biofuel screw failed resulting in a poor mix of fuels feeding the boiler.



	(b) Notification requirements for  the breach of a limit

	To be notified within 24 hours of detection unless  otherwise specified below

	Emission point reference/ source
	 Boiler 7 CEMS

	Parameter(s)
	 CO

	Limit
	 100mg/m3

	Measured value and uncertainty
	 124.1mg/m3

	Date and time of monitoring
	 01.07.2015  03:30-04:00hrs

	Measures taken, or intended  to

be taken, to stop the emission
	Boiler output temporarily reduced. Conditions stabilized.






	Time periods for notification following detection of a breach of a limit

	Parameter
	Notification period

	CO – 6.7mg/m3                                                  01.07.2015
	 04:00 - 04:30

	CO – 17.3 mg/m3                                               01.07.2015
	 04:30 - 05:00 

	CO – 21.6mg/m3                                                01.07.2015
	 05:00 - 05:30






	(c) Notification requirements for the detection of any significant adverse environmental effect

	To be notified within 24 hours of detection

	Description of where the effect on
the environment was detected
	Boiler 7 stack to atmosphere.

	Substances(s) detected
	CO

	Concentrations of substances
detected
	124.1mg/m3

	Date of monitoring/sampling
	01.07.2015




 Part B- to be submitted as soon as practicable
	Any more accurate information on the matters for
notification under Part A.
	Biofuel screw failed resulting in a poor mix of fuels feeding the boiler. 

	Measures taken, or intended to be taken, to
prevent a recurrence of the incident
	Operator continued to run fuel as he investigated the alarm for failure of the screw. The Screw was reset and normal Feed was resumed. Further investigation found the Inverter Drive as failing. Inverter Drive Replaced. 
Failure of Inverter added to Management System for Route Cause Analysis. This system will identify the Route Cause and identify what procedures need to be implemented to prevent re-occurrence. 

	Measures taken, or intended to be taken, to rectify,
limit or prevent any pollution of the environment which has been or may be caused by the emission
	Route Cause Analysis system will be used to identify a method of avoiding this incident if the Screw Inverter Drive Fails in the future.

	The dates of any unauthorised emissions from the
facility in the preceding 24 months.
	02:00 hours   
05/06/2015





	NAME*
	Grant Fraser

	POST
	Utilities Day Supervisor

	SIGNATURE
	x

	DATE
	02/07/2015




• authorised to sign on behalf of the operator



