Schedule 5 - Notification

These pages outline the information that the operator must provide.

Units of measurement used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission. Where appropriate, a comparison should be made of actual emissions and authorised emission limits.

If any information is considered commercially confidential, it should be separated  from non-confidential information, supplied on a separate sheet and accompanied by an application for commercial confidentiality under the provisions of the EP Regulations.

Part A

| Permit Number | BT4885 |
| --- | --- |
| Name of operator | UPM-Kymmene UK Ltd |
| Location of Facility | Weighbridge Rd, Shotton, Deeside, Flintshire. CH5 2LL |
| Time and date of the detection |  |

| (a) Notification requirements for any malfunction, breakdown or failure of equipment or techniques, accident, or emission of a substance not controlled by an emission limit which has caused, is causing or may cause significant pollution |  |
| --- | --- |
| To be notified within 24 hours of detection |  |
| Date and time of the event | 01.07.2015 03:30-04:00hrs |
| Reference or description of the location of the event | Boiler 7 stack. Continuous emissions monitoring system. |
| Description of where any release into the environment took place | Boiler 7 stack to atmosphere. |
| Substances(s) potentially released | CO |
| Best estimate of the quantity or rate of release of substances | 124.1mg/m3 (30min average) |
| Measures taken, or intended to be taken, to stop any emission | Boiler output temporarily reduced. Conditions stabilized. |
| Description of the failure or accident. | Biofuel screw failed resulting in a poor mix of fuels feeding the boiler. |

| (b) Notification requirements for the breach of a limit |  |
| --- | --- |
| To be notified within 24 hours of detection unless otherwise specified below |  |
| Emission point reference/ source | Boiler 7 CEMS |
| Parameter(s) | CO |
| Limit | 100mg/m3 |
| Measured value and uncertainty | 124.1mg/m3 |
| Date and time of monitoring | 01.07.2015 03:30-04:00hrs |
| Measures taken, or intended to be taken, to stop the emission | Boiler output temporarily reduced. Conditions stabilized. |

| Time periods for notification following detection of a breach of a limit |  |
| --- | --- |
| Parameter | Notification period |
| CO – 6.7mg/m3 01.07.2015 | 04:00 - 04:30 |
| CO – 17.3 mg/m3 01.07.2015 | 04:30 - 05:00 |
| CO – 21.6mg/m3 01.07.2015 | 05:00 - 05:30 |

| (c) Notification requirements for the detection of any significant adverse environmental effect |  |
| --- | --- |
| To be notified within 24 hours of detection |  |
| Description of where the effect on the environment was detected | Boiler 7 stack to atmosphere. |
| Substances(s) detected | CO |
| Concentrations of substances detected | 124.1mg/m3 |
| Date of monitoring/sampling | 01.07.2015 |

Part B- to be submitted as soon as practicable

| Any more accurate information on the matters for notification under Part A. | Biofuel screw failed resulting in a poor mix of fuels feeding the boiler. |
| --- | --- |
| Measures taken, or intended to be taken, to prevent a recurrence of the incident | Operator continued to run fuel as he investigated the alarm for failure of the screw. The Screw was reset and normal Feed was resumed. Further investigation found the Inverter Drive as failing. Inverter Drive Replaced. Failure of Inverter added to Management System for Route Cause Analysis. This system will identify the Route Cause and identify what procedures need to be implemented to prevent re-occurrence. |
| Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment which has been or may be caused by the emission | Route Cause Analysis system will be used to identify a method of avoiding this incident if the Screw Inverter Drive Fails in the future. |
| The dates of any unauthorised emissions from the facility in the preceding 24 months. | 02:00 hours 05/06/2015 |

| NAME* | Grant Fraser |
| --- | --- |
| POST | Utilities Day Supervisor |
| SIGNATURE | x |
| DATE | 02/07/2015 |

• authorised to sign on behalf of the operator