Schedule 5 - Notification

These pages outline the information that the operator must provide.

Units of measurement used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission. Where appropriate, a comparison should be made of actual emissions and authorised emission limits.

If any information is considered commercially confidential, it should be separated  from non-confidential information, supplied on a separate sheet and accompanied by an application for commercial confidentiality under the provisions of the EP Regulations.

Part A

| Permit Number | BT4885 |
| --- | --- |
| Name of operator | UPM-Kymmene UK Ltd |
| Location of Facility | Weighbridge Rd, Shotton, Deeside, Flintshire. CH5 2LL |
| Time and date of the detection |  |

| (a) Notification requirements for any malfunction, breakdown or failure of equipment or techniques, accident, or emission of a substance not controlled by an emission limit which has caused, is causing or may cause significant pollution |  |
| --- | --- |
| To be notified within 24 hours of detection |  |
| Date and time of the event | 01.07.2015 03:30-04:00hrs |
| Reference or description of the location of the event | Boiler 7 stack. Continuous emissions monitoring system. |
| Description of where any release into the environment took place | Boiler 7 stack to atmosphere. |
| Substances(s) potentially released | CO |
| Best estimate of the quantity or rate of release of substances | 124.1mg/m3 (30min average) |
| Measures taken, or intended to be taken, to stop any emission | Boiler output temporarily reduced. Conditions stabilized. |
| Description of the failure or accident. | Biofuel screw failed resulting in a poor mix of fuels feeding the boiler. |

| (b) Notification requirements for the breach of a limit |  |
| --- | --- |
| To be notified within 24 hours of detection unless otherwise specified below |  |
| Emission point reference/ source | Boiler 7 CEMS |
| Parameter(s) | CO |
| Limit | 100mg/m3 |
| Measured value and uncertainty | 124.1mg/m3 |
| Date and time of monitoring | 01.07.2015 03:30-04:00hrs |
| Measures taken, or intended to be taken, to stop the emission | Boiler output temporarily reduced. Conditions stabilized. |

| Time periods for notification following detection of a breach of a limit |  |
| --- | --- |
| Parameter | Notification period |
| CO – 6.7mg/m3 01.07.2015 | 04:00 - 04:30 |
| CO – 17.3 mg/m3 01.07.2015 | 04:30 - 05:00 |
| CO – 21.6mg/m3 01.07.2015 | 05:00 - 05:30 |

| (c) Notification requirements for the detection of any significant adverse environmental effect |  |
| --- | --- |
| To be notified within 24 hours of detection |  |
| Description of where the effect on the environment was detected |  |
| Substances(s) detected |  |
| Concentrations of substances detected |  |
| Date of monitoring/sampling |  |

Part B- to be submitted as soon as practicable

| Any more accurate information on the matters for notification under Part A. |  |
| --- | --- |
| Measures taken, or intended to be taken, to prevent a recurrence of the incident |  |
| Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment which has been or may be caused by the emission |  |
| The dates of any unauthorised emissions from the facility in the preceding 24 months. |  |

| NAME* |  |
| --- | --- |
| POST |  |
| SIGNATURE |  |
| DATE |  |

• authorised to sign on behalf of the operator