Schedule 6 Notification

Part A

	Permit Number
	BU0800IZ

	Name of Operator
	3C Waste Limited

	Location of Installation
	Llanddulas Landfill Site

	Time and date of the detection
	6th January 2016


(a) Notification requirements for any malfunction, breakdown or failure of equipment or techniques, accident, or fugitive emission which has caused, is causing or may cause significant pollution

To be notified within 24 hours of detection

	Date and time of the event


	n/a

	Reference or description of the     

Location of the event
	n/a

	Description of where any release into 

The environment took place


	n/a

	Substance(s) potentially released


	n/a


	Best estimate of the quantity or rate

Of release substances


	n/a

	Measures taken or intended to be taken,

To stop any emission


	n/a

	Description of the failure or accident
	n/a


(b) Notification requirements for the breach of a limit

To be notified within 24 hours unless otherwise specified below

	Emission point reference/ source


	Leachate Collection Point LCP2Ar2 (Phase 2A)
Leachate Collection Point LCP2Br2 (Phase 2B)



	Parameters(s)
	Leachate


	Limit
	See below


	Measured value and uncertainty


	Sample ID

Date
Trigger

Value

LCP2Ar2
LCP2Br2

05/01/16
13/01/16

13/01/16

2.00m
2.00m

2.72m
6.52m

4.75m


	Date and time of monitoring


	Scheduled weekly monitoring took place on the 5th January and 13th January 2016.



	Measures taken or intended to be taken,

to stop any emission


	The breach in leachate compliance level has arisen due to the persistent heavy rain experienced towards the end of November and throughout December (39mm in October, 136mm in November and 178mm in December). Following such a prolonged period of rain, it is likely that the rainwater has now found a preferential pathway through the waste directly into these wells.
In addition, with Phase 2C and Phase 3A remaining compliant, it is suspected that leachate from the upper levels of Phase 3A and Phase 2C might also be draining to LCP2Ar2 and LCP2Br2, hence the sudden rise in levels.
A second pneumatic pump was installed to LCP 2Ar2 on Friday 8th January to enable compliance to be achieved as quickly as possible. Additional monitoring is being carried out to check progress.  There was a rapid rise in leachate levels since the monitoring on 5th January, but these have been reversed in LCP2Ar2 by installing a 2nd pump. Levels in LCP2Br2 are also starting to reduce.
Subsequent daily monitoring;

 LCP2Ar2 – 14/01/16 – 6.16m
                     15/01/16 – 5.68m

LCP2Br2 -   14/01/16 -  4.75m

                     15/01/16 -  4.55m

Tankering imports to the treatment plant have been reduced to ensure adequate capacity is maintained in the tanks for leachate coming off site, so that leachate pumping is uninterrupted.


	
	


Time periods for notification following detection of a breach of a limit 
Parameter  







               Notification period
(c} Notification requirements for the detection of any significant adverse environmental effect

To be notified within 24 hours of detection

	Description of where the effect on 

The environment was detected


	n/a

	Substance(s) detected


	n/a

	Concentrations of substances

Detected


	n/a

	Date of monitoring/sampling 


	n/a


Part B
	Any more accurate information on the matters for notification under Part A.
	To be closed out once leachate level compliant.

	Measures taken, or intended to be taken, to prevent a recurrence of the incident
	As above

	Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment or harm which has been or may be caused by the emission
	As above

	The dates of any unauthorised emissions from the installation in the preceding 24 months.
	As previously reported via Schedule 6.


	Name:               Peter Taberner

	Post:                Site Manager

	Signature:  [image: image1.png]




	Date:                15/01/16


