Permit with introductory note

The Environmental Permitting (England & Wales) Regulations 2016

Tata Steel UK Ltd

Tata Steel Colors

Shotton Site

Shotton

Flintshire

CH5 2NH

Permit number

EPR/BR7321IK

Tata Steel Colors

Permit number EPR/BR7321IK

Introductory note

This introductory note does not form a part of the permit

Tata Steel Colors, which extends over 500 acres, is the operational headquarters for a group of works specialising in the manufacture of coated coiled steel. It is situated approximately 1Km from Shotton Town Centre, Deeside, Grid Reference 330274,370560. The site is located in an area predominantly surrounded by agricultural land to the east, marsh land to the west, the River Dee to the south and Deeside Industrial Estate to the north. The site is bounded to the north and west by Chester Road (A548).

The process involves steel coils arriving on site. Cold rolled coils, up to 1650mm wide, are supplied to the works from other plants, mainly in South Wales. They can then pass through two process routes; hot dip galvanising followed by organic coating, or alternatively pass directly through the galvanising line. The hot dip galvanising coats the incoming sheet with either zinc or zinc metal alloys for corrosion resistance. The organic coating lines coat the sheet with specially formulated paints for additional protection and a decorative finish. There are two hot dip galvanising lines (no.5 and no.6) and two colorcoat lines (no.1 and no.2) within the installation. Both colorcoat lines are equipped with a thermal oxidiser to destroy VOCs extracted from the paint application and curing stages. There is a central boiler house with a principal role of providing back up steam to the coating processes. The total output from the installation is around 700,000 tonnes per annum.

The Shotton Lagoons and Reedbeds SSSI is adjacent to the site and accepts storm waters and process waters from the site. Any effluent is treated at an effluent treatment plant to remove metal and metal salts before being discharged to the River Dee.

The status log of the permit sets out the permitting history, including any changes to the permit reference number.

| Status log of the permit |  |  |
| --- | --- | --- |
| Description | Date | Comments |
| Application EPR/BR7321IK/A001 received | Duly made 10/07/2003 |  |
| Additional information requested | 12/12/2003 |  |
| Additional information received | 05/02/2004 |  |
| Application EPR/BR7321IK/A001 determined and permit EPR/BR7321IK issued | 12/03/2004 |  |
| Variation application EPR/BR7321IK/V002 received (BP3835MQ) | 05/09/2006 | Removal of “Particulates” from Tables 2.2.2 and S2. |
| Additional information received | 07/09/2006 |  |
| Application EPR/BR7321IK/V002 determined and variation notice issued | 10/10/2006 |  |
| Variation application EPR/BR7321IK/V003 received (QP3838UM) | 25/04/2007 | Installation of three Zincoff units to recover metallic zinc from the dross skimmed from the surface of the galvanizing baths. |
| Additional information received | 18/05/2007 |  |
| Application EPR/BR7321IK/V003 determined and variation notice issued | 04/06/2007 |  |
| Variation application EPR/BR7321IK/V004 received (XP3235GL) | 13/10/2008 | Installation of a thermal oxidiser to replace two incinerators for abatement of VOCs from Colorcoat line no.1 paint curing ovens. Installation of new bulk storage tanks for solvents used on Colorcoat line no.2. |
| Additional information received | 10/12/2008 |  |
| Application EPR/BR7321IK/V004 determined and variation notice issued | 17/12/2008 |  |
| Partial surrender application EPR/BR7321IK/S005 received (XP3730KG) | Duly made 05/05/2009 |  |
| Additional information requested | 15/07/2009 |  |
| Additional information received | 30/07/2009 |  |
| Application EPR/BR7321IK/S005 determined and partial surrender notice issued | 31/07/2009 |  |
| Notification of change of company name received | 29/09/2010 |  |
| Updated permit issued to show a change of company name | 02/11/2010 |  |
| Variation application EPR/BR7321IK/V006 received | 05/09/2011 | Installation of a thermal oxidiser to replace an existing oxidiser on Colorcoat line no.2 |
| Application EPR/BR7321IK/V006 determined and variation notice issued | 11/11/2011 |  |
| Variation application EPR/BR7321IK/V007 received | Duly made 10/03/2017 | Substantial variation |
| Additional information requested | 11/07/2017 | Updated air quality modelling report required to take account of effects on wildlife sites |
| Additional information received | 07/08/2017 | Statutory deadline extended by 27 days to 03/09/2017 |
| Request for determination extension by NRW | 06/09/2017 |  |
| Request for determination extension agreed by operator | 11/09/2017 | Statutory deadline extended by 3 months to 03/12/2017 |
| Additional information requested | 18/10/2017 | Noise assessment required |
| Additional information received | 19/12/2017 | Statutory deadline extended by 62 days to 03/02/2018 |
| Request for determination extension by NRW | 29/01/2018 |  |
| Request for determination extension agreed by operator | 30/01/2018 | Statutory deadline extended by 1 month to 03/03/2018 |
| Request for determination extension by NRW | 02/03/2018 |  |
| Request for determination extension agreed by operator | 02/03/2018 | Statutory deadline extended by 20 days to 23/03/2018 |
| 20 working days draft consultation period | 23/03/2018 | Statutory deadline extended by 32 days to 24/04/2018 |
| Application EPR/BR7321IK/V007 determined – variation notice and consolidated permit issued | 25/04/2018 |  |

End of introductory note

Permit

The Environmental Permitting (England and Wales) Regulations 2016

Permit number

EPR/BR7321IK

This is the consolidated permit referred to in the variation and consolidation notice for application EPR/BR7321IK/V007 authorising

Tata Steel UK Ltd (“the operator”),

whose registered office is

30 Millbank

London

SW1P 4WY

company registration number 2280000

to operate a regulated facility at

Tata Steel Colors

Shotton Site

Shotton

Flintshire

CH5 2NH

to the extent authorised by and subject to the conditions of this permit.

| Signed | Date |
| --- | --- |
| Holly Noble | 25th April 2018 |

Authorised on behalf of Natural Resources Wales

Conditions

# Management

## General management

### The operator shall manage and operate the activities:

#### in accordance with a written management system that identifies and minimises risks of pollution, including those arising from operations, maintenance, accidents, incidents, non-conformances, closure and those drawn to the attention of the operator as a result of complaints; and

#### using sufficient competent persons and resources.

### Records demonstrating compliance with condition 1.1.1 shall be maintained.

### Any person having duties that are or may be affected by the matters set out in this permit shall have convenient access to a copy of it kept at or near the place where those duties are carried out.

## 1.2	Energy efficiency

### 1.2.1	The operator shall:

(a)	take appropriate measures to ensure that energy is used efficiently in the activities;

(b)	review and record at least every four years whether there are suitable opportunities to improve the energy efficiency of the activities; and

(c)	take any further appropriate measures identified by a review.

## 1.3	Efficient use of raw materials

### 1.3.1	The operator shall:

(a)	take appropriate measures to ensure that raw materials and water are used efficiently in the activities;

(b)	maintain records of raw materials and water used in the activities;

(c)	review and record at least every four years whether there are suitable alternative materials that could reduce environmental impact or opportunities to improve the efficiency of raw material and water use; and

(d)	take any further appropriate measures identified by a review.

## 1.4	Avoidance, recovery and disposal of wastes produced by the activities

### The operator shall take appropriate measures to ensure that:

### (a)	the waste hierarchy referred to in Article 4 of the Waste Framework Directive is applied  to the generation of  waste by the activities; and

### (b)	any waste generated by the activities is treated in accordance with the waste hierarchy referred to in Article 4 of the Waste Framework Directive; and

### (c)	where disposal is necessary, this is undertaken in a manner which minimises its impact on the environment.

### The operator shall review and record at least every four years whether changes to those measures should be made and take any further appropriate measures identified by a review.

# 2	Operations

2.1	Permitted activities

### 2.1.1	The operator is only authorised to carry out the activities specified in schedule 1 table S1.1 (the “activities”).

## 2.2	The site

2.2.1	The activities shall not extend beyond the site, being the land shown edged in blue on the site plan at schedule 7 to this permit.

## 2.3	Operating techniques

#### 2.3.1	(a) 	The activities shall, subject to the conditions of this permit, be operated using the

#### techniques and in the manner described in the documentation specified in 	schedule 1, table S1.2, unless otherwise agreed in writing by Natural Resources Wales.

#### (b)	If notified by Natural Resources Wales that the activities are giving rise to pollution, the operator shall submit to Natural Resources Wales for approval within the period specified, a revision of any plan or other documentation (“plan”) specified in schedule 1, table S1.2 or otherwise required under this permit which identifies and minimises the risks of pollution relevant to that plan , and shall implement the approved revised plan in place of the original from the date of approval, unless otherwise agreed in writing by Natural Resources Wales.

2.3.2	Any raw materials or fuels listed in schedule 2 table S2.1 shall conform to the specifications set out in that table.

### 2.3.3	The operator shall ensure that where waste produced by the activities is sent to a relevant waste operation, that operation is provided with the following information, prior to the receipt of the waste:

### (a)	the nature of the process producing the waste;

### (b)	the composition of the waste;

### (c)	the handling requirements of the waste;

### (d)	the hazardous property associated with the waste, if applicable; and

### (e)	the waste code of the waste.

## 2.4	Improvement programme

### 2.4.1 	The operator shall complete the improvements specified in schedule 1 table S1.3 by the date specified in that table unless otherwise agreed in writing by Natural Resources Wales.

### 2.4.2	Except in the case of an improvement which consists only of a submission to Natural Resources Wales, the operator shall notify Natural Resources Wales within 14 days of completion of each improvement.

# 3	Emissions and monitoring

## 3.1	Emissions to water, air or land

### 3.1.1	There shall be no point source emissions to water, air or land except from the sources and emission points listed in schedule 3 tables S3.1 and S3.2.

### 3.1.2	The limits given in schedule 3 shall not be exceeded.

    - Total annual emissions from the emission point(s) set out in tables schedule 3 S3.1 and S3.2 of a substance listed in schedule 3 table S3.3 shall not exceed the relevant limit in table S3.3.

## Emissions of substances not controlled by emission limits

### Emissions of substances not controlled by emission limits (excluding odour) shall not cause pollution. The operator shall not be taken to have breached this condition if appropriate measures, including, but not limited to, those specified in any approved emissions management plan, have been taken to prevent or where that is not practicable, to minimise, those emissions.

3.2.2	The operator shall:

#### (a)	if notified by Natural Resources Wales that the activities are giving rise to pollution, submit to Natural Resources Wales for approval within the period specified, an emissions management plan which identifies and minimises the risks of pollution from emissions of substances not controlled by emission limits;

#### (b)	implement the approved emissions management plan, from the date of approval, unless otherwise agreed in writing by Natural Resources Wales.

3.2.3	All liquids in containers, whose emission to water or land could cause pollution, shall be provided with secondary containment, unless the operator has used other appropriate measures to prevent or where that is not practicable, to minimise, leakage and spillage from the primary container.

## 3.3	Odour

#### 3.3.1	Emissions from the activities shall be free from odour at levels likely to cause pollution outside the site, as perceived by an authorised officer of Natural Resources Wales, unless the operator has used appropriate measures, including, but not limited to, those specified in any approved odour management plan, to prevent or where that is not practicable to minimise the odour.

3.3.2	The operator shall:

#### (a)	if notified by Natural Resources Wales that the activities are giving rise to pollution outside the site due to odour, submit to Natural Resources Wales for approval within the period specified, an odour management plan which identifies and minimises the  risks of pollution from odour;

#### (b)	implement the approved odour management plan, from the date of approval, unless otherwise agreed in writing by Natural Resources Wales.

## 3.4	Noise and vibration

#### 3.4.1	Emissions from the activities shall be free from noise and vibration at levels likely to cause pollution outside the site, as perceived by an authorised officer of Natural Resources Wales, unless the operator has used appropriate measures, including, but not limited to, those specified in any approved noise and vibration management plan to prevent or where that is not practicable to minimise the noise and vibration.

3.4.2	The operator shall:

#### (a)	if notified by Natural Resources Wales that the activities are giving rise to pollution outside the site due to noise and vibration, submit to Natural Resources Wales for approval within the period specified, a noise and vibration management plan which identifies and minimises the risks of pollution from noise and vibration;

#### (b)	implement the approved noise and vibration management plan, from the date of approval, unless otherwise agreed in writing by Natural Resources Wales.

## 3.5	Monitoring

### 3.5.1	The operator shall, unless otherwise agreed in writing by Natural Resources Wales, undertake the monitoring specified in the following tables in schedule 3 to this permit:

#### point source emissions specified in tables S3.1 and S3.2;

#### (b)	process monitoring specified in table S3.4;

3.5.2	The operator shall maintain records of all monitoring required by this permit including records of the taking and analysis of samples, instrument measurements (periodic and continous), calibrations, examinations, tests and surveys and any assessment or evaluation made on the basis of such data.

3.5.3	Monitoring equipment, techniques, personnel and organisations employed for the emissions monitoring programme and the environmental or other monitoring specified in condition 3.5.1 shall have either MCERTS certification or MCERTS accreditation (as appropriate), where available, unless otherwise agreed in writing by Natural Resources Wales.

3.5.4	Permanent means of access shall be provided to enable sampling/monitoring to be carried out in relation to the emission points specified in schedule 3 tables S3.1 and S3.2 unless otherwise agreed in writing by Natural Resources Wales.

# 4	Information

## 4.1	Records

### All records required to be made by this permit shall:

### be legible;

### be made as soon as reasonably practicable;

### if amended, be amended in such a way that the original and any subsequent amendments remain legible, or are capable of retrieval; and

### be retained, unless otherwise agreed in writing by Natural Resources Wales, for at least 6 years from the date when the records were made, or in the case of the following records until permit surrender:

- off-site environmental effects; and

- matters which affect the condition of the land and groundwater.

4.1.2	The operator shall keep on site all records, plans and the management system required to be maintained by this permit, unless otherwise agreed in writing by Natural Resources Wales.

## 4.2	Reporting

4.2.1	The operator shall send all reports and notifications required by the permit to Natural Resources Wales using the contact details supplied in writing by Natural Resources Wales.

### 4.2.2	A report or reports on the performance of the activities over the previous year shall be submitted to Natural Resources Wales by 31 January (or other date agreed in writing by Natural Resources Wales) each year.  The report(s) shall include as a minimum:

#### (a)	a review of the results of the monitoring and assessment carried out in accordance with the permit including an interpretive review of that data;

#### (b)	the annual production /treatment data set out in schedule 4 table S4.2; and

#### (c)	the performance parameters set out in schedule 4 table S4.3 using the forms specified in table S4.4 of that schedule.

### 4.2.3	Within 28 days of the end of the reporting period the operator shall, unless otherwise agreed in writing by Natural Resources Wales, submit reports of the monitoring and assessment carried out in accordance with the conditions of this permit, as follows:

(a)	in respect of the parameters and emission points specified in schedule 4 table S4.1;

(b)	for the reporting periods specified in schedule 4 table S4.1 and using the forms specified in schedule 4 table S4.4 ; and

(c)	giving the information from such results and assessments as may be required by the forms specified in those tables.

4.2.4	The operator shall, unless notice under this condition has been served within the preceding four years, submit to Natural Resources Wales, within six months of receipt of a written notice, a report assessing whether there are other appropriate measures that could be taken to prevent, or where that is not practicable, to minimise pollution.

### 4.2.5	The operator shall submit an annual solvent management plan in order to demonstrate compliance with the requirements of the Industrial Emissions Directive, by 31 January each year in respect of the previous year.

## 4.3	Notifications

4.3.1	(a)	In the event that the operation of the activities gives rise to an incident or accident which significantly affects or may significantly affect the environment, the operator must immediately—

(i)	inform Natural Resources Wales,

(ii)	take the measures necessary to limit the environmental consequences of such an incident or accident, and

(iii)	take the measures necessary to prevent further possible incidents or accidents;

(b)	in the event of a breach of any permit condition the operator must immediately—

(i)	inform Natural Resources Wales, and

(ii)	take the measures necessary to ensure that compliance is restored within the shortest possible time;

(c)	in the event of a breach of permit condition which poses an immediate danger to human health or threatens to cause an immediate significant adverse effect on the environment, the operator must immediately suspend the operation of the activities or the relevant part of it until compliance with the permit conditions has been restored.

### 4.3.2	Any information provided under condition 4.3.1 (a)(i), or 4.3.1 (b)(i) where the information relates to the breach of a limit specified in the permit, shall be confirmed by sending the information listed in schedule 5 to this permit within the time period specified in that  schedule.

### 4.3.3	Where Natural Resources Wales has requested in writing that it shall be notified when the operator is to undertake monitoring and/or spot sampling, the operator shall inform Natural Resources Wales when the relevant monitoring and/or spot sampling is to take place. The operator shall provide this information to Natural Resources Wales at least 14 days before the date the monitoring is to be undertaken.

### 4.3.4	Natural Resources Wales shall be notified within 14 days of the occurrence of the following matters, except where such disclosure is prohibited by Stock Exchange rules:

Where the operator is a registered company:

#### any change in the operator’s trading name, registered name or registered office address; and

#### (b)	any steps taken with a view to the operator going into administration, entering into a company voluntary arrangement or being wound up.

Where the operator is a corporate body other than a registered company:

#### any change in the operator’s name or address; and

#### any steps taken with a view to the dissolution of the operator.

#### In any other case:

#### the death of any of the named operators (where the operator consists of more than one named individual);

#### any change in the operator’s name(s) or address(es); and

#### any steps taken with a view to the operator, or any one of them, going into bankruptcy, entering into a composition or arrangement with creditors, or, in the case of them being in a partnership, dissolving the partnership.

### 4.3.5	Where the operator proposes to make a change in the nature or functioning, or an extension of the activities, which may have consequences for the environment and the change is not otherwise the subject of an application for approval under the Regulations or this permit:

### Natural Resources Wales shall be notified at least 14 days before making the change; and

### the notification shall contain a description of the proposed change in operation.

### 4.3.6	Natural Resources Wales shall be given at least 14 days notice before implementation of any part of the site closure plan.

### 4.3.7	Where the operator has entered into a climate change agreement with the Government, Natural Resources Wales shall be notified within one month of:

- (a)	a decision by the Secretary of State not to re-certify the agreement;

- (b)	a decision by either the operator or the Secretary of State to terminate the agreement; and

- (c)	any subsequent decision by the Secretary of State to re-certify such an agreement.

## 4.4	Interpretation

### 4.4.1	In this permit the expressions listed in schedule 6 shall have the meaning given in that schedule.

### 4.4.2	In this permit references to reports and notifications mean written reports and notifications, except where reference is made to notification being made “immediately”, in which case it may be provided by telephone.

# Schedule 1 - Operations

| Table S1.1 activities |  |  |  |
| --- | --- | --- | --- |
| Activity listed in Schedule 1 of the EP Regulations | Description of specified activity | Limits of specified activity |
| Section 1.1 Part A(1) (a) – Burning any fuel in an appliance with a rated thermal input of 50 or more megawatts | Operation of boilers | Operation of boilers |
| Section 2.1 Part A(2) (c) – Applying protective fused metal coatings with an input of more than 2 tonnes of crude steel per hour | Galvanising process – applying a fused zinc based alloy coating to steel coils using a hot dip process | From receipt of raw materials to storage of finished goods, excluding warehousing of incoming and outgoing steel coils |
| Section 6.4 Part A(2) (a) – Surface treating substances, objects or products using organic solvents, in particular for dressing, printing, coating, degreasing, waterproofing, sizing, painting, cleaning or impregnating, in plant with a consumption capacity of more than 150kg or more per hour than 200 tonnes per year | Coating process – applying a solvent based painted coating to steel coils | From receipt of raw materials to storage of finished goods, excluding warehousing of incoming and outgoing steel coils |
| Section 5.4 Part A(1) (a) (ii) – Disposal of non-hazardous waste with a capacity exceeding 50 tonnes per day (or 100 tonnes per day if the only waste treatment activity is anaerobic digestion) by physico-chemical treatment | Removal of metal and metal salts from process effluents and from landfill leachate by physico-chemical treatment | Effluent discharge to River Dee |
| Directly Associated Activity |  |  |  |
| Recoiling and trimming - unlisted directly associated activity | Post treatment of finished steel coils | Operation of the recoiling and trimming process |

| Table S1.2 Operating techniques |  |  |
| --- | --- | --- |
| Description | Parts | Date Received |
| Application | Chapter 2 and Chapter 7 of Annex 6, Annex 7, Annex 9, Annex 10, Annex 11, Annex 12 and Annex 16 | 10th July 2003 |
| Application for variation | All | 5th September 2006 |
| Additional information | All | 7th September 2006 |
| Application for variation | All | 25th April 2007 |
| Additional information | All | 21st May 2007 |
| Application for variation | All | 13th October 2008 |
| Additional information | All | 10th December 2008 |
| Application for variation | All | 5th and 7th September 2011 |
| Application for variation EPR/BR7321IK/V007 | All documents as submitted with the exception of the Habitat and Water Level Management Plan and air quality assessment | 10th March 2017 |
| Additional information | Updated air quality assessment | 7th August 2017 |
| Additional information | Noise assessment | 2nd November 2017 (Noise Impact Assessment Report and 3 supporting documents), 21st November 2017 (email forwarded from Spooner Industries Limited), 4th December 2017 (Noise Calculation), 18th December 2017 (updated Noise Calculation), and 19th December 2017 (email from operator confirming noise levels) |
| Shotton Lagoons and Reed beds Water level Management Plan | As agreed with NRW on 2nd November 2017 | 2nd November 2017 |

| Table S1.3 Improvement programme requirements |  |  |
| --- | --- | --- |
| Reference | Requirement | Date |
| 1 | The operator shall carry out an investigation into those open channels used for conveying treated process effluents, cooling water and surface water within the site boundary to establish whether they are in hydraulic continuity with the underlying ground water. A report on these investigations shall be submitted to the Environment Agency. | Completed |
| 2 | The operator shall carry out an investigation into the risk of pollution from mobilising materials present in the sediment in the open channels formerly used for conveying untreated effluents from surface and rain water collected in these channels, A report on these investigations shall be submitted to the Environment Agency. | Completed |
| 3 | The operator shall examine the feasibility of redirecting the boiler blowdown effluent from the package boiler plant to the effluent plant from Greenwood burn. A report on these investigations shall be submitted to the Environment Agency. | Completed |
| 4 | The operator shall carry out monitoring of chromium emissions to air from emission points A17, A24, A34 and A36 using a method of sampling and analysis agreed with the Environment Agency. A report shall be made to the Agency on these emissions. | Completed |
| 5 | The operator shall submit submit a solvent management plan acceptable to the Environment Agency, using the Guidance provided in Schedule 4 of the Pollution Prevention and Control (Solvent Emissions Directive) (England and Wales) Direction 2002. This plan shall include a calculation of the fugitive emissions value as defined in the said Direction. | Completed |
| 6 | In the event that the fugitive emissions value calculated in improvement condition 5 is found to exceed 10% the operator shall submit a reduction scheme which meets the requirements in Schedule 3 of the Pollution Prevention and Control (Solvent Emissions Directive) (England and Wales) Direction 2002. | Completed |
| 7 | The operator shall implement measures, acceptable to the Environment Agency, to protect against small accidental spillages of chromate waste during its transfer to the effluent plant for treatment. | Completed |
| 8 | The operator shall implement measures acceptable to the Environment Agency, to limit the consequences of an accidental spillage whilst loading and offloading paint in bulk at the Coatings 3 building. | Completed |
| 9 | As part of the first water minimisation audit carried out under condition 2.4.2, the operator shall explicitly address the difference in water consumption per tonne of product between Colorcoat line 1 and line 2. | Completed |
| 10 | In respect of the monitoring requirements set out in tables 2.2.5 and 2.10.1 for emissions to water and from the effluent plant, the operator shall provide a report acceptable to the Agency setting out the monitoring methods, and the accreditation status of the equipment, and/or the monitoring organisation as appropriate for the methods used for both sampling and analysis. | Completed |
| 11 | The operator shall review the equipment, techniques, personnel and organisations employed for its emissions monitoring programme against the requirements of condition 2.10.7. The operator shall provide a report and action plan acceptable to the Agency for achieving these standards. | Completed |
| 12 | The operator shall include within their site closure environmental toolkit and within their Environmental Management System, proposals/guidance on maintaining the viability of the Tern Lagoon and Shotton Reedbeds SSSI in the event of site closure. The operator shall make this document available for inspection by the Environment Agency. | Completed |

Schedule 2 - Waste types, raw materials and fuels

| Table S2.1 Raw materials and fuels |  |
| --- | --- |
| Raw materials and fuel description | Specification |
| - | - |

Schedule 3 – Emissions and monitoring

| Table S3.1 Point source emissions to air – emission limits and monitoring requirements |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Emission point ref. & location | Source | Parameter | Limit (including unit) 2 | Reference period | Monitoring frequency | Monitoring standard or method 1 |  |
| A1 Package Boiler House, point 14 on site plan | Package Boiler No. 1 | Oxides of Nitrogen (NO and NO2 expressed as NO2) | 300 mg/m3 3 | - | Annual 6 | BS EN 14792 |  |
|  |  | Oxides of Nitrogen (NO and NO2 expressed as NO2) | 450 mg/m3 4 |  |  | BS EN 14792 |  |
|  |  | Particulates | 50 mg/m3 4 |  |  | BS EN 13284-1 and MID |  |
|  |  | Carbon Monoxide | - mg/m3 |  |  | BS EN 15058 under gas firing conditions. BS EN 15058 under oil firing conditions if period of operation exceeds 30 days in any year. |  |
|  |  | Sulphur Dioxide | - Kg |  |  | By calculation from sulphur content of fuel oil. Under oil firing conditions if period of operation exceeds 30 days in any year. |  |
| A2 Package Boiler House, point 14 on site plan | Package Boiler No. 2 | Oxides of Nitrogen (NO and NO2 expressed as NO2) | 300 mg/m3 3 | - | Annual 6 | BS EN 14792 |  |
|  |  | Oxides of Nitrogen (NO and NO2 expressed as NO2) | 450 mg/m3 4 |  |  | BS EN 14792 |  |
|  |  | Particulates | 50 mg/m3 4 |  |  | BS EN 13284-1 and MID |  |
|  |  | Carbon Monoxide | - mg/m3 |  |  | BS EN 15058 under gas firing conditions. BS EN 15058 under oil firing conditions if period of operation exceeds 30 days in any year. |  |
|  |  | Sulphur Dioxide | - Kg |  |  | By calculation from sulphur content of fuel oil. Under oil firing conditions if period of operation exceeds 30 days in any year. |  |
| A3 Package Boiler House, point 14 on site plan | Package Boiler No. 3 | Oxides of Nitrogen (NO and NO2 expressed as NO2) | 300 mg/m3 3 | - | Annual 6 | BS EN 14792 |  |
|  |  | Oxides of Nitrogen (NO and NO2 expressed as NO2) | 450 mg/m3 4 |  |  | BS EN 14792 |  |
|  |  | Particulates | 50 mg/m3 4 |  |  | BS EN 13284-1 and MID |  |
|  |  | Carbon Monoxide | - mg/m3 |  |  | BS EN 15058 under gas firing conditions. BS EN 15058 under oil firing conditions if period of operation exceeds 30 days in any year. |  |
|  |  | Sulphur Dioxide | - Kg |  |  | By calculation from sulphur content of fuel oil. Under oil firing conditions if period of operation exceeds 30 days in any year. |  |
| A4 Package Boiler House, point 14 on site plan | Package Boiler No. 4 | Oxides of Nitrogen (NO and NO2 expressed as NO2) | 300 mg/m3 3 | - | Annual 6 | BS EN 14792 |  |
|  |  | Oxides of Nitrogen (NO and NO2 expressed as NO2) | 450 mg/m3 4 |  |  | BS EN 14792 |  |
|  |  | Particulates | 50 mg/m3 4 |  |  | BS EN 13284-1 and MID |  |
|  |  | Carbon Monoxide | - mg/m3 |  |  | BS EN 15058 under gas firing conditions. BS EN 15058 under oil firing conditions if period of operation exceeds 30 days in any year. |  |
|  |  | Sulphur Dioxide | - Kg |  |  | By calculation from sulphur content of fuel oil. Under oil firing conditions if period of operation exceeds 30 days in any year. |  |
| A5 Coatings 2 Boiler House, point 14a on site plan | Steam Boiler No. 1 | Oxides of Nitrogen (NO and NO2 expressed as NO2) | 300 mg/m3 3 | - | Annual 6 | BS EN 14792 |  |
|  |  | Oxides of Nitrogen (NO and NO2 expressed as NO2) | 450 mg/m3 4 |  |  | BS EN 14792 |  |
|  |  | Particulates | 50 mg/m3 4 |  |  | BS EN 13284-1 and MID |  |
|  |  | Carbon Monoxide | - mg/m3 |  |  | BS EN 15058 under gas firing conditions. BS EN 15058 under oil firing conditions if period of operation exceeds 30 days in any year. |  |
|  |  | Sulphur Dioxide | - Kg |  |  | By calculation from sulphur content of fuel oil. Under oil firing conditions if period of operation exceeds 30 days in any year. |  |
| A6 Coatings 2 Boiler House, point 14a on site plan | Steam Boiler No. 2 | Oxides of Nitrogen (NO and NO2 expressed as NO2) | 300 mg/m3 3 | - | Annual 6 | BS EN 14792 |  |
|  |  | Oxides of Nitrogen (NO and NO2 expressed as NO2) | 450 mg/m3 4 |  |  | BS EN 14792 |  |
|  |  | Particulates | 50 mg/m3 4 |  |  | BS EN 13284-1 and MID |  |
|  |  | Carbon Monoxide | - mg/m3 |  |  | BS EN 15058 under gas firing conditions. BS EN 15058 under oil firing conditions if period of operation exceeds 30 days in any year. |  |
|  |  | Sulphur Dioxide | - Kg |  |  | By calculation from sulphur content of fuel oil. Under oil firing conditions if period of operation exceeds 30 days in any year. |  |
| A7 Coatings 2 Boiler House, point 14a on site plan | High Pressure Hot Water boiler No. 1 | Oxides of Nitrogen (NO and NO2 expressed as NO2) | 300 mg/m3 3 | - | Annual 6 | BS EN 14792 |  |
|  |  | Oxides of Nitrogen (NO and NO2 expressed as NO2) | 450 mg/m3 4 |  |  | BS EN 14792 |  |
|  |  | Particulates | 50 mg/m3 4 |  |  | BS EN 13284-1 and MID |  |
|  |  | Carbon Monoxide | - mg/m3 |  |  | BS EN 15058 under gas firing conditions. BS EN 15058 under oil firing conditions if period of operation exceeds 30 days in any year. |  |
|  |  | Sulphur Dioxide | - Kg |  |  | By calculation from sulphur content of fuel oil. Under oil firing conditions if period of operation exceeds 30 days in any year. |  |
| A8 Coatings 2 Boiler House, point 14a on site plan | High Pressure Hot Water Boiler No. 2 | Oxides of Nitrogen (NO and NO2 expressed as NO2) | 300 mg/m3 3 | - | Annual 6 | BS EN 14792 |  |
|  |  | Oxides of Nitrogen (NO and NO2 expressed as NO2) | 450 mg/m3 4 |  |  | BS EN 14792 |  |
|  |  | Particulates | 50 mg/m3 4 |  |  | BS EN 13284-1 and MID |  |
|  |  | Carbon Monoxide | - mg/m3 |  |  | BS EN 15058 under gas firing conditions. BS EN 15058 under oil firing conditions if period of operation exceeds 30 days in any year. |  |
|  |  | Sulphur Dioxide | - Kg |  |  | By calculation from sulphur content of fuel oil. Under oil firing conditions if period of operation exceeds 30 days in any year. |  |
| A12 No. 1 Colorcoat Line, point 6 on site plan | Regenerative Thermal Oxidiser (Original) | Oxides of Nitrogen (NO and NO2 expressed as NO2) | 100 mg/m3 | - | Annual | BS EN 14792 |  |
|  |  | Carbon Monoxide | 100 mg/m3 5 |  | Continuous | Not for reporting purposes |  |
|  |  | Carbon Monoxide | 100 mg/m3 |  | Annual | BS EN 15058 |  |
|  |  | Volatile Organic Carbon (as C) | 50 mg/m3 |  | Annual | BS EN 12619 |  |
| A12a No. 1 Colorcoat Line, point 6 on site plan | Regenerative Thermal Oxidiser (Replacement) | Oxides of Nitrogen (NO and NO2 expressed as NO2) | 100 mg/m3 | - | Annual | BS EN 14792 |  |
|  |  | Carbon Monoxide | 100 mg/m3 5 |  | Continuous | Not for reporting purposes |  |
|  |  | Carbon Monoxide | 100 mg/m3 |  | Annual | BS EN 15058 |  |
|  |  | Volatile Organic Carbon (as C) | 50 mg/m3 |  | Annual | BS EN 12619 |  |
| A13 No. 1 Colorcoat Line, point 6 on site plan | Coater House Extraction LEV | Volatile Organic Carbon (as C) | - mg/m3 | - | Annual | BS EN 12619 |  |
| A14 No. 1 Colorcoat Line, point 6 on site plan | Wash Tank Extraction LEV | Volatile Organic Carbon (as C) | - mg/m3 | - | Annual | BS EN 12619 |  |
| A15 No. 1 Colorcoat Line, point 6 on site plan | Paint Kitchen Extraction LEV | Volatile Organic Carbon (as C) | - mg/m3 | - | Annual | BS EN 12619 |  |
| A16 No. 1 Colorcoat Line, point 6 on site plan | Pre Clean Extraction LEV | - | - | - | - | - |  |
| A18 – No. 1 Colorcoat Line, point 6 on site plan | COBRA Regenerative Thermal Oxidiser | Oxides of Nitrogen (NO and NO2 expressed as NO2) | 100 mg/m3 | - | Annual | BS EN 14792 |  |
|  |  | Carbon Monoxide | 100 mg/m3 5 |  | Continuous | Not for reporting purposes |  |
|  |  | Carbon Monoxide | 100 mg/m3 |  | Annual | BS EN 15058 |  |
|  |  | Volatile Organic Carbon (as C) | 20 mg/m3 |  | Annual | BS EN 12619 |  |
| A21 No. 2 Colorcoat Line, point 17 on site plan | Thermal Oxidiser Unit (Original)/Regenerative Thermal Oxidiser Unit (Replacement) | Oxides of Nitrogen (NO and NO2 expressed as NO2) | 100 mg/m3 | - | Annual | BS EN 14792 |  |
|  |  | Carbon Monoxide | 100 mg/m3 5 |  | Continuous | Not for reporting purposes |  |
|  |  | Carbon Monoxide | 100 mg/m3 |  | Annual | BS EN 15058 |  |
|  |  | Volatile Organic Carbon (as C) | 20 mg/m3 |  | Annual | BS EN 12619 |  |
| A22 No. 2 Colorcoat Line, point 17 on site plan | Paint Kitchen Extraction LEV | - | - | - | - | - |  |
| A23 No. 2 Colorcoat Line, point 17 on site plan | Pre Clean Extraction LEV | - | - | - | - | - |  |
| A31 No. 5 Galvanising Line, point 7 on site plan | Direct Fired Furnace Stack (waste heat boiler not used) | Carbon Monoxide | - mg/m3 | - | Annual | BS EN 15058 |  |
|  |  | Oxides of Nitrogen (NO and NO2 expressed as NO2) |  |  |  | BS EN 14792 |  |
| A32 No. 5 Galvanising Line, point 7 on site plan | Direct Fired Furnace Stack (including waste heat boiler) | Carbon Monoxide | - mg/m3 | - | Annual | BS EN 15058 |  |
|  |  | Oxides of Nitrogen (NO and NO2 expressed as NO2) |  |  |  | BS EN 14792 |  |
| A33 No. 5 Galvanising Line, point 7 on site plan | Radiant Tube Furnace Stack | Carbon Monoxide | - mg/m3 | - | Annual | BS EN 15058 |  |
|  |  | Oxides of Nitrogen (NO and NO2 expressed as NO2) |  |  |  | BS EN 14792 |  |
| A34 No. 5 Galvanising Line, point 7 on site plan | Former Chromate Extraction | - | - | - | - | - |  |
| A35 No. 6 Galvanising Line, point 8 on site plan | Direct Fired Furnace and Radiant Tube Furnace Stack | Carbon Monoxide | - mg/m3 | - | Annual | BS EN 15058 |  |
|  |  | Oxides of Nitrogen (NO and NO2 expressed as NO2) |  |  |  | BS EN 14792 |  |

Note 1: Or as subsequently recommended in Technical Guidance Note M2 or devolved equivalent

Note 2: All thermal oxidiser emissions and furnace emissions are to be reported as actual oxygen, not corrected.

Note 3: Limit under gas firing conditions

Note 4: Limit under oil firing conditions

Note 5: Limit based on 24-hour average of 15 minute values

Note 6: Monitoring only to be undertaken if period of operation exceeds 30 days in any year

| Table S3.2 Point Source emissions to water (other than sewer) and land – emission limits and monitoring requirements |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Emission point ref. & location | Source | Parameter | Limit (incl. unit) | Reference Period | Monitoring frequency |  | Monitoring standard or method |
| W1 – Broken Bank Pumping House discharging to the River Dee | Lagoon collecting all site surface waters, treated process effluent and waste water from water supply treatment plant | Flow | 15,000 m3/day(4 hours commencing one hour before each high tide) | - | Continuous |  | Method to be agreed in writing with NRW |
|  |  | Flow at all other times | 0 |  | Continuous |  |  |
|  |  | pH | 5 - 9 |  | Daily sample 1 |  |  |
|  |  | Suspended solids (mg/l) | 100 |  | Daily sample 1 |  |  |
|  |  | Chemical Oxygen Demand (mg/l) | 200 |  | Daily sample 1 |  |  |
|  |  | Iron (mg/l) | 10 |  | Daily sample 1 |  |  |
|  |  | Chromium (mg/l) | 0.3 |  | Daily sample 1 |  |  |
|  |  | Mercury (µg/l) | 10 |  | Every 3 months |  |  |
|  |  | Nickel (mg/l) | 0.6 |  | Daily sample 1 |  |  |
|  |  | Zinc (mg/l) | 0.8 |  | Daily sample 1 |  |  |
|  |  | Ammoniacal Nitrogen (mg/l) | - |  | Daily sample 1 |  |  |
| Effluent Plant Discharge | Effluent Plant Discharge | pH | - | - | Daily sample 1 |  | Method to be agreed in writing with NRW |
| Effluent Plant Discharge | Effluent Plant Discharge | Iron (mg/l) | - | - | Daily sample 1 |  | Method to be agreed in writing with NRW |
| Effluent Plant Discharge | Effluent Plant Discharge | Chromium (mg/l) | - | - | Daily sample 1 |  | Method to be agreed in writing with NRW |
| Effluent Plant Discharge | Effluent Plant Discharge | Nickel (mg/l) | - | - | Daily sample 1 |  | Method to be agreed in writing with NRW |
| Effluent Plant Discharge | Effluent Plant Discharge | Zinc (mg/l) | - | - | Daily sample 1 |  | Method to be agreed in writing with NRW |
| Effluent Plant Discharge | Effluent Plant Discharge | Mercury (µg/l) | - | - | Every 3 months |  | Method to be agreed in writing with NRW |

Note 1: Monitoring requirement suspended if effluent plant not operational and therefore not discharging

| Table S3.3 Annual limits |  |  |
| --- | --- | --- |
| Substance | Medium | Limit (including unit) |
| - | - | - |

| Table S3.4 Process monitoring requirements |  |  |  |  |
| --- | --- | --- | --- | --- |
| Emission point reference or source or description of point of measurement | Parameter | Monitoring frequency | Monitoring standard or method | Other specifications |
| Thermal oxidisers on No.1 and No.2 Colorcoat Lines | Combustion temperature | Continuous monitoring | - | - |
| Thermal oxidisers on No.1 and No.2 Colorcoat Lines | Flame failure detection | Continuous monitoring | - | - |

Schedule 4 - Reporting

Parameters, for which reports shall be made, in accordance with conditions of this permit, are listed below.

| Table S4.1 Reporting of monitoring data |  |  |  |
| --- | --- | --- | --- |
| Parameter | Emission or monitoring point/reference | Reporting period | Period begins |
| Sulphur Dioxide (Kg) | A1 to A8 | Annually | 17/03/2004 1 |
| Oxides of Nitrogen (NO and NO2 expressed as NO2) (mg/m3) | A1 to A8 | Annually | 17/03/2004 2 |
| Carbon Monoxide (mg/m3) | A1 to A8 | Annually | 17/03/2004 2 |
| Oxides of Nitrogen (NO and NO2 expressed as NO2) (mg/m3) | A1 to A8 | Annually | 17/03/2004 3 |
| Particulates (mg/m3) | A1 to A8 | Annually | 17/03/2004 3 |
| Carbon Monoxide (mg/m3) | A1 to A8 | Annually | 17/03/2004 3 |
| Oxides of Nitrogen (NO and NO2 expressed as NO2) (mg/m3) | A12 4, A12a, A18, A21, A31, A32, A33 and A35 | Annually | 17/03/2004 |
| Carbon Monoxide (mg/m3) | A12 4, 5, A12a 5, A18 5 and A21 5 | Annually | 17/03/2004 |
| VOCs (mg/m3) | A12 4, A12a, A13 to A15, A18 and A21 | Annually | 17/03/2004 |
| Flow (m3/day) | W1 | Every 3 months | 01/04/2004 (mean and maximum) |
| Chemical Oxygen Demand (mg/l) | W1 | Every 3 months | 01/04/2004 (mean and maximum) |
| Suspended Solids (mg/l) | W1 | Every 3 months | 01/04/2004 (mean and maximum) |
| pH | W1 and Effluent Plant | Every 3 months | 01/04/2004 (minimum and maximum) |
| Iron (mg/l) | W1 and Effluent Plant | Every 3 months | 01/04/2004 (mean and maximum) |
| Chromium (mg/l) | W1 and Effluent Plant | Every 3 months | 01/04/2004 (mean and maximum) |
| Mercury (µg/l) | W1 and Effluent Plant | Every 3 months | 01/04/2004 |
| Nickel (mg/l) | W1 and Effluent Plant | Every 3 months | 01/04/2004 (mean and maximum) |
| Zinc (mg/l) | W1 and Effluent Plant | Every 3 months | 01/04/2004 (mean and maximum) |
| Ammoniacal Nitrogen (mg/l) | W1 | Every 3 months | 01/04/2004 (mean and maximum) |
| Water usage | - | Annually | 17/03/2004 |
| Energy usage | - | Annually | 17/03/2004 |
| Waste disposal and/or recovery | - | Annually | 17/03/2004 |

Note 1: Calculation from sulphur content of fuel oil and fuel oil consumption

Note 2: For gas firing conditions

Note 3: For oil firing conditions if period of operation exceeds 30 days in any year

Note 4: A12 to be removed from condition on confirmation of decommissioning of redundant thermal oxidiser

Note 5: Reported on basis of annual monitoring result

| Table S4.2: Annual production/treatment |  |
| --- | --- |
| Parameter | Units |
| Production of galvanised steel product | tonnes |
| Production of colorcoated steel product | tonnes |
| Total production of coated steel products | tonnes |

| Table S4.3 Performance parameters |  |  |
| --- | --- | --- |
| Parameter | Frequency of assessment | Units 1 |
| Primary energy use | Annually | MW-hr/tonne |
| Total VOC emission to air as Carbon | Annually | Kg/tonne 2 |
| VOC Fugitive emissions value | Annually | % |
| Potable water use | Annually | m3/tonne |
| Non potable water use | Annually | m3/tonne |
| Quantity of hazardous waste | Annually | Kg/tonne |
| Quantity of non-hazardous waste | Annually | Kg/tonne |

Note 1: Performance indicator should be referenced to total production of coated steel products unless otherwise stated

Note 2: VOC emissions should be referenced to production of colorcoated steel products only

| Table S4.4 Reporting forms |  |  |
| --- | --- | --- |
| Media/parameter | Reporting format | Date of form |
| Air | Form air 1 or other form as agreed in writing by Natural Resources Wales | 25/04/2018 |
| Water (excluding sewer) | Form water 1 or other form as agreed in writing by Natural Resources Wales | 25/04/2018 |
| Water usage | Form water usage 1 or other form as agreed in writing by Natural Resources Wales | 25/04/2018 |
| Energy usage | Form energy 1 or other form as agreed in writing by Natural Resources Wales | 25/04/2018 |
| Other performance indicators | Form performance 1 or other form as agreed in writing by Natural Resources Wales | 25/04/2018 |

# Schedule 5 - Notification

These pages outline the information that the operator must provide.

Units of measurement used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission. Where appropriate, a comparison should be made of actual emissions and authorised emission limits.

#### If any information is considered commercially confidential, it should be separated from non-confidential information, supplied on a separate sheet and accompanied by an application for commercial confidentiality under the provisions of the EP Regulations.

Part A

| Permit Number |  |
| --- | --- |
| Name of operator |  |
| Location of Facility |  |
| Time and date of the detection |  |

| (a) Notification requirements for any activity that gives rise to an incident or accident which significantly affects or may significantly affect the environment |  |
| --- | --- |
| To be notified Immediately |  |
| Date and time of the event |  |
| Reference or description of the location of the event |  |
| Description of where any release into the environment took place |  |
| Substances(s) potentially released |  |
| Best estimate of the quantity or rate of release of substances |  |
| Measures taken, or intended to be taken, to stop any emission |  |
| Description of the failure or accident. |  |

| (b) Notification requirements for the breach of a permit condition |  |
| --- | --- |
| To be notified immediately |  |
| Emission point reference/ source |  |
| Parameter(s) |  |
| Limit |  |
| Measured value and uncertainty |  |
| Date and time of monitoring |  |
| Measures taken, or intended to be taken, to stop the emission |  |

| Time periods for notification following detection of a breach of a limit |  |
| --- | --- |
| Parameter | Notification period |

| (c) In the event of a breach of permit condition which poses an immediate danger to human health or threatens to cause an immediate significant adverse effect on the environment: |  |
| --- | --- |
| To be notified immediately |  |
| Description of where the effect on the environment was detected |  |
| Substances(s) detected |  |
| Concentrations of substances detected |  |
| Date of monitoring/sampling |  |

Part B - to be submitted as soon as practicable

| Any more accurate information on the matters for notification under Part A. |  |
| --- | --- |
| Measures taken, or intended to be taken, to prevent a recurrence of the incident |  |
| Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment which has been or may be caused by the emission |  |
| The dates of any unauthorised emissions from the facility in the preceding 24 months. |  |

| Name* |  |
| --- | --- |
| Post |  |
| Signature |  |
| Date |  |

* authorised to sign on behalf of the operator

Schedule 6 - Interpretation

“accident” means an accident that may result in pollution.

“application” means the application for this permit, together with any additional information supplied by the operator as part of the application and any response to a notice served under Schedule 5 to the EP Regulations.

“authorised officer” means any person authorised by Natural Resources Wales under section 108(1) of The Environment Act 1995 to exercise, in accordance with the terms of any such authorisation, any power specified in section 108(4) of that Act.

“disposal” means any of the operations provided for in Annex IIA to Directive 2006/12/EC of the European Parliament and of the Council of 5 April 2006 on Waste.

“EP Regulations” means The Environmental Permitting (England and Wales) Regulations SI 2016 No.1154 and words and expressions used in this permit which are also used in the Regulations have the same meanings as in those Regulations.

“emissions of substances not controlled by emission limits” means emissions of substances to air, water or land from the activities, either from the emission points specified in schedule 3 or from other localised or diffuse sources, which are not controlled by an emission limit..

“groundwater” means all water, which is below the surface of the ground in the saturation zone and in direct contact with the ground or subsoil.

“hazardous property” has the meaning in Annex lll of the Waste Framework Directive.

“Industrial Emissions Directive” means DIRECTIVE 2010/75/EU OF THE EUROPEAN PARLIAMENT AND OF THE COUNCIL of 24 November 2010 on industrial emissions.

“MCERTS” means the Environment Agency’s Monitoring Certification Scheme.

“recovery” means any of the operations provided for in Annex II to Directive 2008/98/EC of the European Parliament and of the Council on waste.

“Waste code” means the six digit code referable to a type of waste in accordance with the list of wastes established by Commission Decision 2000/532/EC as amended from time to time (the ‘List of Wastes Decision’) and in relation to hazardous waste, includes the asterisk.

“year” means calendar year ending 31 December.

Where a minimum limit is set for any emission parameter, for example pH, reference to exceeding the limit shall mean that the parameter shall not be less than that limit.

Unless otherwise stated, any references in this permit to concentrations of substances in emissions into air means:

in relation to emissions from combustion processes (other than thermal oxidisers and furnaces), the concentration in dry air at a temperature of 273K, at a pressure of 101.3 kPa and with an oxygen content of 3% dry for liquid and gaseous fuels, 6% dry for solid fuels; and/or

in relation to emissions from thermal oxidisers, furnaces and non-combustion sources, the concentration at a temperature of 273K and at a pressure of 101.3 kPa, with no correction for water vapour content

Schedule 7 - Site plan

End of Permit