Permit Reference Number: EPR/MP3239FQ



Variation Reference Number: EPR/MP3239FQ V002




Operator: Tradebe Healthcare National Limited 






Form Number: Agency Form / A1/ AP3538SM/ Form Dated 20 October 2011
Installation: Wrexham Clinical Waste Incinerator

Reporting of Emissions to Air for the period from July 2017 to December  2017
	Emission

Point
	Substance /

Parameter
	Emission

Limit Value
	Result 
Note 1
	Test

Method

Note 2
	Sample

Date and Times
Note 3
	Accreditation/ Certification 
Note 4
	Uncertainty

Note 5

	A1
	Particulate Matter

mg/m3
	20 mg/m3

periodic over minimum 1-hour period
	2.7
	BS EN 13284-1
	29/09/2017
11:00 - 11:30, 11:31 - 12:01
	UKAS & MCERTS
	+/ -0.62

	A1
	Total Organic Carbon (TOC)

mg/m3
	20 mg/m3

periodic over minimum 1-hour period
	3.3
	BS EN 12619
	28/07/2017
11:30 - 12:30
	UKAS & MCERTS
	+/- 1.2

	A1
	Oxides of Nitrogen (as NO2)

mg/m3
	400 mg/m3

periodic over minimum 4-hour period
	229
	BS EN 14792
	28/07/2017

11:30 - 12:30
	UKAS & MCERTS
	+/- 10.6

	A1
	Carbon Monoxide

mg/m3
	100 mg/m3

periodic over minimum 4-hour period
	21.4
	BS EN 15058
	28/07/2017

11:30 - 12:30
	UKAS & MCERTS
	+/- 2.2

	A1
	Sulphur Dioxide

mg/m3
	200 mg/m3

periodic over minimum 4-hour period
	0.15
	BS EN14791
	28/07/2017

11:00 - 15:00
	UKAS & MCERTS
	+/- 0.02

	A1
	Hydrogen chloride

mg/m3
	30 mg/m3

periodic over minimum 1-hour period
	11.2
	BS EN 1911
	29/09/2017

11:00 - 11:30, 11:31 - 12:01
	UKAS & MCERTS
	+/- 1.2

	A1
	Hydrogen fluoride
mg/m3
	2 mg/m3

periodic over minimum 1-hour period
	<0.13
	BS ISO 15713
	27/09/2017

13:58 - 14:58
	UKAS & MCERTS
	+/- 0.02

	A1
	Cadmium & thallium and their compounds (total)

mg/m3
	0.05 mg/m3 periodic over minimum 30 minute, maximum 8 hour period
	0.002
	BS EN 14385
	29/09/2017

09:46 - 10:16, 10:18 - 10:48
	UKAS & MCERTS
	+/- 0.0003

	A1
	Mercury and its compounds

mg/m3
	0.05 mg/m3 periodic over minimum 30 minute, maximum 8 hour period
	0.0007
	BS EN 13211
	29/09/2017

09:46 - 10:16, 10:18 - 10:48
	UKAS & MCERTS
	+/- 0.0001

	A1
	Sb, As, Pb, Cr, Co, Cu, Mn, Ni and V and their compounds (total)
mg/m3
	0.5 mg/m3 periodic over minimum 30 minute, maximum 8 hour period
	0.18
	BS EN 14385
	29/09/2017

09:46 - 10:16, 10:18 - 10:48
	UKAS & MCERTS
	+/- 0.03

	A1
	Dioxins / furans (I-TEQ)6
ng/m3
	0.1 ng/m3 periodic over minimum 6 hours, maximum 8 hour period
	0.021-0.021
	BS EN 1948
	28/09/2017
09:53 - 12:53, 12:55 - 15:55
	UKAS & MCERTS
	+/- 0.005

	A1
	Dioxin-like PCBs (WHO-TEQ Humans / Mammals)6 ng/m3
	No limit applies
	0.00074-0.00074
  
	BS EN 1948
	28/09/2017

09:53 - 12:53, 12:55 - 15:55
	UKAS & MCERTS
	+/- 0.000163

	A1
	Dioxin-like PCBs (WHO-TEQ Fish)6
ng/m3
	No limit applies
	0.00004-0.00004
	BS EN 1948
	28/09/2017

09:53 - 12:53, 12:55 - 15:55
	UKAS & MCERTS
	+/- 0.000008

	A1
	Dioxin-like PCBs (WHO-TEQ Birds)6
ng/m3
	No limit applies
	0.00186 -0.00186
	BS EN 1948
	28/09/2017

09:53 - 12:53, 12:55 - 15:55
	UKAS & MCERTS
	+/- 0.000413

	A1
	poly-cyclic aromatic hydrocarbons (PAHs) ug/m3
	No limit applies
	2.7
	BS ISO 11338
	27/09/2017
10:55 - 13:55, 13:57 - 16:57
	UKAS & MCERTS
	+/- 0.62

	A1
	Dioxins / furans (WHO-TEQ Humans / Mammals) 6

ng/m3
	No limit applies
	0.019 -0.019
	BS EN 1948
	28/09/2017

09:53 - 12:53, 12:55 - 15:55
	UKAS & MCERTS
	+/- 0.004

	A1
	Dioxins / furans (WHO-TEQ  Fish)6
ng/m3
	No limit applies
	0.021 - 0.021
	BS EN 1948
	28/09/2017

09:53 - 12:53, 12:55 - 15:55
	UKAS & MCERTS
	+/- 0.005

	A1
	Dioxins / furans (WHO-TEQ Birds)6
ng/m3
	No limit applies
	0.032 - 0.032
	BS EN 1948
	28/09/2017

09:53 - 12:53, 12:55 - 15:55
	UKAS & MCERTS
	+/- 0.007

	A1
	Anthanthrene
ug/m3
	No limit applies
	<0.03
	BS ISO 11338
	27/09/2017

10:55 - 13:55, 13:57 - 16:57
	UKAS & MCERTS
	+/- 0.01

	A1
	Benzo{a}anthracene
ug/m3
	No limit applies
	<0.03
	BS ISO 11338
	27/09/2017

10:55 - 13:55, 13:57 - 16:57
	UKAS & MCERTS
	+/- 0.01

	A1
	Benzo[b]fluoranthene
ug/m3
	No limit applies
	<0.03
	BS ISO 11338
	27/09/2017

10:55 - 13:55, 13:57 - 16:57
	UKAS & MCERTS
	+/- 0.01

	A1
	Benzo[k]fluoranthene
ug/m3
	No limit applies
	<0.03
	BS ISO 11338
	27/09/2017

10:55 - 13:55, 13:57 - 16:57
	UKAS & MCERTS
	+/- 0.01

	A1
	Benzo[b]naph(2,1-d}thiophene
ug/m3
	No limit applies
	<0.03
	BS ISO 11338
	27/09/2017

10:55 - 13:55, 13:57 - 16:57
	UKAS & MCERTS
	+/- 0.01

	A1
	Benzo[c]phenanthrene
ug/m3
	No limit applies
	<0.03
	BS ISO 11338
	27/09/2017

10:55 - 13:55, 13:57 - 16:57
	UKAS & MCERTS
	+/- 0.01

	A1
	Benzo[ghi]perylene
ug/m3
	No limit applies
	<0.03
	BS ISO 11338
	27/09/2017

10:55 - 13:55, 13:57 - 16:57
	UKAS & MCERTS
	+/- 0.01

	A1
	Benzo[a]pyrene
ug/m3
	No limit applies
	<0.03
	BS ISO 11338
	27/09/2017

10:55 - 13:55, 13:57 - 16:57
	UKAS & MCERTS
	+/- 0.01

	A1
	Cholanthrene
ug/m3
	No limit applies
	<0.03
	BS ISO 11338
	27/09/2017

10:55 - 13:55, 13:57 - 16:57
	UKAS & MCERTS
	+/- 0.01

	A1
	Chrysene
ug/m3
	No limit applies
	<0.03
	BS ISO 11338
	27/09/2017

10:55 - 13:55, 13:57 - 16:57
	UKAS & MCERTS
	+/- 0.01

	A1
	Cyclopenta(c,d)pyrene
ug/m3
	No limit applies
	<0.03
	BS ISO 11338
	27/09/2017

10:55 - 13:55, 13:57 - 16:57
	UKAS & MCERTS
	+/- 0.01

	A1
	Dibenzo[ah]anthracene
ug/m3
	No limit applies
	<0.03
	BS ISO 11338
	27/09/2017

10:55 - 13:55, 13:57 - 16:57
	UKAS & MCERTS
	+/- 0.001

	A1
	Dibenzo[a,i]pyrene
ug/m3
	No limit applies
	<0.12
	BS ISO 11338
	27/09/2017

10:55 - 13:55, 13:57 - 16:57
	UKAS & MCERTS
	+/- 0.03

	A1
	Fluoranthene
ug/m3
	No limit applies
	0.22
	BS ISO 11338
	27/09/2017

10:55 - 13:55, 13:57 - 16:57
	UKAS & MCERTS
	+/- 0.05

	A1
	Indo[1,2,3-cd]pyrene
ug/m3
	No limit applies
	<0.03
	BS ISO 11338
	27/09/2017

10:55 - 13:55, 13:57 - 16:57
	UKAS & MCERTS
	+/- 0.01

	A1
	Naphthalene
ug/m3
	No limit applies
	1.97
	BS ISO 11338
	27/09/2017

10:55 - 13:55, 13:57 - 16:57
	UKAS & MCERTS
	+/- 0.45


Note 1 
The result given is the maximum value (or the minimum value in the case of a limit that is expressed as a minimum) obtained during the reporting period, expressed in the same 
terms as the emission limit value. Where the emission limit value is expressed as a range, the result is given as the ‘minimum – maximum’ measured values.
Note 2
Where an internationally recognised standard test method is used the reference number is given. Where another method that has been formally agreed with the Agency is used, 
then the appropriate identifier is given. In other cases the principal technique is stated, e.g. gas chromatography.

Note 3 
For non-continuous measurements the date and time of the sample that produced the result is given. For continuous measurements the percentage of the process operating time 
covered by the result is given. 
Note 4
The accreditation status of the equipment and/or the monitoring organisation, as appropriate, for the methods used for both sampling and analysis.

Note 5
The uncertainty associated with the quoted result at the 95% confidence interval, unless otherwise stated.

Note 6
The result to be reported as a range based on: All congeners less than the detection limit assumed to be zero as a minimum, and all congeners less than the detection limit assumed to be 
at the detection limit as a maximum

Signed …………………V Norris……………………….  







Date……23/01/2018…………………..   



(Authorised to sign as representative of Tradebe Healthcare National Limited)
