[image: image1.jpg]Cyfoeth
Naturiol
Cymru

Natural
Resources
Wales




Wrexham Clinical Waste Incinerator
Meeting Notes
01st October 2014 10:00hrs Buckley
Attendees: 
Lara Cubley NRW (LC)



Eirian Macdonald (EM)
Chris Dunckley Tradebe (CD)


Stephen Blay (SB)
Alan Gartside (AG)

	Item
	Note
	Action

	1
	Meeting held to discuss the documentation prepared by Sita for the variation of the Wrexham Incinerator to move from Clinical to Hazardous.
	

	2
	Site plan needs to be better quality. 
	CD

	3
	The Application requires much more detail on system for introducing liquid waste streams and new waste streams including their storage.  
Options for liquid waste with process and rationale behind moving from one option to next (i.e. drummed to tank waste) to be provided in application.  This is also the case for other solid feeds.


	CD

	4
	The design philosophy of the incinerator must be re-visited to ensure the system is capable of taking the newly proposed waste types and volume.  The question of CV and increased volumetric flow of the efflux gases must be addressed with regard to impact on emissions and the abatement system, as well as additional controls thus required.
	CD

	5
	The Operator must use the correct version of H1 and ensure that the effective height is as per guidance.
NRW to provide correct H1 version.
	CD
LC

	6
	Sita may also want to take radioactive waste in the future.  This would currently require a separate RSR permit.
	

	7
	The Operator must also provide details of knock on impacts of additional storage of wastes coming in, wastes out (APC and BA), including reagents.  Details of location and storage standards to be provided with the application.
	CD

	8
	More detail regarding the new EWCs planned to be accepted at the site must be provided.  In particular, how they will be managed and your capability for treating and accepting them.  You can do this for groups of them not individual.  Waste acceptance procedures to be provided.  Restrictions should be put in place to ensure wastes are only incinerated if not feasible to recycle or otherwise higher up the chain of utility. 
	CD

	9
	The Operator is to undertake air dispersion modelling with updated data. 
	CD

	10
	EM to advice on where to use short term/long term limits.

	EM

	11
	Operator to submit Health Impact Assessment as part of application.


	CD

	12
	The variation is deemed to be a substantial change.  As such the Operator is advised to allow a 4 – 6 month determination period if the application is of good quality.  However, this can take even longer if the application is poor or significant amounts of additional information need to be submitted.
	


