NOTIFICATION OF EMERGENCY RELIEF VENT OPERATION

Notification in accordance with PPC permit condition 5.1.1.6

| Permit number: | WP3836ZF |
| --- | --- |
| Name of operator: | Tradebe Healthcare National Limited |
| Location of installation | Marlborough Rd, Wrexham Industrial Estate, Wrexham LL13 9RJ |
| Location of emission: | Release Point A2 – Incinerator Emergency Relief Vent |
| The emergency relief vent opened at: | 09.45 19/06/2017 (ref1703212) |
| Duration of operation: | 2 hour 0 minute |
| Reasons for operation: | Loss of 110v supply to the ID fan Inverter, this was due to loose wiring within the panel that feeds a 415v to 110v transformer. This was discovered during the investigation to why the ERV had previously lifted on the 17th June 17. |
| Measures taken to prevent a reoccurrence: | Plan to rewire the circuit during the July shutdown. Electrical wiring secured. |
| The plant returned to normal operation at: | 12.00 19/06/2017 |

Notified by:	Vince Norris

Position:	Site Manager

Notification completed at: 			    11.45 	20/06/17