## Air 1
Reporting of emissions to air for the period from 01/01/2015 to 31/03/2015
Operator: E.ON UK |  |  | Site Location: Connahs Quay
Permit/Variation Number: MP3337SH |  |  | Release Points: A11, A12
Release Point | Substance / Parameter | ELV (mg/m3) | Reference Period | Result (mg/m3)
A11 | Oxides of Nitrogen (NO and NO2 expressed as NO2) | 95 | 10 min average | 90
A12 | Oxides of Nitrogen (NO and NO2 expressed as NO2) | 95 | 10 min average | 87*
A11 | Carbon Monoxide | 10 | 10 min average | 8
A12 | Carbon Monoxide | 100 | 10 min average | 22*
A11 | Sulphur dioxide | 9950 | 10 min average | 193
*External monitoring completed by E.ON Engineering wk commencing 22nd July 2014
Signed on behalf of the Operator ……...……………………………………………..
Form Ref: Air - 1 / Connahs Quay PS (01/12/06)

## Air 2
Releases to Air - LCPD/PPC Continuous Measurement
Operational Summary for the 3 months to 31/03/2015
Operator: E.ON UK |  |  |  | Site Location: Connah's Quay
Release Points: A1, A2, A3, A4 |  |  |  | Permit/Variation Number: MP3337SH
Release Point | Pollutant | Month | ELV (mg/m3) | Max Daily Average | Calendar Monthly Mean | 95% of validated hourly means
A1 | NOx | Jan | 75 | 51.1 | 46.94 | 52.6
A1 | CO | Jan | 30 | 2.14 | 1.56 | 1.5
A1 | NOx | Feb | 75 | 55.01 | 48.82 | 51.9
A1 | CO | Feb | 30 | 1.7 | 1.45 | 1.6
A1 | NOx | Mar | 75 | 58.67 | 48.41 | 60.1
A1 | CO | Mar | 30 | 1.88 | 1.52 | 1.5
A1 | NOx | Annual | 75 |  |  | Due at end of year
A1 | CO | Annual | 30 |  |  | Due at end of year
A2 | NOx | Jan | 75 | 31.99 | 28.7 | 32.6
A2 | CO | Jan | 30 | 6.08 | 3.01 | 3
A2 | NOx | Feb | 75 | 34.55 | 29.09 | 31.5
A2 | CO | Feb | 30 | 6.1 | 2.39 | 2.9
A2 | NOx | Mar | 75 | 38.67 | 24.92 | 28.1
A2 | CO | Mar | 30 | 11.62 | 5.96 | 22.3
A2 | NOx | Annual | 75 |  |  | Due at end of year
A2 | CO | Annual | 30 |  |  | Due at end of year
A3 | NOx | Jan | 75 | 51.83 | 41.19 | 52.1
A3 | CO | Jan | 30 | 1.54 | 1.4 | 1.8
A3 | NOx | Feb | 75 | 47.74 | 37.03 | 51.1
A3 | CO | Feb | 30 | 1.89 | 1.61 | 2.1
A3 | NOx | Mar | 75 | 44.94 | 36.22 | 47.6
A3 | CO | Mar | 30 | 1.8 | 1.44 | 1.4
A3 | NOx | Annual | 75 |  |  | Due at end of year
A3 | CO | Annual | 30 |  |  | Due at end of year
A4 | NOx | Jan | 75 | 31.17 | 29.53 | 31.5
A4 | CO | Jan | 30 | 9.65 | 3.12 | 1.3
A4 | NOx | Feb | 75 | 31.55 | 29.87 | 31.1
A4 | CO | Feb | 30 | 13.17 | 4.31 | 10.1
A4 | NOx | Mar | 75 | 31.73 | 28.92 | 32.2
A4 | CO | Mar | 30 | 12.53 | 3.81 | 1.4
A4 | NOx | Annual | 75 |  |  | Due at end of year
A4 | CO | Annual | 30 |  |  | Due at end of year
Notes - 1 | Compliance with LCPD articles 4.1, 4.3 require measurement results for:
Nitrogen oxides (as NO2) to demonstrate that:
i) none of the validated daily averages exceeds the ELV
ii) 95% of all validated hourly averages do not exceed 150% of the ELV
Signed.............................................................. |  |  |  | Date......................................................
(Authorised to sign as a representative of operator)
Air - 2 LCPD Continuous (01/12/06)