## LCP 96
RELEASES TO AIR
QUARTERLY RETURN
MONTHLY MEAN, MAXIMUM DAILY MEAN AND ANNUAL PERCENTILE CONCENTRATIONS (a),(b),(c)
OPERATING MODE: | NORMAL
Operator: | Uniper UK Ltd |  | Form: |  | ESI/03B (Gas Turbines)
Location: | Connah's Quay |  | Version/date: |  | V.10.6 Oct 2015
Permit/Variation Number: | NP3037AF | LCP96
Year: | LCP:
| NOx (mg/m3) |  |  | CO (mg/m3)
Month | Monthly Mean (d) | Max Daily Mean (d) | Part Load Max Daily Mean (e) | Monthly Mean (d) | Max Daily Mean (d) | Part Load Max Daily Mean (e)
January | - | - | - | - | - | -
February | 21.728 | 24.224 | 24.224 | 1.08 | 9 | 58.23
March | 20.752 | 23 | 23.056 | 0.9 | 6.12 | 6.12
April
May
June
July
August
September
October
November
December
Monthly ELV/Daily ELV (f) | 75 | 75 | 75 | 30 | 30 | 200
Annual 95th Percentile (g) | - | - | - | - | - | -
Annual Percentile ELV (h) | 110 | - | - | 60 | - | -
NOTES:
(a) All data based on validated hourly average concentrations, excluding start-up and shut-down and periods of malfunction or breakdown of abatement equipment, at 15% O2, dry, 273.15K, 101.325 kPa
(b) Annual percentiles are submitted with the final return (Quarter 4)
(c) Extend report to cover the required number of LCP on each site and repeat report for each separately regulated Operating Mode as required, e.g., Combined Cycle, Open Cycle, Supplementary firing, Auxiliary firing
(d) Averages determined at loads in the range 70% < Load ≤ 100% ISO base load and above
(e) Averages determined at loads in the range MSUL* < Load ≤ 100% ISO base load and above (* For a 3 parameter approach, from the point of Start-Up to the point of Shut-down)
(f) Leave the Daily ELV blank if this is applied as a 95th percentile ELV within the Permit
(g) For each pollutant, report the Annual 95th percentile ELV for hourly averages in the first column and, if applicable, the Annual 95th percentile ELV for daily means in the second column
(h For each pollutant, report the Annual 95th percentile of hourly averages in the first column and, if applicable, the Annual 95th percentile of daily means in the second column
Signed on behalf of the Operator by: |  |  | ……………..………………………………………………..
Date of return: |  |  | ……………..………………………………………………..

## LCP 97
RELEASES TO AIR
QUARTERLY RETURN
MONTHLY MEAN, MAXIMUM DAILY MEAN AND ANNUAL PERCENTILE CONCENTRATIONS (a),(b),(c)
OPERATING MODE: | NORMAL
Operator: | Uniper UK Ltd |  | Form: |  | ESI/03B (Gas Turbines)
Location: | Connah's Quay |  | Version/date: |  | V.10.6 Oct 2015
Permit/Variation Number: | NP3037AF | LCP97
Year: | LCP:
| NOx (mg/m3) |  |  | CO (mg/m3)
Month | Monthly Mean (d) | Max Daily Mean (d) | Part Load Max Daily Mean (e) | Monthly Mean (d) | Max Daily Mean (d) | Part Load Max Daily Mean (e)
January | 25.152 | 27.184 | 27.184 | 0.72 | 1.8 | 23.22
February | 25.648 | 26.984 | 26.984 | 0.72 | 0.9 | 12.6
March | 25.576 | 27.704 | 27.704 | 0.72 | 1.17 | 2.07
April
May
June
July
August
September
October
November
December
Monthly ELV/Daily ELV (f) | 75 | 75 | 75 | 30 | 30 | 200
Annual 95th Percentile (g) | - | - | - | - | - | -
Annual Percentile ELV (h) | 110 | - | - | 60 | - | -
NOTES:
(a) All data based on validated hourly average concentrations, excluding start-up and shut-down and periods of malfunction or breakdown of abatement equipment, at 15% O2, dry, 273.15K, 101.325 kPa
(b) Annual percentiles are submitted with the final return (Quarter 4)
(c) Extend report to cover the required number of LCP on each site and repeat report for each separately regulated Operating Mode as required, e.g., Combined Cycle, Open Cycle, Supplementary firing, Auxiliary firing
(d) Averages determined at loads in the range 70% < Load ≤ 100% ISO base load and above
(e) Averages determined at loads in the range MSUL* < Load ≤ 100% ISO base load and above (* For a 3 parameter approach, from the point of Start-Up to the point of Shut-down)
(f) Leave the Daily ELV blank if this is applied as a 95th percentile ELV within the Permit
(g) For each pollutant, report the Annual 95th percentile ELV for hourly averages in the first column and, if applicable, the Annual 95th percentile ELV for daily means in the second column
(h For each pollutant, report the Annual 95th percentile of hourly averages in the first column and, if applicable, the Annual 95th percentile of daily means in the second column
Signed on behalf of the Operator by: |  |  | ……………..………………………………………………..
Date of return: |  |  | ……………..………………………………………………..

## LCP 98
RELEASES TO AIR
QUARTERLY RETURN
MONTHLY MEAN, MAXIMUM DAILY MEAN AND ANNUAL PERCENTILE CONCENTRATIONS (a),(b),(c)
OPERATING MODE: | NORMAL
Operator: | Uniper UK Ltd |  | Form: |  | ESI/03B (Gas Turbines)
Location: | Connah's Quay |  | Version/date: |  | V.10.6 Oct 2015
Permit/Variation Number: | NP3037AF | LCP98
Year: | LCP:
| NOx (mg/m3) |  |  | CO (mg/m3)
Month | Monthly Mean (d) | Max Daily Mean (d) | Part Load Max Daily Mean (e) | Monthly Mean (d) | Max Daily Mean (d) | Part Load Max Daily Mean (e)
January | 19.056 | 21.76 | 21.76 | 0.9 | 1.08 | 1.62
February | 18.728 | 20.616 | 20.808 | 0.9 | 1.08 | 54.09
March | 17.52 | 23.04 | 22.784 | 1.08 | 1.71 | 36.99
April
May
June
July
August
September
October
November
December
Monthly ELV/Daily ELV (f) | 75 | 75 | 75 | 30 | 30 | 200
Annual 95th Percentile (g) | - | - | - | - | - | -
Annual Percentile ELV (h) | 110 | - | - | 60 | - | -
NOTES:
(a) All data based on validated hourly average concentrations, excluding start-up and shut-down and periods of malfunction or breakdown of abatement equipment, at 15% O2, dry, 273.15K, 101.325 kPa
(b) Annual percentiles are submitted with the final return (Quarter 4)
(c) Extend report to cover the required number of LCP on each site and repeat report for each separately regulated Operating Mode as required, e.g., Combined Cycle, Open Cycle, Supplementary firing, Auxiliary firing
(d) Averages determined at loads in the range 70% < Load ≤ 100% ISO base load and above
(e) Averages determined at loads in the range MSUL* < Load ≤ 100% ISO base load and above (* For a 3 parameter approach, from the point of Start-Up to the point of Shut-down)
(f) Leave the Daily ELV blank if this is applied as a 95th percentile ELV within the Permit
(g) For each pollutant, report the Annual 95th percentile ELV for hourly averages in the first column and, if applicable, the Annual 95th percentile ELV for daily means in the second column
(h For each pollutant, report the Annual 95th percentile of hourly averages in the first column and, if applicable, the Annual 95th percentile of daily means in the second column
Signed on behalf of the Operator by: |  |  | ……………..………………………………………………..
Date of return: |  |  | ……………..………………………………………………..

## LCP 99
RELEASES TO AIR
QUARTERLY RETURN
MONTHLY MEAN, MAXIMUM DAILY MEAN AND ANNUAL PERCENTILE CONCENTRATIONS (a),(b),(c)
OPERATING MODE: | NORMAL
Operator: | Uniper UK Ltd |  | Form: |  | ESI/03B (Gas Turbines)
Location: | Connah's Quay |  | Version/date: |  | V.10.6 Oct 2015
Permit/Variation Number: | NP3037AF | LCP99
Year: | LCP:
| NOx (mg/m3) |  |  | CO (mg/m3)
Month | Monthly Mean (d) | Max Daily Mean (d) | Part Load Max Daily Mean (e) | Monthly Mean (d) | Max Daily Mean (d) | Part Load Max Daily Mean (e)
January | 25.728 | 28.048 | 28.048 | 1.62 | 3.24 | 25.56
February | 25.216 | 27.312 | 27.312 | 1.98 | 6.39 | 23.49
March | 24.552 | 25.552 | 25.552 | 1.35 | 6.12 | 16.92
April
May
June
July
August
September
October
November
December
Monthly ELV/Daily ELV (f) | 75 | 75 | 75 | 30 | 30 | 200
Annual 95th Percentile (g) | - | - | - | - | - | -
Annual Percentile ELV (h) | 110 | - | - | 60 | - | -
NOTES:
(a) All data based on validated hourly average concentrations, excluding start-up and shut-down and periods of malfunction or breakdown of abatement equipment, at 15% O2, dry, 273.15K, 101.325 kPa
(b) Annual percentiles are submitted with the final return (Quarter 4)
(c) Extend report to cover the required number of LCP on each site and repeat report for each separately regulated Operating Mode as required, e.g., Combined Cycle, Open Cycle, Supplementary firing, Auxiliary firing
(d) Averages determined at loads in the range 70% < Load ≤ 100% ISO base load and above
(e) Averages determined at loads in the range MSUL* < Load ≤ 100% ISO base load and above (* For a 3 parameter approach, from the point of Start-Up to the point of Shut-down)
(f) Leave the Daily ELV blank if this is applied as a 95th percentile ELV within the Permit
(g) For each pollutant, report the Annual 95th percentile ELV for hourly averages in the first column and, if applicable, the Annual 95th percentile ELV for daily means in the second column
(h For each pollutant, report the Annual 95th percentile of hourly averages in the first column and, if applicable, the Annual 95th percentile of daily means in the second column
Signed on behalf of the Operator by: |  |  | ……………..………………………………………………..
Date of return: |  |  | ……………..………………………………………………..

## Water 1
Permit Number : NP3037AF | [5 empty] | Operator
Installation : Connahs Quay Power Station | [5 empty] | Form Number : Water1 / ConnahsQuay PS (29/09/08)
Reporting of emissions to water (other than to sewer) for the period : | [5 empty] | 2016-01-01 | To | 2016-03-31
Emission Point | Substance / Parameter | Emission Limit Value | Reference Period | Result | Test Method | Sample Date and Times |  | Uncertainty
W1 | Flow | 2.5 m3/s | Instantaneous | 2.1028 | Analyser | 02/02/2016 : 17:57:20 - 19:59:14 |  | 2.47%
W1 | Temperature | 25 C |  | 20.7026 | Analyser | 18/03/2016 21:15:38 - 22:11:18 |  | 0.1c
W1 | Temperature Difference April - October | 13 C |  | N/A |  | N/A |  | 0.1c
W1 | Temperature Difference November - March 95 percentile Maximum | 13 C 20C |  | 13 | Analyser | 09/03/2016 22:40:58 - 00:51:52 |  | N/A
W1 | Salinity | 60 g/l |  | 48.5039 | Analyser | 24/03/2016 13:06:41 - 15:20:09 |  | N/A
W1 | pH Maximum | 9 |  | 8.2081 | Analyser | 02/03/2016 05:30:22 - 06:32:09 |  | 0.01pH
W1 | pH Minimum | 6 |  | 7.3342 | Analyser | 02/03/2016 21:31:39 - 23:14:21 |  | 0.01pH
W1 | Total Residual Oxidant (TRO) [5] | 0.2 mg/l |  | 0** | Analyser | 1st to 4th March 2016 |  | 5%
W1 | Residual Chlorine Dioxide [6] |  |  | 0.0026686 | Analyser | 01/01/2016 17:20:20 - 19:13:40 |  | 0.001 mg/m3
W1 | Residual Chlorite Ion [6] | 10 mg/l (absolute limit) |  | 0.061536 | Analyser | 02/01/2016 17:57:20 - 19:59:14 |  | 0.001 mg/m3
W1 | Residual Chlorite Ion [6] | 5 mg/l | Average | 0.061536 | Analyser | 02/01/2016 17:57:20 - 19:59:14 |  | 0.001 mg/m3
W1 | Oil and Grease | 20 mg/l | Instantaneous | 15.3757 | Analyser | 07/01/2016 10:38:26 - 11:54:04 |  | 0.01 mg/m3
** Sodium Hypochlorite added to Cooling System as Biocide on 1st March 2016 only
Signed | ………………………………………………………………. |  |  |  |  | Date | …………………….
(Authorised to sign as representative of Operator)
Installation : Connahs Quay Power Station | [5 empty] | Form Number : Water1 / ConnahsQuay PS (29/09/08)
Reporting of emissions to water (other than to sewer) for the period : | [5 empty] | 2016-01-01 | To | 2016-03-31
Emission Point | Substance / Parameter | Emission Limit Value | Reference Period | Result | Test Method | Sample Date and Times |  | Uncertainty
W2 | pH Maximum | 9 | Instantaneous | 7.52 | Analyser | 2016-02-12 |  | 0.01pH
W2 | pH Minimum | 6 | Instantaneous | 6.84 | Analyser | 2016-03-01 |  | 0.01pH
W2 | Oil and Grease | 20 mg/l | Instantaneous | None | Analyser | N/A |  | N/A
W2 | Residual Chlorine Dioxide [6] |  | Instantaneous | 0.017526 | Analyser | 2016-02-28 |  | 0.001 mg/m3
W3 | pH Maximum | 9 | Instantaneous | 8.67 | Analyser | 2016-02-02 |  | 0.01pH
W3 | pH Minimum | 6 | Instantaneous | 6.58 | Analyser | 2016-02-15 |  | 0.01pH
Signed | ………………………………………………………………. |  |  |  |  | Date | …………………….
(Authorised to sign as representative of Operator)

## GTP1
Reporting of emissions to air for the period from 01/01/2016 to 31/03/2016
Operator: Uniper UK |  |  | Site Location: Connahs Quay
Permit/Variation Number: NP3037AF |  |  | Release Points: A11, A12
Release Point | Substance / Parameter | ELV (mg/m3) | Reference Period | Result (mg/m3)
A11 | Oxides of Nitrogen (NO and NO2 expressed as NO2) | 95 | 10 min average | 87.16
A12 | Oxides of Nitrogen (NO and NO2 expressed as NO2) | 95 | 10 min average | 63.2*
A11 | Carbon Monoxide | 10 | 10 min average | 9.98
A12 | Carbon Monoxide | 100 | 10 min average | 74.8*
A11 | Sulphur dioxide | 9950 | 10 min average | 837
*External monitoring completed by E.On Technologies week commencing 24th April 2015
Signed on behalf of the Operator ……...……………………………………………..
Form Ref: Air - 1 / Connahs Quay PS (01/12/06)

## LCP 96 IED RTA 1
FORM NAME
V.10.6 Oct 2015
Releases of IED Pollutants to Air
| Operational Summary for the year |  | 2016
| Operator: | A
| Site Location: | Connah's Quay Power Station
| Original permit number: | NP3037AF | LCP: | 96
Note: beginning 1 January 2016, a return is required for each LCP within 28 days of the end of each quarter
| Emissions | SO2 | NOx | Dust
|  | (tonnes) | (tonnes) | (tonnes)
| January |  | 0
| February |  | 13.34
| March |  | 7.66
| Total for Quarter 1 | 0 | 21 | 0
April
May
June
| Total for Quarter 2 | 0 | 0 | 0
July
August
September
| Total for Quarter 3 | 0 | 0 | 0
October
November
December
| Total for Quarter 4 | 0 | 0 | 0
| Annual Total | 0 | 21 | 0
I confirm that this data is not knowingly reported with any omissions, errors or misrepresentation. All measurement equipment used to generate the data has been appropriately calibrated and maintained regularly; this includes calibration against traceable international measurement standards where available. The data is supported by appropriate record keeping. IT is designed, documented, tested, implemented, controlled and maintained to ensure reliable, accurate and timely processing of data; data handling and calculations have been appropriate; data has been checked for false and unusual measurements. The annual report of emissions for the above participating large combustion plant has been verified in accordance with the requirements of the Transitional National Plan Regulations.
| Name of the operator staff responsible for the quality of data supplied to the Register in accordance with the principles above. |  |  | Date
NOTES:
1. Data must be reported in tonnes to 2 decimal places.
2. All forms must be saved in the format IED RTA1—Quarter-Inventory Year-DEFRA IED LCP Number i.e. IED RTA1-Q1-2015-XXX for upload purposes
3. No PDF documents shall be accepted
4. Upload Forms held on GOV.UK will be accepted other variants of the forms will be automatically rejected which may impact their statutory obligations to report on time

## LCP 97 IED RTA 1
FORM NAME
V.10.6 Oct 2015
Releases of IED Pollutants to Air
| Operational Summary for the year |  | 2016
| Operator: | A
| Site Location: | Connah's Quay Power Station
| Original permit number: | NP3037AF | LCP: | 97
Note: beginning 1 January 2016, a return is required for each LCP within 28 days of the end of each quarter
| Emissions | SO2 | NOx | Dust
|  | (tonnes) | (tonnes) | (tonnes)
| January |  | 24.93
| February |  | 27.78
| March |  | 35.52
| Total for Quarter 1 | 0 | 88.23 | 0
April
May
June
| Total for Quarter 2 | 0 | 0 | 0
July
August
September
| Total for Quarter 3 | 0 | 0 | 0
October
November
December
| Total for Quarter 4 | 0 | 0 | 0
| Annual Total | 0 | 88.23 | 0
I confirm that this data is not knowingly reported with any omissions, errors or misrepresentation. All measurement equipment used to generate the data has been appropriately calibrated and maintained regularly; this includes calibration against traceable international measurement standards where available. The data is supported by appropriate record keeping. IT is designed, documented, tested, implemented, controlled and maintained to ensure reliable, accurate and timely processing of data; data handling and calculations have been appropriate; data has been checked for false and unusual measurements. The annual report of emissions for the above participating large combustion plant has been verified in accordance with the requirements of the Transitional National Plan Regulations.
| Name of the operator staff responsible for the quality of data supplied to the Register in accordance with the principles above. |  |  | Date
NOTES:
1. Data must be reported in tonnes to 2 decimal places.
2. All forms must be saved in the format IED RTA1—Quarter-Inventory Year-DEFRA IED LCP Number i.e. IED RTA1-Q1-2015-XXX for upload purposes
3. No PDF documents shall be accepted
4. Upload Forms held on GOV.UK will be accepted other variants of the forms will be automatically rejected which may impact their statutory obligations to report on time

## LCP 98 IED RTA 1
FORM NAME
V.10.6 Oct 2015
Releases of IED Pollutants to Air
| Operational Summary for the year |  | 2016
| Operator: | A
| Site Location: | Connah's Quay Power Station
| Original permit number: | NP3037AF | LCP: | 98
Note: beginning 1 January 2016, a return is required for each LCP within 28 days of the end of each quarter
| Emissions | SO2 | NOx | Dust
|  | (tonnes) | (tonnes) | (tonnes)
| January |  | 7.85
| February |  | 2.84
| March |  | 10.8
| Total for Quarter 1 | 0 | 21.49 | 0
April
May
June
| Total for Quarter 2 | 0 | 0 | 0
July
August
September
| Total for Quarter 3 | 0 | 0 | 0
October
November
December
| Total for Quarter 4 | 0 | 0 | 0
| Annual Total | 0 | 21.49 | 0
I confirm that this data is not knowingly reported with any omissions, errors or misrepresentation. All measurement equipment used to generate the data has been appropriately calibrated and maintained regularly; this includes calibration against traceable international measurement standards where available. The data is supported by appropriate record keeping. IT is designed, documented, tested, implemented, controlled and maintained to ensure reliable, accurate and timely processing of data; data handling and calculations have been appropriate; data has been checked for false and unusual measurements. The annual report of emissions for the above participating large combustion plant has been verified in accordance with the requirements of the Transitional National Plan Regulations.
| Name of the operator staff responsible for the quality of data supplied to the Register in accordance with the principles above. |  |  | Date
NOTES:
1. Data must be reported in tonnes to 2 decimal places.
2. All forms must be saved in the format IED RTA1—Quarter-Inventory Year-DEFRA IED LCP Number i.e. IED RTA1-Q1-2015-XXX for upload purposes
3. No PDF documents shall be accepted
4. Upload Forms held on GOV.UK will be accepted other variants of the forms will be automatically rejected which may impact their statutory obligations to report on time

## LCP 99 IED RTA 1
FORM NAME
V.10.6 Oct 2015
Releases of IED Pollutants to Air
| Operational Summary for the year |  | 2016
| Operator: | A
| Site Location: | Connah's Quay Power Station
| Original permit number: | NP3037AF | LCP: | 99
Note: beginning 1 January 2016, a return is required for each LCP within 28 days of the end of each quarter
| Emissions | SO2 | NOx | Dust
|  | (tonnes) | (tonnes) | (tonnes)
| January |  | 21.88
| February |  | 15.3
| March |  | 26.09
| Total for Quarter 1 | 0 | 63.27 | 0
April
May
June
| Total for Quarter 2 | 0 | 0 | 0
July
August
September
| Total for Quarter 3 | 0 | 0 | 0
October
November
December
| Total for Quarter 4 | 0 | 0 | 0
| Annual Total | 0 | 63.27 | 0
I confirm that this data is not knowingly reported with any omissions, errors or misrepresentation. All measurement equipment used to generate the data has been appropriately calibrated and maintained regularly; this includes calibration against traceable international measurement standards where available. The data is supported by appropriate record keeping. IT is designed, documented, tested, implemented, controlled and maintained to ensure reliable, accurate and timely processing of data; data handling and calculations have been appropriate; data has been checked for false and unusual measurements. The annual report of emissions for the above participating large combustion plant has been verified in accordance with the requirements of the Transitional National Plan Regulations.
| Name of the operator staff responsible for the quality of data supplied to the Register in accordance with the principles above. |  |  | Date
NOTES:
1. Data must be reported in tonnes to 2 decimal places.
2. All forms must be saved in the format IED RTA1—Quarter-Inventory Year-DEFRA IED LCP Number i.e. IED RTA1-Q1-2015-XXX for upload purposes
3. No PDF documents shall be accepted
4. Upload Forms held on GOV.UK will be accepted other variants of the forms will be automatically rejected which may impact their statutory obligations to report on time