Methane Emissions Survey Sheet – Hafod Landfill

| Site | Hafod Landfill: Permit No BS8621IW | Date | 19th February 2015 | Time | in: | 10:00 |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | out: | 15:00 |
| Instrument | Gazomat Inspectra TDL (Serial No.: 1470311) | Test gas reading | N/A | Time |  | N/A |
| Next Calibration due | 2015 | Background reading | 1.9 | Time |  | 10:45 |
| Weather conditions: | Wet, cold, cloud, light breeze. |  |  | Atm. Press. |  | Not recorded |
| Survey Undertaken by: | T Roberts, I Oakes NRW |  |  |  |  |  |

General comments / observations

This Technical Review follow up is being carried out as a key part of Natural Resources Wales’ strategy to reduce methane emissions from landfill sites in Wales. The objectives of the site review include ensuring that the site is being operated and maintained so as to maximise gas collection efficiency and minimise fugitive landfill gas emissions. Treating the gas in a manner that minimises point source emissions. An ATEX certified, Gazomat Inspectra Laser Methane Analyser was used to perform emissions testing at the site. The site surface, surface capping, seams and structures as well as ambient air samples on the site were randomly tested in order to establish potential sources of methane egress. Officers were accompanied by Graham Ball and (in part) Ian Craven, both of Cory Environmental. Note on scope of this work: The surface emission checks undertaken by NRW during this visit should only be considered a snapshot of the site. This exercise should not be considered a comprehensive survey of the entire site.

| Survey Results (only readings >10 ppm recorded) |  |  |  |  |
| --- | --- | --- | --- | --- |
| Point ref. | Time | Methane Reading | Feature and / or Grid Reference | Description / Comment |
| 1 | 13:10 | 56ppm | NE Corner of Cell 3 | Emission from site surface. Consider improved extraction |
| 2 | 13:15 | 34.5% | NE Corner of Cell 3 | Gas bubbling up through the ground. Urgent improvement in extraction required in this area of the site to reduce emissions |
| 3 | 13:17 | 10.3% | NE Corner of Cell 3 | Gas bubbling up through the ground. Urgent improvement in extraction required in this area of the site to reduce emissions |
| 4 | 13:18 | 730ppm | NE Cell 3 Northerly slope | Gas emission through small outbreaks of leachate on slope and site surface. Comments as previous. |
| 5 | 13:20 | 738ppm | NE Cell 3 Northerly slope | Gas emission through small outbreaks of leachate on slope and site surface. Comments as previous. |
| 6 | 13:22-13:30 | 40-60ppm | Transect of cell 3 from East to West | Gas in air approximately half a meter above the ground. |
| 7 | Not recorded | >25ppm | Transect between well 41 and well 32 | Values greater than 25ppm in the air between these two points were recorded in one continuous transect. |
| 8 | Not recorded | 50-80ppm around the well and 100ppm at the base | Well 32 | A range of concentrations was recorded in the air around this well between these values |
| 9 | Not recorded | 100ppm | Base of well 32 | Well requires re-sealing and unblocking so that de-watering can take place. This should increase extraction efficiency in this area and reduce emissions. |
| 10 | Not recorded | 1200ppm | Emission at base of well 35 | De-water well and re-seal if required. |
| 11 | Gas Well 39 | 2.4% | Emission at the base of the well. | Dip, de-water and re-seal then re balance the well to ensure improved function. |
| 12 | New manifold at the base of the Western slope. | 354ppm | Emission detected in the air 1m above the surface of the site | This is a high emission in the air and steps must be taken to improve gas extraction efficiency in this area to reduce emissions. |

Findings/Recommendations

The table above demonstrates that there are emissions from some parts of the site:- From the North East corner of cell 3, there was gas in the air emanating from this part of the cell through numerous leachate weeps. This cell is therefore deemed to be under extracted and requires an urgent improvement in extraction in this area. Gas concentrations of over 34% were being emitted from the surface in this area. In a transect across the site from NE part of cell three to well 32 on the Western side of the site emissions were detected in the air approximately ½ to 1m above ground level. The gas system should therefore be reviewed with these findings in context and improved in these areas to reduce emissions and increase extraction efficiency. The site management is now aware of these issues and has instigated improvement works which include the installation of new pin wells in cell three. The newly drilled and existing wells should be pumped clear of perched leachate and cleared of blockages to ensure extraction efficiency improves and concomitantly emissions should reduce.

Hafod Landfill Site

Surface Emissions Survey

19 February 2015