
Schedule 6 - Notification 

Part A 
	Permit Number
	BR7321 (Site)  

	Name of Operator
	Tata Steel UK

	Location of Installation
	Shotton Works 

	
	

	Time and date of the detection 
	14/05/17 11:30 (confirmed)


	(a) Notification requirements for any malfunction, breakdown or failure of equipment or techniques, accident, or fugitive emission which has caused, is causing or may cause significant pollution

	To be notified within 24 hours of detection

	Date and Time of the event
	14/05/17 08:30 / 11:30

	Reference or description of the location of the event 
	Middle Outfall, Tern Lagoon, Tata Steel Shotton

	Description of where any release into the environment took place
	Middle Outfall, Tern Lagoon, Tata Steel Shotton

	Substances(s) potentially released
	Chrome (Cr)

	Best estimate of the quantity or rate of  release of substances
	Exact quantity not known at this time; detected value of 0.9ppm at 08:30 sample (14/05) and confirmed at 11:30 sample (14/05)
Level at 08:00 on 13/05 below detectable limit (<0.1ppm)

	Measures taken, or intended to be taken, to stop any emission
	Emergency slam shuts activated at ~11:30 once levels confirmed (i.e. not an error in sampling) and process started to reduce water levels and attempt to identify and eliminate source. 

	Description of the failure or accident.
	No failure or accident currently suspected or identified, based on initial investigation Sunday 14th. Investigation continuing.


	(b) Notification requirements for the breach of a limit

	To be notified within 24 hours of detection unless otherwise specified below

	Emission point reference/ source
	

	Parameter(s)
	

	Limit
	

	Measured value and uncertainty
	

	Date and time of monitoring
	


	(c) Notification requirements for the detection of any significant adverse environmental effect

	To be notified within 24 hours of detection

	Description of where the effect on the environment was detected
	N/A

	Substances(s) detected
	N/A

	Concentrations of substances detected
	N/A

	Date of monitoring/sampling
	N/A


Part B to be supplied as soon as practicable
	Any more accurate information on the matters for notification under Part A.
	Samples taken by Exova on the day (Sunday 14th) showed an elevated  level of Chrome (0.9ppm). Consequently, emergency slam shuts were activated, and production was stopped for over eight hours during the investigation, until levels behind the slam shut were below detectable levels, following removal of ~7 tonnes of contaminated water. Removed water was processed through the Effluent Treatment Plant.

Further samples collected on Sunday, and analysed on Monday 15th, identified a potential source from inside 23 Bay (main drain for 5 Galv / 6 Galv and associated predominantly with storm water drains). However, further sampling on Monday, including upstream and at all local feeds to the main drain did not detect any elevation. Sample taken of limited sediment in the 23 Bay drain showed only 0.2 Cr, suggesting the sediment was not the source of the release. 
Repeated sampling (daily) at the outfalls to the Tern Lagoons have not shown any elevated Chrome levels. Samples taken within the Tern Lagoons showed that Chrome levels were below detectable levels.

	Measures taken, or intended to be taken, to prevent a recurrence of the incident
	Investigative sampling of likely sources of contamination (including emergency, unplanned, maintenance, and cleaning tasks) have not revealed any recognised, potential sources for contamination/unplanned release. 
Daily sampling of the outfalls will continue; training and awareness of the processes to reduce impact (including slam shuts, emergency response and call out procedures) have been reviewed. If initial sample is found to be elevated, this will result in an initial call to the relevant management, rather than following confirmation of elevation (i.e. 2nd test).
Operational use of Chrome will be phased out as per the REACH requirements.

	Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment which has been or may be caused by the emission
	Impact of the release into the SSSI is negligible. Tests of the Lagoon waters does not show Cr as being at a detectable level.

	The dates of any unauthorised emissions from the installation in the preceding 24 months.
	None.


	Name*
	Peter Shephard

	Post
	Senior Energy and Environment Officer

	Signature
	Electronic

	Date
	15/06/17



