Culvery Power Limited Decision Document

Rev No1

# Bespoke permit

The application number is:		PAN-003961

The Applicant / Operator is:		Culvery Power Limited

The Facility is located at:		4 Chemistry Lane, Pentre, Deeside, CH5 2DA

We have decided to grant the permit for Culvery Power Limited.

We consider in reaching that decision we have taken into account all relevant considerations and legal requirements and that the permit will ensure that the appropriate level of environmental protection is provided.

## Purpose of this document

This decision document:

explains how the application has been determined

provides a record of the decision-making process

shows how all relevant factors have been taken into account

justifies the specific conditions in the permit other than those in our generic permit template.

Unless the decision document specifies otherwise we have accepted the applicant’s proposals.

## Structure of this document

- Table of contents

- Key issues

## Table of Contents

## Contents

Bespoke permit	2

Purpose of this document	3

Structure of this document	4

Table of Contents	5

Contents	5

Key issues of the decision	6

1	Our decision	6

2	How we reached our decision	7

2.1 Receipt of Application	7

2.2	 Consultation on the Application	7

2.3	 Requests for Further Information	7

3	The Legal Framework	7

4	The Facility	8

4.1 Description of the Facility and related issues	8

4.2 Operation of the Facility – general issues	12

5	Minimising the Facility’s environmental impact	16

5.1	Assessment of Impact on Air Quality	16

5.2	Impact on Habitats sites, SSSIs, non-statutory conservation sites etc	18

5.3 European Sites	19

Assessment of Likely Significant Effect:	22

Appropriate assessment:	22

HRA Overall conclusion:	22

6  Setting ELVs and other Permit conditions	23

6.1	Monitoring	23

6.2	Other Permit Conditions	24

6.3	Reporting	25

7 Specified Generator Charges and Subsistence Fees	25

# Key issues of the decision

## Our decision

We have decided to grant a permit for Culvery Power Limited.

We consider that, in reaching that decision, we have taken into account all relevant considerations and legal requirements and that the permit will ensure that a high level of protection is provided for the environment and human health.

This Application is to operate a regulated facility which is subject principally to the Specified Generator (SG) regulations.

The permit contains many conditions taken from our standard Environmental Permit template including the relevant Annexes. We developed these conditions in consultation with industry, having regard to the legal requirements of the Environmental Permitting Regulations (EPR) and other relevant legislation. This document does not therefore include an explanation for these standard conditions. Where they are included in the permit, we have considered the Application and accepted the details are sufficient and satisfactory to make the standard conditions appropriate.

## How we reached our decision

### 2.1 Receipt of Application

The Application was accepted as duly made on 03/12/2019. This means we considered it was in the correct form and contained sufficient information for us to begin our determination, but not that it necessarily contained all the information we would need to complete that determination.

The Applicant made no claim for commercial confidentiality. We have not received information in relation to the Application that appears to be confidential in relation to any party.

### 2.2	 Consultation on the Application

There was no requirement to carry out a consultation on the Application.

### 2.3	 Requests for Further Information

No further information was requested or required.

## The Legal Framework

The Permit will be granted, under Regulation 13 of the EPR.  The Environmental Permitting regime is a legal vehicle which delivers most of the relevant legal requirements for activities falling within its scope.  In particular, the regulated facility is:

plant as described by Schedule 25A and Schedule 25B covering the Medium Combustion Plant Directive (MCPD) and Specified Generator (SG) regulations respectively;

subject to aspects of the Well-Being of Future Generations (Wales) Act 2015 and the Environment (Wales) Act 2016 which also have to be addressed.

We address the legal requirements directly where relevant in the body of this document.  NRW is satisfied that this decision is consistent with its general purpose of pursuing the sustainable management of natural resources (SMNR) in relation to Wales, and applying the principles of SMNR. In particular, NRW acknowledges that it is a principle of sustainable management to take action to prevent significant damage to ecosystems. We consider that, in granting the Permit a high level of protection will be delivered for the environment and human health through the operation of the Facility in accordance with the permit conditions. NRW is satisfied that this decision is compatible with its general purpose of pursuing the sustainable management of natural resources in relation to Wales and applying the principles of sustainable management of natural resources.

## 4	The Facility

### 4.1 Description of the Facility and related issues

#### 4.1.1	The permitted activities

The Facility is subject to the EPR because it carries out an activity as described in Schedule 25B of the EPR:

One Tranche B Specified Generator aggregated to <50MWth at a specified location

A Generator means any combustion plant generating electricity. The regulations use the term ‘specified generator’ to encompass both individual  generators and multiple generators at the same location or site, operated by the same Operator and for  the same purpose. The “same purpose” means that having a different function does not stop individual  generators being treated as part of a specified generator, e.g. generators with a capacity market agreement  or providing a balancing service whether they are under the same contract or not would be classed as  operating for the “same purpose” as they generate electricity. Similarly generators with different fuels or  technologies are also classed as operating for the “same purpose”.

The specified generator permit will apply to the site, rather than its constituent individual generators. All specified generators equal to or more than 1 MWth will also be Medium Combustion Plant (MCP) and must also meet the requirements of the MCP Directive, although these requirements do not begin to take effect until 2024 or 2025, depending on the size of the MCP.

Specified Generators are also divided into Tranche A and Tranche B sites, which will determine the relevant permitting date.  A site is a Tranche A site if it meets the following criteria:

• It came into operation before 1 December 2016, or

• It is the subject of a capacity agreement arising from the 2014 or 2015 capacity auctions

A generator with a rated thermal input of less than 1MWth will be classed as Tranche A if:

• It is the subject of a capacity agreement arising from the 2014, 2015 or 2016 capacity auctions, or

• A FiT preliminary accreditation application was received by OfGEM before 1 December 2017, or

• Is the subject of an agreement to provide balancing services entered into before 31 October 2017.

Tranche B generators are all those that are not Tranche A.

Culvery Power Limited operates seven 4.65 MWth spark ignition reciprocating engines (one 32.6 MWth Specified Generator) which are used for the purposes of electricity generation The facility at Culvery Power Ltd can be classified as a Tranche B Specified Generator, by virtue of a Short Term Operating Reserve contract with National Grid entered into in August 2018.

#### 4.1.2	The Site

Culvery Power Limited is a small 14MWe natural gas fired power station located at, 4 Chemistry Ln, Pentre, Deeside CH5 2DA. The power plant was constructed on an area of brown field land. The land is the subject of a 20 year lease and is self-contained and fully enclosed by a perimeter fence. No activities other than the generation of electricity from natural gas will take place on site.

#### 4.1.3	What the Facility does

The power plant itself is made up of 7 gas fuelled spark ignition reciprocating engines manufactured by MWM, Germany. Each engine, model TCG 2020V20, has a maximum output of 2MWe. They are best available technology operating with an electrical efficiency of approximately 43%. The electricity is generated by burning the gas within the spark ignition engines exporting the electricity produced at 33,000 volts to the SP Energy Network substation.

Gas is supplied to the power plant via a dedicated gas pipeline connected to the medium pressure gas network owned by Wales and West Utilities running along Chemistry lane The gas engines and all associated equipment are contained within a portal steel framed building on the centre of the site.

The plant is designed to operate intermittently at short notice on short duration runs. The plant has been designed as a flexible power generation facility providing electricity to the grid during times of low renewable energy output, high winter demand, market scarcity, system constraints and system instability.

#### 4.1.4	Key Issues in the Determination

The key environmental and human health issues considered during the determination of this variation were:

Air quality – Oxides of Nitrogen

This will be discussed separately in this decision document.

### 4.2 Operation of the Facility – general issues

#### 4.2.1	Administrative issues

The Applicant is the sole Operator of the Facility. We are satisfied that the Applicant is the person who will have control over the operation of the Facility if the Permit were to be granted; and that the Applicant will be able to operate the Facility so as to comply with the conditions included in the Permit, if issued.

#### Relevant Convictions

NRW’s COLINS Database has been checked to ensure that all relevant convictions have been declared.  No relevant convictions were found. The operator satisfies the criteria in RGN 5 on Operator Competence.

#### Financial Provision

There is no known reason to consider that the operator will not be financially able to comply with the permit.  The decision was taken in accordance with RGN 5 on Operator Competence.

#### 4.2.2	Management

We are satisfied that appropriate management systems and management structures will be in place for this Facility, and that sufficient resources are available to the Operator to ensure compliance with all the Permit conditions.

#### 4.2.3	Operating techniques

The operator has stated that they will implement the following quality assurance techniques and maintenance schedule, in order to for the generators to achieve and retain optimal performance. In order to enable each generator and the power plant in general to achieve and retain optimal performance in both efficiency and emissions, the plant will engage in the following best available operational management techniques:-

(a) Benchmark Performance Testing and Acceptance – On completion of the construction phase of the power plant, tests demonstrating fitness for purpose, reliability, efficiency, emissions and noise ensure the facility complies with all applicable design standards, procurement guarantees, and generally good engineering practice. Such ‘performance acceptance testing’ is carried out in accordance with ISO 3046-4:2009 (Reciprocating internal combustion engines. Performance. Speed governing). This is the main standard of performance tests for reciprocating internal combustion engines and ensures the provision of data for acceptance of the plant based on tests of appropriate scientific quality.

(b) Scheduled Maintenance – The routine operation and maintenance of the plant is contracted to the Original Equipment Manufacturer’s (OEM) UK Agent; typically also the original EPC construction contractor. Maintenance of the plant is therefore undertaken based on strict OEM schedules retaining optimised performance of the assets through-out their life-cycle (>20 years).

(c) Plant remote monitoring and operational control – The performance of each engine and the power plant is monitored continuously. During periods of generation, each generator has sophisticated control systems which monitors operational parameters within strict operating conditions. These control systems detect operation at Other than Normal Operating Conditions (OTNOC) and make adjustments to air/fuel mixture, ignition and valve timing to ensure both efficiency and ELVs are maintained. The performance of the plant is analysed and trended over time to ensure its operating efficiency and energy consumption remain optimal.

(d) Emission monitoring and engine mapping – Emissions monitoring and engine mapping is undertaken as part of scheduled annual maintenance. Measurements are taken generally in accordance with Environment Agency Technical Guidance Note M5 (Medium Combustion Plant Directive and Generator Controls: monitoring point source emissions) using equipment assessed against EN 50379-2. Measurements are made by the organisations that service and maintain the MCP as part of their maintenance regime. Sample points have been provided in readily accessible locations of the exhaust system where the exhaust gasses remain hot (>300C) and are well mixed – typically the location is within the generator housing down-stream of the engine turbochargers but before the exhaust silencing system.

(e) Analysing Plant failures and implementing improvements/remedies – Plant failures are analysed by the operations and maintenance providers for root causes. Cause is identified against maintenance procedures, design requirements and life expectancy invoking a culture of continuous improvement in all aspects of plant reliability and performance.

(f) Recording, analysis and management systems - Through continuous monitoring and remote telemetry, records of performance, maintenance and testing are retained and reviewed regularly as part of performance and commercial plant management. In performing their duties, the plants Operations and Maintenance providers adhere to a fully ISO accredited Health Safety and Environmental and Quality Management System (SHEQ);ISO 9001, 140001 & 180001.

We have reviewed the techniques used by the operator and compared these with the relevant guidance notes. The proposed techniques/ emission levels for priorities for control are in line with the benchmark levels contained in TGN M5 and we consider them to represent appropriate techniques for the facility. These are specified in the Operating Techniques table in the permit.

We have specified that the applicant must operate the permit in accordance with descriptions in the application, including all additional information received as part of the determination process.

## 5	Minimising the Facility’s environmental impact

For this kind of regulated activity, the principal emissions are emissions to air. There are no permit conditions for water, land, energy efficiency, odour or noise and BAT does not apply.

The next sections of this document explain how we have approached the critical issue of assessing the likely impact of air emissions from the MCP/SG on human health and the environment and what measures we are requiring to ensure a high level of protection.

We have reviewed the operator's assessment of the environmental risk from the facility. The operator’s risk assessment is satisfactory. The assessment shows that, applying the conservative criteria in our guidance on Environmental Risk Assessment, all emissions may be categorised as environmentally insignificant.

We will discuss the operators risk assessment in more detail as follows:

### 5.1	Assessment of Impact on Air Quality

This section of the decision document deals primarily with the dispersion modelling of emissions to air from the stack and its impact on local air quality.

The Applicant has assessed the Facility’s potential emissions to air against the relevant air quality standards, and the potential impact upon human health.  These assessments predict the potential effects on local air quality from the Facility’s stack emission.

The air impact assessments and the dispersion modelling has been based on the Facility (peaking plant) operating up to a maximum of 2500 hours per year (this being the maximum number of hours of allowable operation per annum). The assumptions underpinning the model have been checked and are reasonably precautionary. The way in which the Applicant used dispersion models, its selection of input data, use of background data and the assumptions it made have been reviewed by Natural Resources Wales modelling specialists to establish the robustness of the Applicant’s air impact assessment. The output from the model has then been used to inform further assessment of health impacts.

There are several residences within the vicinity of the site. Air quality impacts have been modelled on a receptor grid of 25m spacing and contour plots. These predicted ground level concentrations have been compared with relevant air quality standards and guidelines for the protection of human health.

The results indicate that at all locations within the study area the relevant air quality standard, which is the Air Quality Strategy (AQS) objective level for annual mean NO2 concentrations of 40μg/m3 will be met. At the nearest sensitive locations, which were included as specific receptors within the model, the PC arising from the plant is a maximum of 0.4% of the objective level. In accordance with NRW/EA significance criteria, the impact of the FPP on annual mean NO2 concentrations is therefore considered to be insignificant.

The AQS objective level for hourly mean NO2 concentrations is a concentration of 200μg/m3. This objective level includes 18 allowable exceedances of this level within a year. As part of this applications air quality modelling assessment, concentrations have been predicted as both the 99.8th percentile to allow direct comparison with this objective level and also as a sensitivity test for the 100th percentile (which should not be compared with the limit of 200μg/m3).

The results of the modelling indicate that at all of the selected residential receptors concentrations are predicted to meet the AQS objective level for hourly mean NO2 concentrations. At four locations the level of 200μg/m3 was exceeded but the number of exceedences was below the allowable level, therefore the objective level will be met.

At all but one of the sensitive receptors the predicted process contribution is greater than 10% of the relevant standard, therefore in accordance with the criteria provided by the EA, the impact is considered to be significant. However, it should be noted that worst case assumptions regarding the emissions have been incorporated into the model. The FPP will only operate for up to 2500 hours per year, consideration should therefore also be given to the likelihood of the operation of the FPP during the worst-case meteorological conditions such as would be required to produce the above results. On this basis and as no exceedances of the relevant standard are predicted, it is considered that the impact on hourly mean NO2 concentrations is also insignificant.

### 5.2	Impact on Habitats sites, SSSIs, non-statutory conservation sites etc

There are two SSSIs within 2km of the site:

•	River Dee SSSI

•	Connahs Quay Ponds & Woodlands SSSI

As a result, an Appendix 4 form - CRoW Act 2000: Natural Resources Wales application for permission - Formal Notice, has been completed in conjunction with this application.

Detailed air quality modelling impact assessment has been carried out with regards to any potential impact from the Peaking Plant facility on the designated SSSI sites within 2km of the facility. The significance criteria provided by NRW/EA states that for SSSI’s the air quality impact can be considered to be insignificant if the long-term PC is less than 1% of the Critical Level. Detailed air quality impact assessment modelling shows that the impact of the operation of the Peaking Plant on Connah’s Quay Ponds and Woodland SSSI is therefore considered to be insignificant.

At the River Dee and Bala Lake SAC / SSSI, the predicted long-term PC is greater than 1% of the Critical Level. For sites with a PC of greater than 1% of the Critical Load the relevant guidance recommends that the impact be considered in terms of the total predicted concentration. The maximum PEC at the River Dee and Bala Lake SAC / SSSI is predicted to be 19.14 μg/m3 which is 63.8% of the Critical Level. As the PEC is below 70% of the AQO, the impact of the operation of the Peaking Plant at the River Dee and Bala Lake SAC / SSSI is therefore also considered to be insignificant.

The maximum PC nutrient nitrogen deposition rates at the River Dee and Bala Lake SSSI and Connah’s Quay Ponds and Woodland SSSI arising from the Peaking Plant are low in comparison to the critical loads (less than 1%). Therefore, it is considered that the impact is insignificant. At all of the sensitive habitat sites, the PC is also low in comparison to the existing acid deposition rates and critical loads. Therefore, it is considered that the impact of the operation of FPP on acid deposition is insignificant.

In conclusion, the impact on airborne NOx concentrations, and acid and nitrogen deposition at the designated SSSI’s was determined to be insignificant.

### 5.3 European Sites

The following Natura 2000 sites are located within the relevant screening distance (3.5km) of the main site emission point to air:

- The Dee Estuary (SAC/SPA/Ramsar Site – SAC EU Code

UK0030131) – approximately 2.2 km to the north east of the facility.

- River Dee and Bala Lake/ Afon Dyfrdwy a Llyn Tegid (SAC: EU code

UK0030252) – approximately 0.5km to the north of the facility.

- Deeside and Buckley Newts sites (SAC: EU Code UK0030132), approximately 2.4km to the west of the facility.

A FORM 1 has been completed with regards to a Habitats Regulations Assessment (HRA). This is required because there is a conceivable impact pathway to the Natura 2000 sites listed above.

Detailed air quality modelling has been carried out with regards to the potential impact from the Peaking Plant facility.

The significance criteria provided by NRW/EA states that for SACs and SSSIs, the

impact can be considered to be insignificant if the long-term PC is less than 1% of

the Critical Level. The impact of the operation of the FPP on the Dee Estuary SAC,

the Deeside and Buckley Newt Sites SAC, the Connah’s Quay Ponds and Woodland SSSI is therefore considered to be insignificant.

At the River Dee and Bala Lake SAC / SSSI, the predicted long-term PC is greater

than 1% of the Critical Level. For sites with a PC of greater than 1% of the Critical

Load the EA guidance recommends that the impact can be considered in terms of the

total predicted environmental concentration (PEC). The maximum PEC at the River

Dee and Bala Lake SAC / SSSI is predicted to be 19.14 μg/m3 which is 63.8% of the

Critical Level. As the PEC is below 70% of the AQO, the impact of the operation of

the STOR plant at the River Dee and Bala Lake SAC / SSSI is therefore also

considered to be insignificant.

For short-term (24-hour) concentrations the EA significance criteria states that for

SACs and SSSIs the impact can be considered to be insignificant if the PC is less

than 10% of the Critical Level. Therefore, in accordance with the EA criteria, the impact is considered to be significant.

It should be noted, however that worst case assumptions have been included in the

modelling, the FPP would need to be operating continuously for a 24-hour period in

worst case meteorological conditions to result in the above predicted impact.

Considering the FPP will only operate for approximately 2500 hours per year, this is

considered unlikely to occur. It should further be noted that at the Dee Estuary SAC

and the Deeside and Buckley Newt Sites SAC, the Connah’s Quay Ponds and

Woodland SSSI, the maximum predicted total environmental concentrations (PECs) are well below (less than 75% of) the relevant critical level. As such, the impact of the operation of the FPP on 24- hour NOx concentrations at these locations is also considered to be insignificant.

At the River Dee and Bala Lake SAC and SSSI, the PEC is above the standard within

a small area close to the Site, however as previously discussed as this habitat is a

waterbody the critical level does not apply at this location.

The maximum PC nutrient nitrogen deposition rates arising from the FPP are low in

comparison to the critical loads. Therefore, it is considered that the impact from the FPP is insignificant.

This project complies with NRW agreed criteria for ruling out significant effects without conducting a project-specific LSE test. Therefore this project is considered not likely to have a significant effect on any Natura 2000 sites, either alone or in-combination with other plans and projects.

## Assessment of Likely Significant Effect:

The project has been screened for likelihood of significant effects and, taking account of the advice received from protected sites advisors, is considered not likely to have a significant effect on any Natura 2000/site (As documented in section 3.2 of OGN 200 form 1, or section 5 if applicable).

## Appropriate assessment:

In light of the conclusions of an appropriate assessment, and taking account of the advice received from protected sites advisors, it has been established that the project will not adversely affect the integrity of any Natura 2000 site, taking into account any conditions or restrictions as applicable, either alone or in-combination with other plans and projects. (As documented in section 4 of OGN 200 form 1, and section 5 if applicable).

## HRA Overall conclusion:

All long-term impacts on human receptors are predicted to be below the relevant air quality objective levels at locations where the Air Quality Directive states they must be applied. The short-term impacts at the receptors are also below the relevant air quality objective levels. The short-term impact at the point of maximum impact is above the relevant limit, however taking into account the operating hours, it is considered unlikely that the operation of the Facility will coincide with the worst-case meteorological conditions such that the impact can be considered to be lower than the modelling results indicate.

An assessment of the impact on nearby sensitive ecological sites has also been completed. The impact on airborne NOx concentrations and nitrogen deposition at the sensitive habitats was determined to be insignificant.

In light of the above conclusions of the appropriate assessment, it has not been ascertained that the project will not adversely affect the integrity of any Natura 2000 site, as documented in section 4 of OGN 200 form 1, and section 5 is applicable.

## 6  Setting ELVs and other Permit conditions

We have decided that emission limits should be set for the parameters listed in the permit.  Emissions Limit Values (ELVs) are in line with those set out in the MCP Directive and Specified Generator regulations (Schedule 25B).

### 6.1	Monitoring

We have decided that monitoring should be carried out for the parameters listed in Schedule 3 of the permit using the methods and to the frequencies specified in those tables.  These monitoring requirements have been imposed in order to demonstrate compliance with the emissions limits in the permit, as per the ELV and monitoring frequency requirements specified within the EPR Schedule 25B Regulations.

For a Tranche B Specified Generator, that is an engine fuelled on natural gas, the monitoring requirements are as follows:

| Pollutant | Type of Specified Generator | Fuel Type | Emission Limit Value (mg/Nm3) | Monitoring Required |
| --- | --- | --- | --- | --- |
| NOx | Spark Ignition Engine | Natural Gas | 190* | Periodic – every 3 years |

*380 mg/Nm3 for dual fuel engines in gas mode.

Emission limit values are defined at a temperature of 273,15 K, a pressure of 101,3 kPa and after correction for the water vapour content of the waste gases and at a standardised O2 content of 15% for engines (and gas turbines).

For emissions to air, the methods for continuous and periodic monitoring are in accordance with the Environment Agency’s Technical Guidance Note M5 for monitoring of stack gas emissions from medium combustion plants and specified generators.

Based on the information in the Application and the requirements set in the conditions of the permit we are satisfied that the monitoring techniques, personnel and equipment employed by the Operator will have either MCERTS certification or MCERTS accreditation as appropriate.

### 6.2	Other Permit Conditions

As a Specified Generator, the facility must adhere to the following operating techniques for SG.

As a Specified Generator (SG), these are:

  - Each generator must be operated in accordance with the manufacturer’s instructions and records must be made and retained to demonstrate this.

  - The operator must keep periods of start-up and shut down of the generators as short as possible

  - There must be no persistent emission of ‘dark smoke’ as defined in section 3(1) of the Clean Air Act 1993.

  - Where secondary abatement is required to ensure compliance with the NOx ELV it must be met within 10 minutes from when the generator commences operation or within 20 minutes when the generator was a Tranche A and is now a Tranche B generator.

  - The stack must be vertical and unimpeded by cowls or caps.

### 6.3	Reporting

We have specified the reporting requirements in Schedule 4 of the Permit to ensure data is reported to enable timely review by Natural Resources Wales to ensure compliance with permit conditions.

### 7 Specified Generator Charges and Subsistence Fees

The type of application regarding Specified Generators will have an associated charge. The Specified Generator application type will also form the basis for ongoing subsistence fee’s.  More information on this can be found in our charging scheme on our website.