Cynon Power Limited

Decision Document

Rev No1

# Bespoke permit

The application number is:		PAN-004125

The Applicant / Operator is:		Cynon Power Limited

The Facility is located at:		Aberaman Industrial Estate, Aberdare, Rhondda Cynon Taf, Wales, CF44 6AG

We have decided to grant the permit for Cynon Power Limited.

We consider in reaching that decision we have taken into account all relevant considerations and legal requirements and that the permit will ensure that the appropriate level of environmental protection is provided.

## Purpose of this document

This decision document:

explains how the application has been determined

provides a record of the decision-making process

shows how all relevant factors have been taken into account

justifies the specific conditions in the permit other than those in our generic permit template.

Unless the decision document specifies otherwise we have accepted the applicant’s proposals.

## Structure of this document

- Table of contents

- Key issues

## Table of Contents

## Contents

Bespoke permit	2

Purpose of this document	3

Structure of this document	4

Table of Contents	5

Contents	5

Key issues of the decision	6

1	Our decision	6

2	How we reached our decision	7

2.1 Receipt of Application	7

2.2	 Consultation on the Application	7

2.3	 Requests for Further Information	7

3	The Legal Framework	7

4	The Facility	8

4.1 Description of the Facility and related issues	8

4.2 Operation of the Facility – general issues	13

5	Minimising the Facility’s environmental impact	16

5.1	Assessment of Impact on Air Quality	17

5.2	Impact on Habitats sites, SSSIs, non-statutory conservation sites etc	18

5.3 European Sites	19

Assessment of Likely Significant Effect:	20

Appropriate assessment:	20

HRA Overall conclusion:	20

6  Setting ELVs and other Permit conditions	20

6.1	Monitoring	20

6.2	Other Permit Conditions	21

6.3	Reporting	22

7 Specified Generator Charges and Subsistence Fees	22

# Key issues of the decision

## Our decision

We have decided to grant a permit for Cynon Power Limited.

We consider that, in reaching that decision, we have taken into account all relevant considerations and legal requirements and that the permit will ensure that a high level of protection is provided for the environment and human health.

This Application is to operate a regulated facility which is subject principally to the Specified Generator (SG) regulations.

The permit contains many conditions taken from our standard Environmental Permit template including the relevant Annexes. We developed these conditions in consultation with industry, having regard to the legal requirements of the Environmental Permitting Regulations (EPR) and other relevant legislation. This document does not therefore include an explanation for these standard conditions. Where they are included in the permit, we have considered the Application and accepted the details are sufficient and satisfactory to make the standard conditions appropriate.

## How we reached our decision

### 2.1 Receipt of Application

The Application was accepted as duly made on 06/12/2018. This means we considered it was in the correct form and contained sufficient information for us to begin our determination, but not that it necessarily contained all the information we would need to complete that determination.

The Applicant made no claim for commercial confidentiality. We have not received information in relation to the Application that appears to be confidential in relation to any party.

### 2.2	 Consultation on the Application

There was no requirement to carry out a consultation on the Application.

### 2.3	 Requests for Further Information

In order for us to be able to consider the Application duly made, we needed more information. We requested further information relating to the site plan. Upon receipt of this information we were able to consider the application Duly Made.

A copy of the e-mail requesting further information was placed on our public register as were the responses when received.

## The Legal Framework

The Permit will be granted, under Regulation 13 of the EPR.  The Environmental Permitting regime is a legal vehicle which delivers most of the relevant legal requirements for activities falling within its scope.  In particular, the regulated facility is:

plant as described in Schedule 25A and Schedule 25B covering the Medium Combustion Plant Directive (MCPD) and Specified Generator (SG) regulations respectively;

subject to aspects of the Well-Being of Future Generations (Wales) Act 2015 and the Environment (Wales) Act 2016 which also have to be addressed.

We address the legal requirements directly where relevant in the body of this document.  NRW is satisfied that this decision is consistent with its general purpose of pursuing the sustainable management of natural resources (SMNR) in relation to Wales, and applying the principles of SMNR. In particular, NRW acknowledges that it is a principle of sustainable management to take action to prevent significant damage to ecosystems. We consider that, in granting the Permit a high level of protection will be delivered for the environment and human health through the operation of the Facility in accordance with the permit conditions. NRW is satisfied that this decision is compatible with its general purpose of pursuing the sustainable management of natural resources in relation to Wales and applying the principles of sustainable management of natural resources.

## 4	The Facility

### 4.1 Description of the Facility and related issues

#### 4.1.1	The permitted activities

The Facility is subject to the EPR because it carries out an activity as described in Schedule 25B of the EPR:

One Tranche B Specified Generator aggregated to <50MWth at a specified location

A Generator means any combustion plant generating electricity. The regulations use the term ‘specified generator’ to encompass both individual  generators and multiple generators at the same location or site, operated by the same Operator and for  the same purpose. The “same purpose” means that having a different function does not stop individual  generators being treated as part of a specified generator, e.g. generators with a capacity market agreement  or providing a balancing service whether they are under the same contract or not would be classed as  operating for the “same purpose” as they generate electricity. Similarly generators with different fuels or  technologies are also classed as operating for the “same purpose”.

The specified generator permit will apply to the site, rather than its constituent individual generators. All specified generators equal to or more than 1 MWth will also be Medium Combustion Plant (MCP), and must also meet the requirements of the MCP Directive, once these requirements apply from 01/01/2024.

Specified Generators are also divided into Tranche A and Tranche B sites, which will determine the relevant permitting date.  A site is a Tranche A site if it meets the following criteria:

• It came into operation before 1 December 2016, or

• It is the subject of a capacity agreement arising from the 2014 or 2015 capacity auctions

A generator with a rated thermal input of less than 1MWth will be classed as Tranche A if:

• It is the subject of a capacity agreement arising from the 2014, 2015 or 2016 capacity auctions, or

• A FiT preliminary accreditation application was received by OfGEM before 1 December 2017, or

• Is the subject of an agreement to provide balancing services entered into before 31 October 2017.

Tranche B generators are all those that are not Tranche A.

Cynon Power Limited to operate eight 4.65 MWth spark ignition reciprocating engines (one 37.2MWth Specified Generator) which are used for the purposes of electricity generation. The facility at Cynon Power Limited can be classified as a Tranche B Specified Generator, by virtue of a Short Term Operating Reserve contract with National Grid entered into in August 2018.

#### 4.1.2	The Site

Cynon Power Limited is a small 16MWe natural gas fired power station located within the Aberaman Industrial Estate on the outskirts of Aberdere, Wales. The newly-built Plant is located on a 0.5 hectare site.

#### 4.1.3	What the Facility does

The power plant is on land which is the subject of a long term lease and is self-contained and fully enclosed by a secure perimeter fence. No activities other than the generation of electricity from natural gas will take place on site. The power plant itself is made up of 8 gas fuelled spark ignition reciprocating engines manufactured by MWM. Each engine, model TCG 2020, has a maximum output of 2MWe. They are best available technology operating with an electrical efficiency of approximately 43%.

The electricity is generated by burning the gas within the spark ignition engines exporting the electricity produced at 33,000 volts onto the local distribution network owned and operated by Western Power Distribution.

Gas is supplied to the power plant via a dedicated gas pipeline connected to the medium pressure gas network owned by Wales and West Utilities. The gas engines and all associated equipment are contained within a portal steel framed building and have a combined thermal input of 37.2 MW(th). The plant is designed to operate intermittently at short notice on short duration runs, and will operate up to 2500 hours per year. The plant has been designed as a backup power generation facility providing electricity to the grid during times of low renewable energy output and peak winter demand.

#### 4.1.4	Key Issues in the Determination

The key environmental and human health issues considered during the determination of this variation were:

Air quality – Oxides of Nitrogen

This will be discussed separately in this decision document.

### 4.2 Operation of the Facility – general issues

#### 4.2.1	Administrative issues

The Applicant is the sole Operator of the Facility. We are satisfied that the Applicant is the person who will have control over the operation of the Facility if the Permit were to be granted; and that the Applicant will be able to operate the Facility so as to comply with the conditions included in the Permit, if issued.

#### Relevant Convictions

NRW’s COLINS Database has been checked to ensure that all relevant convictions have been declared.  No relevant convictions were found. The operator satisfies the criteria in RGN 5 on Operator Competence.

#### Financial Provision

There is no known reason to consider that the operator will not be financially able to comply with the permit.  The decision was taken in accordance with RGN 5 on Operator Competence.

#### 4.2.2	Management

We are satisfied that appropriate management systems and management structures will be in place for this Facility, and that sufficient resources are available to the Operator to ensure compliance with all the Permit conditions.

#### 4.2.3	Operating techniques

The operator has stated that they will implement the following quality assurance techniques and maintenance schedule, in order to for the generators to achieve and retain optimal performance. In order to enable each generator and the power plant in general to achieve and retain optimal performance in both efficiency and emissions, the plant will engage in the following best available operational management techniques:-

(a) Benchmark Performance Testing and Acceptance – On completion of the construction phase of the power plant, tests demonstrating fitness for purpose, reliability, efficiency, emissions and noise ensure the facility complies with all applicable design standards, procurement guarantees, and generally good engineering practice. Such ‘performance acceptance testing’ is carried out in accordance with ISO 3046-4:2009 (Reciprocating internal combustion engines. Performance. Speed governing). This is the main standard of performance tests for reciprocating internal combustion engines and ensures the provision of data for acceptance of the plant based on tests of appropriate scientific quality.

(b) Scheduled Maintenance – The routine operation and maintenance of the plant is contracted to the Original Equipment Manufacturer’s (OEM) UK Agent; typically also the original EPC construction contractor. Maintenance of the plant is therefore undertaken based on strict OEM schedules retaining optimised performance of the assets through-out their life-cycle (>20 years).

(c) Plant remote monitoring and operational control – The performance of each engine and the power plant is monitored continuously. During periods of generation, each generator has sophisticated control systems which monitors operational parameters within strict operating conditions. These control systems detect operation at Other than Normal Operating Conditions (OTNOC) and make adjustments to air/fuel mixture, ignition and valve timing to ensure both efficiency and ELVs are maintained. The performance of the plant is analysed and trended over time to ensure its operating efficiency and energy consumption remain optimal.

(d) Emission monitoring and engine mapping – Emissions monitoring and engine mapping is undertaken as part of scheduled annual maintenance. Measurements are taken generally in accordance with Environment Agency Technical Guidance Note M5 (Medium Combustion Plant Directive and Generator Controls: monitoring point source emissions) using equipment assessed against EN 50379-2. Measurements are made by the organisations that service and maintain the MCP as part of their maintenance regime. Sample points have been provided in readily accessible locations of the exhaust system where the exhaust gasses remain hot (>300C) and are well mixed – typically the location is within the generator housing down-stream of the engine turbochargers but before the exhaust silencing system.

(e) Analysing Plant failures and implementing improvements/remedies – Plant failures are analysed by the operations and maintenance providers for root causes. Cause is identified against maintenance procedures, design requirements and life expectancy invoking a culture of continuous improvement in all aspects of plant reliability and performance.

(f) Recording, analysis and management systems - Through continuous monitoring and remote telemetry, records of performance, maintenance and testing are retained and reviewed regularly as part of performance and commercial plant management. In performing their duties, the plant’s Operations and Maintenance providers adhere to a fully ISO accredited Health Safety and Environmental and Quality Management System (SHEQ);ISO 9001, 140001 & 180001.

The installation comprises 8 MWM TCG 2020 high efficiency gas fired spark ignition engines. Each of the engines is configured to meet the relevant emission limit of 190mg/Nm3 @15% O2 specified in EPR for Tranche B Specified Generators. The installation whilst operational is maintained per the manufacturers guidance with regular and routine servicing which involves periodic testing of emissions to ensure the plant operates in accordance with its design and continues to meet the appropriate emission limit values. Emissions tuning is carried out by the Maintenance Contractor as part of their general service work.

We have reviewed the techniques used by the operator and compared these with the relevant guidance notes. The proposed techniques/emission levels for priorities for control are in line with the benchmark levels contained in TGN M5 and we consider them to represent appropriate techniques for the facility. These are specified in the Operating Techniques table in the permit.

We have specified that the applicant must operate the permit in accordance with descriptions in the application, including all additional information received as part of the determination process.

## 5	Minimising the Facility’s environmental impact

For this kind of regulated activity, the principal emissions are emissions to air. There are no permit conditions for water, land, energy efficiency, odour or noise and BAT does not apply.

The next sections of this document explain how we have approached the critical issue of assessing the likely impact of air emissions from the SG on human health and the environment and what measures we are requiring to ensure a high level of protection.

We have reviewed the operator's assessment of the environmental risk from the facility. The operator’s risk assessment is satisfactory. The assessment shows that, applying the conservative criteria in our guidance on Environmental Risk Assessment, all emissions may be categorised as environmentally insignificant.

We will discuss the operators risk assessment in more detail as follows:

### 5.1	Assessment of Impact on Air Quality

This section of the decision document deals primarily with the dispersion modelling of emissions to air from the stack and its impact on local air quality.

The Applicant has assessed the Facility’s potential emissions to air against the relevant air quality standards, and the potential impact upon human health.  These assessments predict the potential effects on local air quality from the Facility’s stack emission.

The air impact assessments and the dispersion modelling has been based on the Facility (peaking plant) operating on a rolling flexible average of up to 2500 hours per year. The assumptions underpinning the model have been checked and are reasonably precautionary. The way in which the Applicant used dispersion models, its selection of input data, use of background data and the assumptions it made have been reviewed by Natural Resources Wales modelling specialists to establish the robustness of the Applicant’s air impact assessment. The output from the model has then been used to inform further assessment of health impacts.

Manufacturer emission limits have been used for the purposes of the modelling assessment and the facility is assumed to be operating at full load for 2500 hours per year for long-term impacts and all hours of the year for short-term impacts.

All long-term impacts at human receptors are predicted to be below limit values at locations where the Air Quality Directive states that they must be applied, and therefore not significant (ie PC below 1% or PEC below 70% of their relevant objectives).The maximum short-term NO2 impact exceeds the EA/NRW criteria, however given the conservative nature of the assessment and the fact all PECs fall well below the AQO, the impact is predicted to be insignificant.

A cumulative assessment to take into account emissions from the neighbouring UK Power Reserve Network Peaking Plant has been undertaken. Background annual concentrations at each receptor were increased by the predicted Cynon Peaking Plant PC to represent the emissions from the UKPR Peaking Plant to calculate the adjusted background concentrations. PCs from the Cynon Peaking Plant were then added to the adjusted background to calculate the PEC for annual NO2 and NOx, and twice the annual backgrounds to calculate short term NO2 and NOx PEC concentrations. Impacts were found to be insignificant.

In summary, the air quality impact of the Cynon Peaking Plant is considered to be below limits at relevant human receptor locations.

### 5.2	Impact on Habitats sites, SSSIs, non-statutory conservation sites etc

There is one SSSI within the relevant 2km radius screening distance from the site -  Caeau Nant Y Groes SSSI. A CRoW Appendix 4 (140_10_SD02) form has been submitted with regards to this application, the conclusions of which are summarised below.

An assessment has been carried out to determine the local air quality impacts associated with the operation Cynon Peaking Plant. Detailed air quality modelling using the AERMOD dispersion model has been undertaken to predict the impacts associated with stack emissions from the peaking plant. The assessment has found that there will be no exceedances of the relevant Air Quality Objectives at locations of relevant exposure as a result of emissions from the Peaking Plant.

The Air Quality modelling assessment has been run with the Peaking Plant as a standalone operation, and also separately with background cumulative emissions. The assessment has shown that Annual NOx process contributions are below 1% of the critical level and as such can be considered ‘insignificant’. Short term NOx concentrations exceed the NRW/EA criteria at each receptor; however, the short-term assessment has been run for 8760 hours, far exceeding the maximum number of hours the plant is expected to run for (2500 hrs) and PEC concentrations fall well below the applicable critical level, as such the impacts are still considered to be ‘insignificant’.

The contribution of the Peaking Plant to total nitrogen & acid deposition is less than 0.16% of the relevant critical load. Based on NRW guidance this level of impact on nitrogen & acid deposition is ‘insignificant’. In summary, the air quality impact of the Cynon Peaking Plant is considered to be below limits at relevant habitat receptor locations.

### 5.3 European Sites

There are no designated European sites (SACs, SPAs or Ramsar sites) within a 5km radius of the site, and thus no impact assessment was required for these designations.

## Assessment of Likely Significant Effect:

N/A

## Appropriate assessment:

N/A

## HRA Overall conclusion:

An assessment of the impact on nearby sensitive ecological sites has been completed. The impact on airborne NOx concentrations and nitrogen deposition at the sensitive habitats was determined to be insignificant.

## 6  Setting ELVs and other Permit conditions

We have decided that emission limits should be set for the parameters listed in the permit.  Emissions Limit Values (ELVs) are in line with those set out in Schedule 25B covering Specified Generators (and the MCP Directive where applicable).

### 6.1	Monitoring

We have decided that monitoring should be carried out for the parameters listed in Schedule 3 of the permit using the methods and to the frequencies specified in those tables.  These monitoring requirements have been imposed in order to demonstrate compliance with the emissions limits in the permit, as per the ELV and monitoring frequency requirements specified within the EPR Schedule 25B Regulations.

For a Tranche B Specified Generator, that is an engine fuelled on natural gas, the monitoring requirements are as follows:

| Pollutant | Type of Specified Generator | Fuel Type | Emission Limit Value (mg/Nm3) | Monitoring Required |
| --- | --- | --- | --- | --- |
| NOx | Spark Ignition Engine | Natural Gas | 190* | Periodic – every 3 years |

*380 mg/Nm3 for dual fuel engines in gas mode.

Monitoring will be required on each individual generator unit that comprises the Specified Generator, at least once, and at the frequency specified.  Emission limit values are defined at a temperature of 273,15 K, a pressure of 101,3 kPa and after correction for the water vapour content of the waste gases and at a standardised O2 content of 15% for engines (and gas turbines).

For emissions to air, the methods for continuous and periodic monitoring are in accordance with the Environment Agency’s Technical Guidance Note M5 for monitoring of stack gas emissions from medium combustion plants and specified generators.

Based on the information in the Application and the requirements set in the conditions of the permit we are satisfied that the monitoring techniques, personnel and equipment employed by the Operator will have either MCERTS certification or MCERTS accreditation as appropriate.

### 6.2	Other Permit Conditions

As a Specified Generator, the facility must adhere to the following operating techniques for SG.

As a Specified Generator (SG), these are:

  - Each generator must be operated in accordance with the manufacturer’s instructions and records must be made and retained to demonstrate this.

  - The operator must keep periods of start-up and shut down of the generators as short as possible

  - There must be no persistent emission of ‘dark smoke’ as defined in section 3(1) of the Clean Air Act 1993.

  - Where secondary abatement is required to ensure compliance with the NOx ELV it must be met within 10 minutes from when the generator commences operation or within 20 minutes when the generator was a Tranche A and is now a Tranche B generator.

  - The stack must be vertical and unimpeded by cowls or caps.

### 6.3	Reporting

We have specified the reporting requirements in Schedule 4 of the Permit to ensure data is reported to enable timely review by Natural Resources Wales to ensure compliance with permit conditions.

### 7 Specified Generator Charges and Subsistence Fees

The type of application regarding Specified Generators will have an associated charge. The Specified Generator application type will also form the basis for ongoing subsistence fee’s.  More information on this can be found in our charging scheme on our website.