Site Condition Report evaluation form

	Applicant
	Arcadis (UK) Limited

	Permit reference
	PAN-017388

EPR/MB3333RY/S003

	Address
	Meritor Heavy Vehicle Braking Systems (UK) Ltd, Meritor H V B S (UK) Ltd, Grange Road, Cwmbran, Torfaen, NP44 3XU

	Grid reference
	ST 29680 95190

	Activity Type
	A17 Physico-Chemical Treatment Facility- remediation activity for the treatment of contaminated groundwater.


	SCR document reference
	XXXXXXXX-AUK-XX-XX-RP-ZZ-0001-01-site condition report at surrender _VM_ED_JS

	SCR date and version number
	Dated: February 2022

Submitted:10/03/22


	1.0 Site details (Source)

	Has the applicant provided the following information as required by the application SCR template?
	Response 

	Site plans showing site layout, drainage, surfacing, receptors, sources of emissions/releases and monitoring points


	Required site plans were provided with original application in 2012/13.

Site plans provided with surrender: 

· 909364112-SLP (Site Location Plan)

· 909364168 - Site Layout Plan

· 909364167 - Remediation area layout plan

· 909364166 - Remediation system layout plan – georef

· 909363812 - Anticipated Distribution of Dissolved Phase CVOC Plume Beneath the Zone 3 Area

· 909364110 - Anticipated Extent of LNAPL

· 909364111- On-site drainage and SW outfalls

· 909364113 - Odour monitoring points

· 909364114 - VOC monitoring points

· 909364115 - Noise monitoring points

· 909364116 - GW monitoring points

· 909364159 - Anticipated Extent of Impacts to Groundwater Quality SSAC Protective of Water Resources

· 2766210431_02 Remediation Verification Report /July 2019 – Figure 2: Pre-remediation source areas: CVOC

· 2766210431_02 Remediation Verification Report /July 2019 – Figure 3: Pre-remediation source areas: Petroleum Compounds

. 


	2.0 Condition of the land at permit issue (Receptor)

	Has the applicant provided the following information as required by the application SCR template?
	Response 

	a) Environmental setting including geology, hydrogeology and surface waters

b) Pollution history including:

· pollution incidents that may have affected land

· historical land-uses and associated contaminants

· visual/olfactory evidence of existing contamination

· evidence of damage to existing pollution prevention measures

c) Evidence of historic contamination (i.e. historical site investigation, assessment, remediation and verification reports (where available)

d) Has the applicant chosen to collect baseline reference data?
	Geoscience assessment at time of original application in 2012/13:

· Sufficient information has been submitted through planning to GWCL to address these bullet points. A baseline groundwater monitoring round has been carried out
Further information provided in section 2 of the surrender site condition report.




	3.0 Permitted activities (Source)

	Has the applicant provided the following information

as required by the application SCR template?
	Response 

	a) Permitted activities

b) Non-permitted activities undertaken at the site


	a) remediation activity for the treatment of contaminated groundwater

b) Monitoring of groundwater and soil gas quality throughout the active remediation period.


	3.0(a) Environmental Risk Assessment (Source)

	The H1 environmental risk assessment should identify elements that could impact on land and waters, cross- referenced back to documents and plans provided as part of the wider permit application.
	Risk assessment provided and assessed at time of original application in 2012/13:


	3.0(b) Will the pollution prevention measures protect land and groundwater? (Conceptual model)

	Are the activities likely to result in pollution of land?
	None identified at time of original application in 2012/13

	For dangerous and/or hazardous substances only, are the pollution prevention measures for the relevant activities to a standard that is likely to prevent pollution of land?
	n/a


	4.0 Changes to the activities (Source)

	Have there been any changes to the following during the operation of the site?
	Response 

	a) Activity boundaries

b) Permitted activities

c) “Dangerous substances” used or produced
	a) no changes- the permitted activities were only carried out in Zone 3.

b) no changes

c) no changes


	5.0 Measures taken to protect land (Pathway)

	Has the applicant provided evidence from records collated during the lifetime of the permit, to show that the pollution prevention measures have worked?
	Information provided in section 5 of the surrender site condition report:

· all treatment and storage contained in a bunded area.

· waste produced by the remediation process were stored in sealed containers in a bunded area.

· monthly site inspections and proactive maintenance carried out where necessary.

Following records kept, examples supplied with the surrender:

· Appendix A: Treated water discharge records are presented to demonstrate emissions were within the permitted limits of the facility discharge consent during operation of the permitted activity. 

· Appendix B: An example of monthly site inspection records is presented 

· Appendix C: An example of maintenance site visit records is presented. 

· Appendix F: An example of in-situ gas monitoring site records 

· Appendix E: An example of waste transfer notes 


	6.0 Pollution incidents that may have impacted on land and their remediation (Sources)

	Has the applicant provided evidence to show that any pollution incidents which have taken place during the life of the permit, and which may have impacted on land or water have been investigated and remediated (where necessary)?
	n/a no pollution incidents identified on the DMS or EDRM or highlighted by compliance team


	7.0 Soil gas and water quality monitoring

	Where soil gas and/or water quality monitoring has been undertaken, does this demonstrate that there has been no change in the condition of the land? Has any change that has occurred been investigated and remediated?


	Monitoring undertaken is to show the effectiveness of the remediation activity, however it would also identify any significant spills or releases from the remediation system should these have occurred. 

Permitted activity has largely been successful in completing its task. 
Further information is provided in section 7 of the surrender site condition report.


	8.0 Decommissioning and removal of pollution risk

	Has the applicant demonstrated that decommissioning works have been undertaken and that all pollution risks associated with the site have been removed? Has any contamination of land that has occurred during these activities been investigated and remediated?
	Confirmed: 

· extraction and monitoring wells have been backfilled and capped.

· equipment decontaminated

· pumps, pipework, GAC vessels, separators, above ground containers and all waste removed

Further information is provided in section 8 of the surrender site condition report.

Supported by: 

· Appendix D Decommissioning Pictures 

· Appendix J Decommissioning Report Section 

· Fig 5 909364516 - SVE remediation system layout - georef-A3P_rev 

Final site visit was carried out on 14/09/2022. Compliance Assessment Report CAR_NRW0040396 confirms that the operation is no longer occurring on site, and all equipment has been removed. The Drainage system and access covers Arcadis used have all be sealed with concrete or removed.


	9.0 Reference data and remediation

	Has the applicant provided details of any surrender reference data that they have collected and any remediation that they have undertaken? 

	Yes:

Main documents:

· 2766210516_01 Remediation Closure Plan For LNAPL and CVOC Remediation – ZONE 3 Meritor Heavy Vehicle Breaking Systems, dated July 2017

· 2766210431_02 Remediation Verification Report for LNAPL and CVOC Remediation – ZONE 3 Meritor Heavy Vehicle Braking Systems, dated July 2019. 

Monitoring data- 2766210431_02 Remediation Verification Report /July 2019 

· Appendix D1: Concentrations of Volatile Organic Compounds Pre, During Remedial Measures, and During Verification Monitoring Appendix D2: detailed remediation trend graphs for groundwater samples collected from selected wells within the treatment area (CVOCs) 

· Figure 5: verification monitoring well locations (CVOCs) 

· Appendix E.2 Percentage Reduction in LNAPL Levels - Extraction Wells 

· Appendix E.3 Extraction Well Trend Data 

· Appendix E.5: Cumulative LNAPL Recovery April 2013 to March 2017 

· Appendix E.7 Total Petroleum Hydrocarbons in Groundwater (μg/l) 

· Figure 9: Biannual LNAPL recovery progress groundwater monitoring well location plan 

· Appendix F Bulk Ground Gas Monitoring 

Revised Quantitative Risk Assessment: 

· 2766210516_01 Remediation Closure Plan /July 2017 - Appendix E.1 - Quantitative Risk Assessment Review: Human Health Risk Assessment Review, Water Resources Risk Assessment Review 

Statement of completion: 

· 2766210431_02 Remediation Verification Report /July 2019, Section 8 

Geoscience comments: 

happy for the permit to be surrendered on the basis of no additional pollution/deterioration (as a result of the remediation works themselves) and that the agreed remediation criteria have been broadly met.

	If the surrender reference data shows that the condition of the land has changed as a result of the permitted activities, the applicant will need to undertake remediation to return the condition of the land back to that at permit issue. You should not require remediation of historic contamination or contamination arising from non-permitted activities as part of the permit surrender.
	n/a


	10.0 Statement of site condition 

	Has the applicant provided a statement, backed up with evidence, confirming that the permitted activities have ceased, decommissioning works are complete, and that pollution risk has been removed and that the land and waters at the site are in a satisfactory state? 
	Yes:
· The treatment infrastructure required for the Permitted Activity has been decommissioned and removed from site.

· Monitoring and extraction wells have been decommissioned.

· Groundwater quality has been improved over the lifetime of the Environmental Permit.


	Surrender SCR decision summary
	Tick relevant decision

	Sufficient information has been supplied to show that pollution risk has been removed and that the site is in a satisfactory state – accept the application to surrender the permit
	X

	Insufficient information has been supplied to show that pollution risk has been removed or that the site is in a satisfactory state – do not accept the application to surrender the permit. The following information must be obtained from the applicant before the permit is determined
	

	Date and name of reviewer
	Louise Bailey
14/09/2022


Page 1
Page 1

