Schedule 5 - Notification 

These pages outline the information that the operator must provide. 

Units of measurement used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission. Where appropriate, a comparison should be made of actual emissions and authorised emission limits.

If any information is considered commercially confidential, it should be separated from non-confidential information, supplied on a separate sheet and accompanied by an application for commercial confidentiality under the provisions of the EP Regulations.

Part A 
	Permit Number
	BJ9681IX

	Name of operator
	Essity UK Ltd Oakenholt Mill.

	Location of Facility
	Chester Road, Oakenholt, Flintshire, CH6 5PU

	Time and date of the detection 
	12th December


	(a) Notification requirements for any malfunction, breakdown or failure of equipment or techniques, accident, or emission of a substance not controlled by an emission limit which has caused, is causing or may cause significant pollution

	To be notified within 24 hours of detection

	Date and time of the event
	00:45 12/12/22

	Reference or description of the location of the event 
	Effluent treatment plant discharge

	Description of where any release into the environment took place
	

	Substances(s) potentially released
	

	Best estimate of the quantity or rate of release of substances
	

	Measures taken, or intended to be taken, to stop any emission
	

	Description of the failure or accident.
	Due to very low temperatures (-6°C), some solenoid valves froze. 


	(b) Notification requirements for the breach of a limit

	To be notified within 24 hours of detection unless otherwise specified below

	Emission point reference/ source
	W1

	Parameter(s)
	Flow Rate 

	Limit
	108 m³/hr 

	Measured value and uncertainty
	121.25 m³/hr 

	Date and time of monitoring
	12th December 2022 00:45 

	Measures taken, or intended to be taken, to stop the emission
	Improved insulation of solenoid valves.


	Time periods for notification following detection of a breach of a limit

	Parameter
	Notification period

	
	

	
	

	
	


	Notification requirements for the detection of any significant adverse environmental effect

	To be notified within 24 hours of detection

	Description of where the effect on the environment was detected
	

	Substances(s) detected
	

	Concentrations of substances detected
	

	Date of monitoring/sampling
	


Part B – to be submitted as soon as practicable
	Any more accurate information on the matters for notification under Part A.
	Solenoid values froze due to moist air being able to enter the control panel as air receiver drain had frozen.

	Measures taken, or intended to be taken, to prevent a recurrence of the incident
	The air receiver has now been insulated and a heating element installed in the panel to prevent recurrence.

	Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment which has been or may be caused by the emission
	

	The dates of any unauthorised emissions from the facility in the preceding 24 months.
	NOx breaches – Jan 22 & Nov 22

Suspended solids – 2 x Oct 21


	Name*
	Dawn Harris

	Post
	Quality & Environment Manager 

	Signature
	Via Email Account

	Date
	13th December 2022


* authorised to sign on behalf of the operator


