Schedule 5 - Notification 

These pages outline the information that the operator must provide. 

Units of measurement used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission. Where appropriate, a comparison should be made of actual emissions and authorised emission limits.

If any information is considered commercially confidential, it should be separated from non-confidential information, supplied on a separate sheet and accompanied by an application for commercial confidentiality under the provisions of the EP Regulations.

Part A 
	Permit Number
	BJ9681IX

	Name of operator
	Essity UK Ltd Oakenholt Mill.

	Location of Facility
	Chester Road, Oakenholt, Flintshire, CH6 5PU

	Time and date of the detection 
	Reported received on 24th November 2022


	(a) Notification requirements for any malfunction, breakdown or failure of equipment or techniques, accident, or emission of a substance not controlled by an emission limit which has caused, is causing or may cause significant pollution

	To be notified within 24 hours of detection

	Date and time of the event
	

	Reference or description of the location of the event 
	

	Description of where any release into the environment took place
	

	Substances(s) potentially released
	

	Best estimate of the quantity or rate of release of substances
	

	Measures taken, or intended to be taken, to stop any emission
	

	Description of the failure or accident.
	


	(b) Notification requirements for the breach of a limit

	To be notified within 24 hours of detection unless otherwise specified below

	Emission point reference/ source
	A1b

	Parameter(s)
	Oxides of Nitrogen 

	Limit
	Oxides of Nitrogen – 250 mg/m³ 

	Measured value and uncertainty
	Oxides of Nitrogen - 327 mg/m³ 
Measurement Uncertainty – 13 mg/m³ 

Reference Conditions (REF) are: 273K, 101.3kPa, dry gas, 3% oxygen.

	Date and time of monitoring
	24th November 2022 13:02 -14:02 (60-minute duration)

	Measures taken, or intended to be taken, to stop the emission
	Orders have already been placed for the replacement of the Bono Boiler combustion burner and associated control system. 



	Time periods for notification following detection of a breach of a limit

	Parameter
	Notification period

	
	

	
	

	
	


	Notification requirements for the detection of any significant adverse environmental effect

	To be notified within 24 hours of detection

	Description of where the effect on the environment was detected
	

	Substances(s) detected
	

	Concentrations of substances detected
	

	Date of monitoring/sampling
	


Part B – to be submitted as soon as practicable
	Any more accurate information on the matters for notification under Part A.
	None

	Measures taken, or intended to be taken, to prevent a recurrence of the incident
	Gensuite Concern Report #151667, Corporate Escalation event ID #14 are in place. Funding has been allocated and orders have been placed for the burner replacement and associated control system. This was planned for Q4 2022, however delivery has been delayed due to availability of electrical components. The burner is now expected to be commissioned in Q1 2023

	Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment which has been or may be caused by the emission
	The management team are committed to the replacement of the current Burner and Control System with a low NOx equivalent. 

	The dates of any unauthorised emissions from the facility in the preceding 24 months.
	13th Aug 2020, 8th Sept 21, 8th Dec 21.


	Name*
	Dawn Harris

	Post
	Quality & Environment Manager 

	Signature
	Via Email Account

	Date
	13th December 2022


* authorised to sign on behalf of the operator



