Schedule 5 - Notification 

These pages outline the information that the operator must provide. 

Units of measurement used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission. Where appropriate, a comparison should be made of actual emissions and authorised emission limits.

If any information is considered commercially confidential, it should be separated from non-confidential information, supplied on a separate sheet and accompanied by an application for commercial confidentiality under the provisions of the EP Regulations.

Part A 

	Permit Number
	EPR/LP3030XA

	Name of operator
	Viridor Waste Management Limited

	Location of Facility
	Cardiff Energy from Waste Facility, Trident Park, Cardiff.

	Time and date of the detection 
	Approx. 00:30H on  10 January 2019 


	(a) Notification requirements for any malfunction, breakdown or failure of equipment or techniques, accident, or fugitive emission which has caused, is causing or may cause significant pollution

	To be notified within 24 hours of detection

	Date and time of the event
	

	Reference or description of the location of the event 
	

	Description of where any release into the environment took place
	

	Substances(s) potentially released
	

	Best estimate of the quantity or rate of  release of substances
	

	Measures taken, or intended to be taken, to stop any emission
	

	Description of the failure or accident.
	


	(b) Notification requirements for the breach of a limit

	To be notified within 24 hours of detection unless otherwise specified below

	Emission point reference/ source
	A2; 

	Parameter(s)
	CO

	Limit
	Daily Mean              50mg/m3

Updated on 22 January 2019.  Breach of a CO 10 minute average also occurred value of 181.85 when ELV is 150mg/m3  

      

	Measured value and uncertainty
	Between 00:00 and 23:59H on 9 January 2019 the DAILY  MEAN was recorded at 94.00mg/m3



	Date and time of monitoring
	9 January 2019 continuous monitoring undertaken 

	Measures taken, or intended to be taken, to stop the emission
	As this was a Daily Mean exceedance then a review meeting was held on 10 January 2019 between Shift Team Leader (Shane Holyoake) and Gwyn Jones. The meeting concluded that on the 9 January 2019 Viridor had Industrial Cleaning contractor on site undertaking a “bang and clean” procedure on Line 2. The action of opening entry points to the incineration process gave rise to combustion instability and a CO release.  Today (10 January 2019) we are running normal operations and no ELVs have occurred. 
  


	Time periods for notification following detection of a breach of a limit

	Parameter
	Notification period

	
	


	(c) Notification requirements for the detection of any significant adverse environmental effect

	To be notified within 24 hours of detection

	Description of where the effect on the environment was detected
	

	Substances(s) detected
	

	Concentrations of substances detected
	

	Date of monitoring/sampling
	


Part B - to be submitted as soon as practicable

	Any more accurate information on the matters for notification under Part A.
	Updated Part B

There were two clusters of CO spikes immediately following boiler trips. The boiler trips resulted from high back end pressure which tripped the Induced Draught (ID) fan.  Getting the boiler stabilised when back on contributed to the CO spikes as the Under-Fire Air (UFA) was low for a period of time during furnace stabilisation. 
Updated on 22 January 2019 . . . Having completed a data review of all 144 CO data values for that day it has been calculated that there was a single (1 of) breach of the 10 minute average. The breach value was 181.85 when the ELV was 150mg/m3. Actions already addressed with the Daily Mean breach action plan.


	Measures taken, or intended to be taken, to prevent a recurrence of the incident
	Review of the Industrial Cleaning procedure. Review of Standard Operating Procedure (SOP) undertaken.  Action complete. 


	Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment which has been or may be caused by the emission
	Short term event. Action complete.

	The dates of any unauthorised emissions from the facility in the preceding 24 months.
	22/02/2017 

17/04/2017 

22/04/2017 

24/04/2017 

02/05/2017  

30/05/2017  

01/06/2017 
06/06/2017  
09/06/2017  

18/06/2017 

19/06/2017 

29/06/2017 

04/07/2017 

21/07/2017 

24/07/2017 

28/07/2017 

31/07/2017
19/12/2017

24/9/2018


Part C

	Permit Number
	EPR/LP3030XA

	Name of operator
	Viridor Waste Management Limited

	Location of installation
	Cardiff Energy from Waste Facility, Trident Park, Cardiff.


	Time at which abnormal operation commenced
	

	Time at which abnormal operation ceased
	

	Duration of this incidence of abnormal operation
	

	Cumulative abnormal operation duration in current year (at end of present incidence)
	

	Reasons for abnormal operation
	

	How did the abnormal operation end? (e.g. plant repaired, reaching maximum permitted duration, initiation of shutdown, etc.)
	

	Where the abnormal operation was caused by the failure of the particulate, CO or TOC CEM, attach a copy of the alternate monitoring data which was used to demonstrate compliance with the abnormal operation emission limit values.
	

	Where abatement plant has failed, give the half-hourly average emissions for pollutants of relevance during the abnormal operation in the rows below

	Pollutant
	1st ½ hour
	2nd ½ hour
	3rd ½ hour
	4th ½ hour
	5th ½ hour
	6th ½ hour
	7th ½ hour
	8th ½ hour

	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	

	Name*
	Gwyn Jones

	Post
	EHS Manager

	Signature
	G Jones 

	Date
	22_1_2019


* authorised to sign on behalf of Viridor Waste Management Limited
