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Notice of variation and consolidation with introductory note
The Environmental Permitting (England & Wales) Regulations 2016	

Dŵr Cymru Cyfyngedig

Tenby Wastewater Treatment Works
Gumfreston
Nr Tenby
SA70 8RA

Variation application number
PAN-021848
Permit number
BP0251904	




	





Tenby Wastewater Treatment Works
Permit number BP0251904
Introductory note
This introductory note does not form a part of the permit

The following notice gives notice of the variation and consolidation of an environmental permit.

This permit has been varied following an application from DCWW to correct an error in the suspended solids compliance statistic in Table S3.1. The registered office of DCWW has also been updated.

The schedules specify the changes made to the permit.

The status log of the permit sets out the permitting history, including any changes to the permit reference number. It is not backdated before 6 April 2010.

	Status Log of the permit

	Detail
	Date
	Comments

	Application BP0251904/V001
(variation and
consolidation)
	Duly made 20/03/2013
	Application to vary UV dose from applied to measured applied dose and update the permit to modern conditions.

	Variation determined BP0251904
	28/07/2016
	Varied and consolidated permit issued in modern condition format.

	Regulator-initiated variation
Application PAN-021848
	Duly Made
25/04/2023
	Admin variation to correct the total suspended solids limits.

	Variation Issued
BP0251904
	10/05/2023
	Varied permit issued to Dŵr Cymru Cyfyngedig.



End of Introductory Note
	[bookmark: _Toc77056945]
Notice of variation and consolidation 


The Environmental Permitting (England and Wales) Regulations 2016

[bookmark: _Hlt13295849]The Natural Resources Body for Wales (“Natural Resources Wales”) in exercise of its powers under regulation 20 of the Environmental Permitting (England and Wales) Regulations 2016 varies and consolidates

Permit number
BP0251904

[bookmark: _Hlk13917238]Issued to
Dŵr Cymru Cyfyngedig (“the operator”)

[bookmark: InstallationAddress21]whose registered office is
Linea 
Fortran Road 
St Mellons 
Cardiff 
CF3 0LT

company registration number 02366777

to operate a water discharge activity at
[bookmark: _Hlk133939202]Tenby Wastewater Treatment Works
Gumfreston
Nr Tenby
SA70 8RA

to the extent set out in the schedules.

The notice shall take effect from 10/05/2023.

	Name
	Date

	Emma Jones
	10/05/2023



Authorised on behalf of Natural Resources Wales

Schedule 1
The following conditions were varied as a result of the application made by the operator:
• Altered: Table S3.1

Schedule 2 – consolidated permit
Consolidated permit issued as a separate document. 
Variation application: 
PAN-021848	Page iv
	
Permit


The Environmental Permitting (England and Wales) Regulations 2016

Permit number
BP0251904

This is the consolidated permit referred to in the variation and consolidation notice for application PAN-021848 authorising 

Dŵr Cymru Cyfyngedig (“the operator”)

whose registered office is
Linea 
Fortran Road 
St Mellons 
Cardiff 
CF3 0LT

company registration number 02366777

to operate a water discharge activity at
Tenby Wastewater Treatment Works
Gumfreston
Nr Tenby
SA70 8RA

to the extent authorised by and subject to the conditions of this permit.

	Name
	Date

	Emma Jones
	10/05/2023


Authorised on behalf of Natural Resources Wales


Conditions

1 Management
1.1 General management
1.1.1 The operator shall manage and operate the activity:
(a) in accordance with a written management system that identifies and minimises risks of pollution so far as is reasonably practicable, including those risks arising from operations, maintenance, accidents, incidents, non-conformances and those drawn to the attention of the operator as a result of complaints; and
(b) using sufficient competent persons and resources.
1.1.2 Records demonstrating compliance with condition 1.1.1 shall be maintained.
1.1.3 Any person having duties that are or may be affected by the matters set out in this permit shall have convenient access to a copy of the permit.

2 Operations
2.1 Permitted activities
2.1.1 The only activity authorised by the permit is the activity specified in schedule 1 table S1.1.

2.2 The site
2.2.1 The discharge activity shall take place at the discharge point marked on the site plan at schedule 7 to this permit, and as listed in table S3.2; and, the operating techniques that are the subject of conditions prefixed by 2.3 shall be applied at the location shown, or otherwise described, in schedule 7.

2.3 Operating techniques
2.3.1 For the activity referenced in schedule 1, table S1.1 The operator shall comply with the relevant requirements of the Urban Waste Water Treatment (England and Wales) Regulations 1994.
2.3.2 
(a) The discharge in schedule 3 table S3.3b shall consist solely of secondary treated sewage effluent which has been disinfected by means of ultra violet (UV) radiation as specified in that table.
(b) The full dose limit in schedule 3 table S3.3b must be exceeded in at least 99% of the specified measurements in any period of 12 consecutive months/the period specified in schedule 3 table S3.3b.
(c) No more than 10% of measurements taken consecutively during any 24 hour period from midnight to midnight should fall below the 50% dose limit specified in schedule 3 table S3.3b.
(d) In the event of a failure of the flow monitor and/or UV transmittance meter used in the control of the UV dosing system:
(i) the maximum available number of duty banks of UV lamps shall be automatically activated;
(ii) the minimum applied UV dose at maximum effluent flow rates calculated using the 5%ile transmittance shown in schedule 3 table S3.3b, shall not be less than the full dose limit shown in that table.
(e) There shall be no failure to achieve the full dose limit in schedule 3 table S3.3b which is as a result of planned maintenance.

3 Emissions and monitoring
3.1 Emissions to water
3.1.1 The limits given in schedule 3 table S3.1 shall not be exceeded.
3.1.2 The limits in schedule 3 table S3.1 to which this condition applies may be exceeded where: in any series of samples of the discharge taken at regular but randomised intervals in any period of twelve consecutive months as listed in column 1 of schedule 3A, no more than the relevant number of samples, as listed in column 2 of schedule 3A, exceed the applicable limit for that relevant parameter. For relevant parameters subject to schedule 3C the assessment is based on a fixed calendar year from 1 January to 31 December inclusive.
3.1.3 
(a) For the emission limits in schedule 3 table S3.1 to which this condition applies, no sample of the discharge taken at a time when unusual weather conditions are adversely affecting the operation of the waste water treatment works, shall be taken into account in deciding whether or not the emission limit has been complied with.
(b) On any occasion where unusual weather conditions adversely affect the operation of the waste water treatment works, the operator shall use its best endeavours to mitigate that adverse effect.
(c) For any sample of the discharge taken to be considered for the purposes of (a) above, the operator shall notify Natural Resources Wales in writing within 14 days of becoming aware that an emission limit has been exceeded. That notification shall include a full description of the unusual weather conditions and their impact on the operation of the works.
3.1.4 
(a) For the emission limits in schedule 3, table S3.1 to which this condition applies, no sample of the discharge taken at a time when abnormal operating conditions are adversely affecting the operation of the waste water treatment works, shall be taken into account in deciding whether or not the emission limit has been complied with.
(b) On any occasion where abnormal operating conditions adversely affect the operation of the waste water treatment works, the Operator shall use its best endeavours to mitigate that adverse effect.
(c) For any sample of the discharge taken to be considered for the purposes of (a) above, the Operator shall notify Natural Resources Wales in writing within 14 days of becoming aware that an emission limit has been exceeded. That notification shall include a full description of the abnormal operating conditions and their impact on the operation of the works.


3.1.5 
(a) If the measured Dry Weather Flow exceeds the permitted Dry Weather Flow limit then the operator shall, as soon as is practicable, investigate the reasons for the exceedance. The operator shall report the reasons for the exceedance to Natural Resources Wales and the steps that it proposes to take to restore compliance. An exceedance of the Dry Weather Flow limit shall not be recorded as a failure if the operator takes appropriate steps to restore compliance;
(b) If the measured Dry Weather Flow exceeds the permitted Dry Weather Flow limit because of unusual rainfall during the 12-month period, then it will not be recorded as a failure of the Dry Weather Flow limit. For the purposes of this condition, unusual rainfall shall mean rainfall that causes significantly higher sewage flows during the three-month period that normally records the lowest flows;
(c) The permitted Dry Weather Flow limit is set at the operator’s planned annual 80% exceeded flow;
(d) For compliance with this permit, the measured Dry Weather Flow is that total daily volume that is exceeded by 90% of the recorded measured total daily volume values in any period of 12 months; and
(e) For unusual rainfall to be considered, the operator shall notify Natural Resources Wales and provide supporting evidence as part of the normal specified data returns.

3.2 Emissions of substances not controlled by emission limits
3.2.1 The operator shall take appropriate measures to minimise so far as reasonably practicable the polluting effects of the emissions of substances in the discharge not controlled by emission limits (excluding odour).

3.3 Monitoring
3.3.1 The operator shall, unless otherwise agreed in writing by Natural Resources Wales, undertake the monitoring specified in the following tables in schedule 3 to this permit:
(a) point source emissions specified in tables S3.1 and S3.4;
(b) inlet quality specified in tables S3.1 and S3.4;
(c) efficacy monitoring specified in tables S3.4 and S3.5.
3.3.2 The operator shall maintain records of all monitoring required by this permit.
3.3.3 Monitoring equipment, techniques, personnel and organisations employed for the emissions monitoring programme (and the environmental or other monitoring) specified in condition 3.3.1 shall have either MCERTS certification or MCERTS accreditation (as appropriate), where available, unless otherwise agreed in writing by Natural Resources Wales.
3.3.4 Accessible monitoring points shall be provided and maintained to enable the emissions monitoring programme sampling/monitoring of emissions to be carried out at the monitoring points specified in table S3.4 of schedule 3 and shown marked on the site plan in schedule 7.
3.3.5 The monitoring programme for the parameters subject to schedule 3B shall be:
(a) pre-scheduled to cover a calendar year and the programme recorded before the start of a calendar year sample period; and
(b) spot samples collected at approximately equal intervals during the year, including samples from different days of the week and different times. Approximately 10% of samples should be outside the normal sampling window which is 9am-3pm, Monday to Friday.
3.3.6 After becoming aware, or following a notification that a sample has not been taken on the schedule 3B Monitoring Programme pre-scheduled date, or is lost, or a result for that sample cannot be reported, the operator shall record the details and reschedule the sample.
3.3.7 The monitoring programme for the parameters subject to schedule 3C shall be:
(a) pre-scheduled before each calendar year.
(b) Unless otherwise agreed in writing by the Natural Resources Wales, the operator shall submit the monitoring programme for the following calendar year to the Natural Resources Wales before the 1st of December; and

(c) samples must be collected at approximately equal intervals during the year from different days of the week and approximately 10% of samples should be taken at weekends

3.3.8 Unless otherwise agreed in writing by the Natural Resources Wales, after becoming aware, or following notification that a sample has not been taken on the schedule 3C Monitoring Programme pre- scheduled date, or is lost, or a result for that sample cannot be reported, the operator shall notify Natural Resources Wales of the missed event and the reschedule date as soon as reasonably practicable.
3.3.9 Continuous recorders, with on-site visual display from which readings may be readily obtained, shall be provided and maintained by the operator and the following shall be measured and recorded at 15 minute intervals:
(a) the instantaneous flow rate through each UV irradiation channel;
(b) the instantaneous measured applied UV dose for each UV irradiation channel;
(c) the number of operational UV lamps for each UV irradiation channel;
(d) the instantaneous measured UV transmittance at the inlet to the UV irradiation plant;
(e) any other parameters used in calculating the UV dose.

4 Information
4.1 Records
4.1.1 All records required to be made by schedule 3, 4 and 5 to this permit shall:
(a) be legible;
(b) be made as soon as reasonably practicable;
(c) if amended, be amended in such a way that the original and any subsequent amendments remain legible, or are capable of retrieval; and
(d) be retained, unless otherwise agreed in writing by Natural Resources Wales, for at least 6 years from the date when the records were made.
4.1.2 The operator shall maintain convenient access, in either electronic or hard copy, to the records, plan and management system required to be maintained by this permit.

4.2 Reporting
4.2.1 The operator shall send all reports and notifications required by the permit to Natural Resources Wales using the contact details supplied in writing by Natural Resources Wales.
4.2.2 Within the time period after the end of the reporting period specified in schedule 4 table S4.1 the operator shall, unless otherwise agreed in writing by Natural Resources Wales, submit reports of the monitoring and assessment carried out in accordance with the conditions of this permit, as follows:
(a) in respect of the parameters and monitoring points specified in schedule 4 table S4.1;
(b) [for the reporting periods specified in schedule 4 table S4.1 and] using the forms specified in schedule 4 table S4.2; and
(c) giving the information from such results and assessments as may be required by the forms specified in those tables.

4.3 Notifications
4.3.1 Natural Resources Wales shall be notified as soon as reasonably practicable following detection, within the site of the regulated facility of:
(a) any malfunction, breakdown or failure of equipment or techniques, accident, or emission of a substance not controlled by an emission limit which has caused, is causing or may cause significant pollution; and
(b) any breach of a limit specified in schedule 3 table S3.1 including individual exceedances of limits which are covered by condition 3.1.2.
Any other significant adverse environmental effects, which may have been caused by the activity, shall also be notified to Natural Resources Wales as soon as reasonably practicable following detection.
4.3.2 The information provided under condition 4.3.1 shall be supported by sending the information listed in schedule 5 to this permit within the time period specified in that schedule.
4.3.3 Where Natural Resources Wales has requested in writing that it shall be notified when the operator is to undertake monitoring and/or spot sampling specified in schedule 3B/3C, the operator shall inform Natural Resources Wales when the relevant monitoring and/or spot sampling is to take place. The operator shall provide this information to Natural Resources Wales at least 14 days before the date the monitoring is to be undertaken.
4.3.4 Natural Resources Wales shall be notified within 14 days of the occurrence of the following matters, except where such disclosure is prohibited by Stock Exchange rules:
Where the operator is a registered company:
(a) any change in the operator’s trading name, registered name or registered office address; and
(b) any steps taken with a view to the operator going into administration, entering into a company voluntary arrangement or being wound up.
Where the operator is a corporate body other than a registered company:
(a) any change in the operator’s name or address; and
(b) any steps taken with a view to the dissolution of the operator.
4.3.5 Where the operator proposes to make a change in the nature of the activity by increasing the concentration of, or the addition of, or allowing the introduction of, a substance to the activity to an extent that the operator considers could have a significant adverse environmental effect on the receiving waters, and the change is not permitted by emission limits specified within schedule 3 table S3.1 or the subject of an application for approval under the EP Regulations or under the terms of this permit:
(a) Natural Resources Wales shall be notified in writing at least 14 days before the increase or addition or allowing the introduction; and
(b) the notification shall contain a description of the proposed change.
4.3.6 For the activity referenced in schedule 1, table S1.1 the operator shall inform Natural Resources Wales in writing of any change, or proposed change, to the population equivalent such as would make a material change to the application of the Regulations and shall, on request, inform the Natural Resources Wales in writing of the actual population equivalent.

4.4 Interpretation
4.4.1 In this permit the expressions listed in schedule 6 shall have the meaning given in that schedule.
4.4.2 In this permit references to reports and notifications mean written reports and notifications, except where reference is made to notification being made “as soon as reasonably practicable”, in which case it may be provided by telephone.




Schedule 1 – Operations 
	Table S1.1 Activities

	Description of activity
	Limits of specified activity

	Discharge of secondary treated sewage effluent subject to disinfection by ultra violet irradiation via Outlet 1
	N/A





Schedule 2 – Waste types, raw materials and fuels
Schedule 2 not in use.



Schedule 3 – Emissions and monitoring
	[bookmark: _Hlk94713128] Table S3.1 Point Source emissions to water (other than sewer) – emission limits and monitoring requirements

	Effluent and discharge point
	Parameter  
	Limit (including unit)
	Reference Period
	Limit of effective range
	Monitoring frequency
	Compliance Statistic

	Secondary treated sewage effluent subject to disinfection by ultra violet irradiation via Outlet 1
	Dry weather flow
	8200 m3/day


	Total daily volume
	N/A                                                                
	Continuous
	Conditions 3.1.5 applies

	
	15-minute instantaneous or averaged flow
	No limit set. Record as l/s
	15-minute
	N/A
	Continuous
	N/A

	
	ATU-BOD as O2
	50 mg/l
	Instantaneous (spot sample)
	N/A
	As specified in schedule 3B
	Look up table
(Conditions 3.1.2 and 3.1.3 apply)

	
	ATU-BOD as O2
	100 mg/l
	Instantaneous (spot sample)
	N/A
	As specified in schedule 3B
	Maximum
(Condition 3.1.3 applies)

	
	Suspended solids (measured after drying at 105°C)
	60 mg/l
	Instantaneous (spot sample)
	N/A
	As specified in schedule 3B
	Look up table
(Conditions 3.1.2 and 3.1.3 apply)

	
	Suspended solids (measured after drying at 105°C)
	250 mg/l
	Instantaneous (spot sample)
	N/A
	As specified in schedule 3B
	Maximum 
(Condition 3.1.3 applies)

	
	ATU-BOD as O2  (UWWTR)
	Minimum of 70 % removal compared to influent
	24-hour composite
	To be compliant a sample has to meet the 70% removal standard or the 25 mg/l limit not both 
	As specified in schedule 3C 
	Look up table
(Conditions 3.1.2 and 3.1.4 apply) 

	
	ATU-BOD as O2  (UWWTR)
	25 mg/l
	
	
	
	

	
	ATU-BOD as O2  (UWWTR)
	50 mg/l
	24-hour composite
	This limit does not apply if a sample has met the 70% removal standard
	As specified in schedule 3C

	Maximum
(Condition 3.1.4 applies)

	
	COD as O2 (UWWTR)
	Minimum of 75 % removal compared to influent
	24-hour composite
	To be compliant a sample has to meet the 75% removal standard or the 125 mg/l limit not both 
	As specified in schedule 3C
	Look up table
(Conditions 3.1.2 and 3.1.4 apply) 

	
	COD as O2 (UWWTR)
	125 mg/l
	
	
	
	

	
	COD as O2 (UWWTR)
	250 mg/l
	24-hour composite
	This limit does not apply if a sample has met the 75% removal standard 
	As specified in schedule 3C

	Maximum
(Condition 3.1.4 applies)




	Table S3.2 Discharge points

	Effluent Name
	Discharge Point
	Discharge point NGR
	Receiving water/Environment

	Secondary treated sewage effluent subject to disinfection by ultra violet irradiation
	Outlet 1
	SS 15540 98870
	Coastal Waters – Carmarthen Bay



	Table S3.3 UV process details and process limits

	Effluent and discharge point 
	UV source
	Dose type
	Full dose mJ/cm2 (see condition 2.3.2(b))
	50% dose mJ/cm2 (see condition 2.3.2(b))
	Effective dates
	5%ile transmittance

	Secondary treated sewage effluent subject to disinfection by ultra violet irradiation via Outlet 1
	Narrow spectrum low pressure artificial UV source with at least 85% of available UV radiation emitted in the wavelength range 250 to 260nm
	Measured applied
	24
	12
	1st Jan – 31st Dec
	45%





	[bookmark: _Hlk133940828]Table S3.4 Monitoring points

	Effluent and discharge point
	Monitoring type
	Monitoring point NGR
	Monitoring point reference

	Secondary treated sewage effluent subject to disinfection by ultra violet irradiation via Outlet 1
	Crude influent inlet sampling
	SN 11368 00958
	Crude influent

	
	UWWTR crude inlet sampling point
	SN 11375 00931
	UWWTD Crude Sewage Sampling Point

	
	Pre UV treatment monitoring
	SN 11470 00846
	Pre UV

	
	UWWTR post UV treatment monitoring
	SN 11493 00860
	Sampling Point (post UV) and UWWTD Final Effluent Sampling Point

	
	Post UV treatment monitoring
	
	

	
	Effluent sampling point
	
	

	
	Flow Monitoring
	
	



	Table S3.5 UV efficacy monitoring point requirements

	Monitoring type
	Parameters
	Monitoring frequency

	Pre UV treatment monitoring point
	No monitoring
	As specified for sanitary parameters in table 3B and 3C.

Monitoring for all parameters in table S3.5 to coincide

	UV irradiation plant inlet monitoring point
	UV transmittance at 254nm
	

	UV Irradiation channel monitoring points W4
	Instantaneous flow rate
Measured applied dose
	

	Post UV treatment monitoring point
	Esherichia Coli (E.coli)
Intestinal Enterococci
Suspended solids
	





Schedule 3A - Look up table
	Look up table

	[bookmark: _Hlt511551491]Number of samples taken in any period of 12 months
	Maximum number of samples permitted to exceed limit for given parameter

	4–7  
	 1

	8–16
	 2

	17–28 
	 3

	29–40 
	 4

	41–53  
	 5

	54–67  
	 6

	68–81  
	 7

	82–95 
	 8

	96–110 
	 9

	111–125  
	 10

	126–140  
	 11

	141–155  
	 12

	156–171  
	 13

	172–187 
	 14

	188–203  
	 15

	204–219  
	 16

	220–235  
	 17

	236–251 
	 18

	252–268 
	 19

	269–284  
	 20

	285–300  
	 21

	301–317 
	 22

	318–334  
	 23

	335–350 
	 24

	351–365 
	 25




Schedule 3B - OSM tier 3 sampling frequency
	Parameter
	‘Normal frequency’ of samples per year
	Reduced Sampling frequency after 12 consecutive months of numeric permit compliance, samples per year or pro rata over the remainder of a year
	On numeric limit failure return to normal frequency as soon as reasonably practicable, samples per 12 months1
	Out of hours samples

	Sanitary

	24
	12
	24
	For 24 samples 2 out of hours samples per annum

	Non sanitary

	12
	12
	12
	For 12 samples 1 out of hours sample per annum


1 For UV efficacy monitoring use sanitary frequency and increase following failure of UV requirements only.

Schedule 3C – Urban Waste Water Treatment Regulations sampling frequency
	Population equivalent
	Samples per year
	Reduced sampling frequency after a year without an UWWTR exceedance or failure, samples per year
	Following an UWWTR exceedance or failure return to the higher frequency in the year that follows, samples per year

	2,000 to 9,999

	12
	4
	12

	10,000 to 49,999

	12
	N/A
	N/A

	50,000 or over

	24
	N/A
	N/A




Schedule 4 – Reporting
Parameters, for which reports shall be made, in accordance with conditions of this permit, are listed below.
	Table S4.1 Reporting of monitoring data

	Parameter
	Monitoring point reference
	Reporting period
	Period begins

	Dry Weather Flow (daily flows total)
	Sampling Point (Post-UV) and UWWTD Final Effluent Sampling Point
	Annually
Report to be submitted within 2 months of the end of the calendar year
	1st January

	15-minute flow 
	Sampling Point (Post-UV) and UWWTD Final Effluent Sampling Point
	Reports to be provided to Natural Resources Wales upon request
	Upon request by Natural Resources Wales

	UWWTR – ATU-BOD as O2, COD as O2
	Sampling Point (Post-UV) and UWWTD Final Effluent Sampling Point
	Monthly
Report to be submitted within 2 months
	1st of month

	Operator Self Monitoring – ATU-BOD as O2, suspended solids (measured after drying at 105°C)
	Sampling Point (Post-UV) and UWWTD Final Effluent Sampling Point
	Quarterly
Report to be submitted within 2 months
	1st of month

	Operator Self Monitoring summary report
	Sampling Point (Post-UV) and UWWTD Final Effluent Sampling Point
	Annually
Report to be submitted within 2 months of the end of the calendar year
	1st January

	UV disinfection measurements specified by condition 3.3.9
	Sampling Point (Post-UV) and UWWTD Final Effluent Sampling Point
	Quarterly
Report to be submitted within 2 months
	1st  January, 1st  April, 1st July, 1st October

	Disinfection efficacy
Parameter required by condition 3.3.1 and table S3.5
	Sampling Point (Post-UV) and UWWTD Final Effluent Sampling Point
	Quarterly
Report to be submitted within 2 months
	1st  January, 1st  April, 1st July, 1st October

	UV disinfection performance reports
	Sampling Point (Post-UV) and UWWTD Final Effluent Sampling Point
	Reports to be provided to Natural Resources Wales upon request
Reports to be submitted within 2 months otherwise specified in writing by Natural Resources Wales
	Upon request by Natural Resources Wales





	Table S4.2 Reporting forms

	Parameter
	Reporting format

	Dry Weather Flow 
	WISKI electronic format specified by Natural Resources Wales

	15-minute flow 
	WISKI electronic format specified by Natural Resources Wales

	UWWTR – ATU-BOD as O2, COD as O2
	Electronic format specified by Natural Resources Wales


	OSM – ATU-BOD as O2, suspended solids (measured after drying at 105°C)
	Quarterly - Electronic format as agreed in writing by Natural Resources Wales. 

	Operator Self Monitoring summary report
	Annually - Summary report of compliance with the monitoring programme specified in Table 3.1 and schedule 3B in a format specified by Natural Resources Wales

	UV disinfection measurements specified by condition 3.3.9
	Form as agreed in writing by Natural Resources Wales

	Disinfection efficacy
	Form as agreed in writing by Natural Resources Wales

	UV disinfection performance reports
	Form as agreed in writing by Natural Resources Wales





Schedule 5 – Notification 
These pages outline the information that the operator must provide. 
Units of measurement used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission. Where appropriate, a comparison should be made of actual emissions and authorised emission limits.
If any information is considered commercially confidential, it should be separated from non-confidential information, supplied on a separate sheet and accompanied by an application for commercial confidentiality under the provisions of the EP Regulations.
Part A
	Permit Number
	BP0251904

	Name of operator
	Dŵr Cymru Cyfyngedig

	Location of Facility
	Tenby Wastewater Treatment Works, Gumfreston, Nr Tenby, SA70 8RA

	Time and date of the detection 
	



	(a) Notification requirements for any malfunction, breakdown or failure of equipment or techniques, accident, or emission of a substance not controlled by an emission limit which has caused, is causing or may cause significant pollution

	To be notified within 7 days of detection unless otherwise agreed in writing by Natural Resources Wales

	Date and time of the event
	

	Reference or description of the location of the event 
	

	Description of where any release into the environment took place
	

	Substances(s) potentially released/type or nature of sewage released
	

	Best estimate of the quantity or rate of release of substances and/or duration of discharge
	

	Best estimate of the environmental impact of the discharge
	

	Measures taken, or intended to be taken, to stop any emission
	

	Description of the failure or accident.
	



	(b) Notification requirements for the breach of a limit specified in schedule 3 table S3.1 including individual exceedances of limits which are covered by condition 3.1.2

	The information specified below is to be notified to Natural Resources Wales as soon as reasonably practicable following detection.

	Monitoring point reference/ source
	

	Self monitoring regime (where relevant)
	OSM/UWWTR

	Type of failure 
	e.g. LUT failure/LUT exceedance/upper tier/other


	Date of sample/event
	

	Parameter
	

	Result and units
	

	Limit and units
	


Part B – to be submitted as soon as reasonably practicable unless otherwise agreed in writing by Natural Resources Wales
	Any more accurate information on the matters for notification under Part A.
	

	Measures taken, or intended to be taken, to prevent a recurrence of the incident/breach/exceedance
	

	Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment which has been or may be caused by the emission
	



	Name*
	

	Post
	

	Signature
	

	Date
	


* authorised to sign on behalf of the operator


Schedule 6 – Interpretation 
“abnormal operating conditions” include but are not limited to, the circumstances described in Regulation 40(1) of, or paragraph 6(5) of Schedule 21 to, the Environmental Permitting Regulations 2010 (illegal discharge to sewer), unusual weather, or during a defined period where the permit authorising the permitted activity has been varied for reasons such as capital works construction.
“accident” means an accident that may result in pollution.
“annually” means once every year.
“application” means the application for this permit, together with any additional information supplied by the operator as part of the application and any response to a notice served under Schedule 5 to the EP Regulations.
“appropriate measures” for the purposes of the emission of substances not controlled by emission limits condition (condition 3.2.1) do not require the operator to undertake treatment to a level beyond that specified in schedule 1 table S1.1, or to carry out routine monitoring for substances not controlled by emission limits. 
“ATU-BOD as O2” means the biochemical oxygen demand (measured after 5 days at 20oC with nitrification suppressed by the addition of allylthiourea). 
“COD as O2” means the chemical oxygen demand (measured using the standard dichromate procedure).
“disinfection” means the use of a process designed specifically to reduce the number of viable, potentially infectious micro organisms in the effluent.
“emissions of substances not controlled by emission limits” means emissions of substances to air, water or land from the permitted activities, which are not controlled by an emission limit.
“EP Regulations” means The Environmental Permitting (England and Wales) Regulations SI 2016 No.1154 and words and expressions used in this permit which are also used in the Regulations have the same meanings as in those Regulations.
“MCERTS” means Environment Agency’s Monitoring Certification Scheme.
“minimum screen capacity flow” means the minimum flow passed through the screens to the outfall when the screen bypass operates. 
“Natural Resources Wales” means the Natural Resources Body for Wales established by article 3 of the Natural Resources Body for Wales (Establishment) Order 2012. The Natural Resources Body for Wales (Functions) Order 2013 transferred the relevant functions of the Countryside Council for Wales, and functions of the Environment Agency and the Forestry Commission in Wales to the Natural Resources Body for Wales.
“overflow” for the purposes of schedule 7, overflow means the weir or orifice or other control which directs excess flow away from the continuation sewer when the flow exceeds the overflow setting due to rainfall and/or snowmelt. 
“overflow setting” means the minimum flow passed forward to the continuation sewer when the overflow operates.
“quarter” means a calendar year quarter commencing on 1 January, 1 April, 1 July or 1 October.
“significant pollution” means a category 1 or category 2 incident indicated by the Common Incident Classification Scheme (CICS).
“unusual weather conditions” includes, but is not limited to:
· low ambient temperatures, or the freezing of mechanical equipment in the works;
· significant snow deposits;
· tidal or fluvial flooding;
· weather conditions causing unforeseen loss of power supply to the sewage treatment that could not be ameliorated by the reasonable provision and operation of standby generation facilities.
[bookmark: _Hlk13661209]
“Urban Waste Water Treatment (England and Wales) Regulations 1994(UWWTR)” means Urban Waste Water Treatment (England and Wales) Regulations 1994 SI 2841and the words and expressions used in this permit which are also used in the Regulations have the same meanings as in those Regulations.
“Abnormal operating conditions” include but are not limited to, the circumstances described in Regulation 40(1) of, or paragraph 6(5) of Schedule 21 to, the Environmental Permitting Regulations 2010 (illegal discharge to sewer), unusual weather, or during a defined period where the permit authorising the permitted activity has been varied for reasons such as capital works construction.
“year” means calendar year ending 31 December.
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