## Imp_Cond
Permit number | Site / asset name | NGR | Improvement Condition requirement | Improvement condition response
S/09/08931/R | Knighton STW SPS | SO 30061 72380 | The operator shall provide the following in writing by 2 years from date of issue of the permit - Storage provision and whether on or offline if relevant | Operational CSO card indicates that there may be chamber storage but waiting on confirmation from operational team whether that refers to the SPS or the sewage treatment works.
S/01/21276/O | Llanfair Caereinion - Bridge St CSO | SJ 10446 06627 | The operator shall provide the following in writing by 2 years from date of issue of the permit - Details of any screening | No screen present
S/01/21474/O | Llanfair Caereinion - Watergate St CSO | SJ 10155 06043 | The operator shall provide the following in writing by 2 years from date of issue of the permit - Details of any screening | No screen present
S/01/07909/O | Llanfair Caereinion Railway Station | SJ 10611 06761 | The operator shall provide the following in writing by 2 years from date of issue of the permit - Details of any screening | No screen present
| Penybontfawr | SJ 09275 24524 | The operator shall provide the following in writing by 2 years from date of issue of the permit - Details of any screening | No screen present
| Carno | SN 96494 96444 | The operator shall provide the following in writing by 2 years from date of issue of the permit - Details of any screening | No screen present
| Llanfyllin Ffordd y Cain | SJ 14403 19469 | The operator shall provide the following in writing by 2 years from date of issue of the permit - Details of any screening | No screen present
S/01/21301/O | Llanfyllin - Y Dolydd CSO | SJ 15230 18717 | The operator shall provide the following in writing by 2 years from date of issue of the permit - Details of any screening | No screen present
S/01/50116/O | Llanidloes - Berth Llwyd Farm | SN 96735 85503 | The operator shall provide the following in writing by 2 years from date of issue of the permit - Details of any screening | No screen present
S/01/07315/O | Llanidloes - Shortbridge Street | SN 95271 84575 | The operator shall provide the following in writing by 2 years from date of issue of the permit - Details of any screening | Screen present - no screen details currently available; review of screening requirement to be carried out across all CSO assets once updated NRW EPR 7.01 guidance has been issued
| Llanidloes - Longbridge South | SN 95486 84766 | The operator shall provide the following in writing by 2 years from date of issue of the permit - Details of any screening | Screen present - no screen details currently available; review of screening requirement to be carried out across all CSO assets once updated NRW EPR 7.01 guidance has been issued
| Llanidloes - Longbridge North | SN 95516 84824 | The operator shall provide the following in writing by 2 years from date of issue of the permit - Details of any screening | Screen present - no screen details currently available; review of screening requirement to be carried out across all CSO assets once updated NRW EPR 7.01 guidance has been issued
S/01/05873/O | Newtown - Dolafon Terrace | SO 11453 91667 | The operator shall provide the following in writing by 2 years from date of issue of the permit - Details of any screening | CSO has been blocked off and decommissioned
S/01/05871/O | Newtown - Dysart Terrace | SO 11568 91914 | The operator shall provide the following in writing by 2 years from date of issue of the permit - Details of any screening | Screen in chamber not in position
S/01/05872/O | Newtown - Ponthafren Longbridge | SO 10733 91848 | The operator shall provide the following in writing by 2 years from date of issue of the permit - Details of any screening | Screen present - no screen details currently available; review of screening requirement to be carried out across all CSO assets once updated NRW EPR 7.01 guidance has been issued
S/01/04428/O | Newtown - Severn St 13/14 | SO 10903 91660 | The operator shall provide the following in writing by 2 years from date of issue of the permit - Details of any screening | Screen present - no screen details currently available; review of screening requirement to be carried out across all CSO assets once updated NRW EPR 7.01 guidance has been issued
|  |  | 1) The operator shall provide the following in writing by 2 years from date of issue of the permit - Details of any screening | Screen present - no screen details currently available; review of screening requirement to be carried out across all CSO assets once updated NRW EPR 7.01 guidance has been issued
| Newtown - Shortbridge St 26 | SO 10954 91562 | 2) Improve the operation of the CSO to satisfactory status; CSO shall be constructed and operated in accordance with the design; provide calculations & evidence to confirm the CSO is designed in accordance with these conditions | The following improvements have been undertaken: - Laid one length of 225mm diameter sewer to act as diversion for flows - The new sewer will pass 52l/sec at first spill in a 5 year event (satisfies Formula A value of 49l/sec)
|  |  | 1) The operator shall provide the following in writing by 2 years from date of issue of the permit - Details of any screening | Screen present but displaced due to monitor issues
| Newtown - Shortbridge Street | SO 11002 91528 | 2) Improve the operation of the CSO to satisfactory status; CSO shall be constructed and operated in accordance with the design; provide calculations & evidence to confirm the CSO is designed in accordance with these conditions | The following improvements have been undertaken: - Laid one length of 225mm diameter sewer to act as diversion for flows - The new sewer will pass 52l/sec at first spill in a 5 year event (satisfies Formula A value of 49l/sec)
S/01/07393/O | Welshpool - Salop Road CSO | SJ 23019 07647 | The operator shall provide the following in writing by 2 years from date of issue of the permit - Details of any screening | No screen present
| Welshpool - Salop Rd/Erw Wen | SJ 23019 07647 | The operator shall provide the following in writing by 2 years from date of issue of the permit - Details of any screening | No screen present
S/01/55969/R | Welshpool STW | SJ 23519 07259 | CSO (Storm) - Once the installation of EDM is complete for activity A3, the operator shall apply for an administrative variation to incorporate the NGR for the EDM monitoring point into the permit | An application to vary the permit (as required by the improvement condition) will be submitted as part of a larger package of permitting work that we are currently pulling together - timeline to be confirmed with NRW permitting team.