Permit Reference Number:

Installation:

Operator:
Permit Reference Number: BX72821S

Installation: InBev Magor Brewery

Operator: InBev UK Ltd

Form Number: W1

Reporting of Emissions to Water (other than to Sewer) for the period from 1st September 2018 to 31st December 2018           (1st January 2018 to 31st December 2018 for metals)
	Emission

Point
	Substance /

Parameter
	Emission

Limit Value
	Result [1]
	Test

Method [2]
	Sample

Date and Times [3]
	Accreditation/

Certification [4]
	Uncertainty

[5]

	W2
	Flow
	10,000m3/day
	7045
	Continuous / cumulative – AAB flow meter
	10th March
	MCerts accredited
	+/- 1.04 %

	W2
	Flow
	126 litres/s
	60.78
	Spot – AAB flow meter
	12th  March
	MCerts accredited
	+/- 1.04 %

	W2
	pH
	5 – 9 [6]
	8.9 – 8.9
	Continuous sample 
	15th August  and 14th September
	EA approved (IP 18)
	+/- 0.05 pH

	W2
	Temperature
	30°C
	29
	Continuous sample – knick in line meter
	9th July
	EA approved (IP 18)
	+/- 1 degree C

	W2
	BOD
	200mg/l
	26
	SCA Blue Book 130
ISBN 0117522120
	18th March
	UKAS Lab 1314
	20.1%

	W2
	COD
	450mg/l
	129
	SCA Blue Book 97
ISBN 0117519154
	25th February
	UKAS Lab 1314
	5.8%

	W2
	Suspended Solids
	150mg/l
	140
	SCA Blue Book 105
ISBN 011751957X
	15th July
	UKAS Lab 1314
	19.7%

	W2
	Total cadmium & its compounds
	0.005mg/l

(as annual average)
	0.0009
	BS EN ISO 5961:1995,

BS 6068-2.21:1995
	
	UKAS Lab 1314
	7.83%

	W2
	Total chromium & its compounds
	0.015mg/l

(as annual average)
	0.00344
	BS EN ISO 11885:1998,

BS 6068-2.60:1998
	
	UKAS Lab 1314
	7.93%

	W2
	Total copper & its compounds
	0.01mg/l

(as annual average)
	0.0037
	BS EN ISO 11885:1998,

BS 6068-2.60:1998
	
	UKAS Lab 1314
	9.03%

	W2
	Total mercury & its compounds
	0.0005mg/l

(as annual average)
	0.00009
	BS EN ISO 11885:1998,

BS 6068-2.60:1998
	
	UKAS Lab 1314
	11.5%

	W2
	Total nickel & its compounds
	0.03mg/l

(as annual average)
	0.0092
	BS EN ISO 11885:1998,

BS 6068-2.60:1998
	
	UKAS Lab 1314
	8.82%

	W2
	Total zinc & its compounds
	0.07mg/l

(as annual average)
	0.0039
	BS EN ISO 11885:1998,

BS 6068-2.60:1998
	
	UKAS Lab 1314
	9.85%

	W2
	Total arsenic & its compounds
	0.025mg/l

(as annual average)
	0.0016
	BS EN 26595:1993,

BS 6068-2.1:1983, ISO 6595-1985
	
	UKAS Lab 1314
	10.04%

	W2
	Total iron & its compounds
	None (mg/l)
	0.003
	SCA Blue Book 163

ISBN 0117532444
	
	UKAS Lab 1314
	9.27%

	W2
	Total cadmium & its compounds
	9150g
	98
	BS EN ISO 5961:1995,

BS 6068-2.21:1995
	
	UKAS Lab 1314
	7.83%

	W2
	Total mercury & its compounds
	915g
	84
	BS EN ISO 11885:1998,

BS 6068-2.60:1998
	
	UKAS Lab 1314
	11.5%


Form Number: W1

[1] The result given is the maximum value (or the minimum value in the case of a limit that is expressed as a minimum) obtained during the reporting period, expressed in the same terms as the emission limit value. Where the emission limit value is expressed as a range, the result is given as the ‘minimum – maximum’ measured values.

[2] Where an internationally recognised standard test method is used the reference number is given. Where another method that has been formally agreed with the Agency is used, then the appropriate identifier is given. In other cases the principal technique is stated, e.g. colorimetry.

[3] For non-continuous measurements the date and time of the sample that produced the result is given. For continuous measurements, or flow/time proportional samples, the percentage of the process operating time covered by the monitoring is given.   

[4] The accreditation status of the equipment and/or the monitoring organisation, as appropriate, for the methods used for both sampling and analysis.

[5] The uncertainty associated with the quoted result at the 95% confidence interval, unless otherwise stated. The following uncertainties are quoted on a different basis (basis as stated) – {The basis of any other uncertainty figure needs to be stated. Where no figure is available the Agency will need to agree an appropriate uncertainty value.} 

[6] The emission limit values for {pH} are expressed as {minimum and maximum individual values}.

Signed …………Carl Rogers………………………………………………….  

Date……..15/02/19…………………..




(authorised to sign as representative of the Operator)
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