## Notes
Reference conditions
All concentrations in this spreadsheet are reported in dry air at a temperature of 273K, at a pressure of 101.3 kPa and with an oxygen content of 3% dry
Uncertainty
Concentrations in this spreadsheet are reported after having subtracted the value of the 95% confidence interval (see Section 3.6.7 of the permit):
95% confidence interval for nitrogen oxides is taken to be 20%
95% confidence interval for sulphur dioxide is taken to be 20%
95% confidence interval for dust is taken to be 30%
95% confidence interval for carbon monoxide is taken to be 10%
Normal operating conditions
The document "Power Plant Boiler Abnormal Conditions" sets out the criteria for excluding emissions monitoring data from permitting or other reporting obligations:
| Parameter | Plant | Level representing abnormal conditions
| Boiler oxygen | All boilers | >17% oxygen
| Fuel input | A51, A52A, A52B, A53 and A62 | <50% BFG by thermal input
|  | A50 (Service Boilers) | <35% BFG by thermal input

## A50 Service Boilers
|  | Concentrations in mg/m³ at reference conditions after subtracting uncertainty | [9 empty] | Daily means, excluding hours outside normal operating conditions
|  | 2023-01-01 |  |  | 2023-02-01 |  |  | 2023-03-01 |  |  | Date | Fuel mix |  |  |  |  | No. hours OTNOC | Particulate Matter concentration (mg/m³) after subtracting uncertainty |  |  |  | Sulphur dioxide concentration (mg/m³) after subtracting uncertainty |  |  |  | Oxides of nitrogen concentration (mg/m³) after subtracting uncertainty
|  | PM | SO2 | NOx | PM | SO2 | NOx | PM | SO2 | NOx |  | % BFG | % COG | % BOSg | % NG | % HFO |  | No.valid hours | Measured | Limit | Breach? | No.valid hours | Measured | Limit | Breach? | No.valid hours | Measured | Limit | Breach?
Daily means | Minimum | 1.3 | 18.4 | 33 | 1 | 14 | 32 | 0.4 | 14.6 | 40 | Jan 01 2023 | 76.05% | 22.39% | 0% | 1.56% | 0% | 0 | 24 | 1.9 | 14.2 | NO | 24 | 52.9 | 249.8 | NO | 24 | 40.7 | 325.8 | NO
| Maximum | 5.5 | 88.9 | 59 | 6 | 49.6 | 60 | 3.3 | 96.2 | 70 | Jan 02 2023 | 75.78% | 22.67% | 0% | 1.56% | 0% | 0 | 24 | 1.8 | 12 | NO | 24 | 21.3 | 228.2 | NO | 24 | 41.5 | 326.1 | NO
| No. > Limit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Jan 03 2023 | 75.46% | 22.96% | 0% | 1.58% | 0% | 0 | 24 | 1.7 | 13.9 | NO | 24 | 58 | 246.3 | NO | 24 | 40.6 | 325.8 | NO
Monthly mean |  | 2.8 | 39.7 | 45 | 1.8 | 24.1 | 43 | 1.3 | 45.8 | 53 | Jan 04 2023 | 75.27% | 23.13% | 0% | 1.6% | 0% | 0 | 24 | 3.4 | 13.7 | NO | 24 | 39 | 245.1 | NO | 24 | 35.2 | 326 | NO
Monthly mean limit |  | 12.4 | 217.4 | 287.9 | 12.8 | 213.7 | 274.5 | 12.9 | 221.4 | 287.3 | Jan 05 2023 | 75.21% | 23.18% | 0% | 1.62% | 0% | 0 | 24 | 3.2 | 12.7 | NO | 24 | 30.3 | 219 | NO | 24 | 57.3 | 298.3 | NO
[11 empty] | Jan 06 2023 | 75.29% | 23.09% | 0% | 1.62% | 0% | 0 | 24 | 1.7 | 13.7 | NO | 24 | 54.2 | 243.6 | NO | 24 | 59.1 | 323.4 | NO
[11 empty] | Jan 07 2023 | 75.45% | 22.94% | 0% | 1.61% | 0% | 0 | 24 | 1.6 | 12.7 | NO | 24 | 43.8 | 234.7 | NO | 24 | 51.4 | 325.6 | NO
[11 empty] | Jan 08 2023 | 75.63% | 22.78% | 0% | 1.6% | 0% | 0 | 24 | 2.3 | 13 | NO | 24 | 34.5 | 237.9 | NO | 24 | 47.9 | 326 | NO
[11 empty] | Jan 09 2023 | 76.04% | 22.37% | 0% | 1.59% | 0% | 0 | 24 | 3 | 12.9 | NO | 24 | 30.6 | 235.1 | NO | 24 | 49.8 | 322.8 | NO
[11 empty] | Jan 10 2023 | 76.5% | 21.92% | 0% | 1.58% | 0% | 0 | 24 | 2.8 | 17.6 | NO | 24 | 39 | 281.6 | NO | 24 | 48.4 | 321.9 | NO
[11 empty] | Jan 11 2023 | 76.72% | 21.64% | 0% | 1.64% | 0% | 0 | 24 | 2 | 12.5 | NO | 24 | 36.5 | 232.2 | NO | 24 | 46 | 325.8 | NO
[11 empty] | Jan 12 2023 | 76.89% | 21.36% | 0% | 1.75% | 0% | 11 | 24 | 3.2 | 15.1 | NO | 24 | 19.9 | 225.9 | NO | 24 | 39.4 | 269.1 | NO
[11 empty] | Jan 13 2023 | 76.97% | 21.15% | 0% | 1.88% | 0% | 0 | 24 | 3.1 | 15.2 | NO | 24 | 51.7 | 258.1 | NO | 24 | 48.2 | 322.9 | NO
[11 empty] | Jan 14 2023 | 77.1% | 21.01% | 0% | 1.9% | 0% | 0 | 24 | 3.3 | 16 | NO | 24 | 51.6 | 268.3 | NO | 24 | 38.3 | 326.9 | NO
[11 empty] | Jan 15 2023 | 77.16% | 20.84% | 0% | 2% | 0% | 0 | 24 | 3.8 | 15.6 | NO | 24 | 53 | 264.5 | NO | 24 | 43.9 | 327.1 | NO
[11 empty] | Jan 16 2023 | 83.68% | 14.21% | 0% | 2.11% | 0% | 0 | 24 | 2.9 | 13.4 | NO | 24 | 23.8 | 242.2 | NO | 24 | 42.3 | 326.6 | NO
[11 empty] | Jan 17 2023 | 96.54% | 0.98% | 0% | 2.48% | 0% | 0 | 24 | 2.8 | 12.6 | NO | 24 | 28.1 | 233.1 | NO | 24 | 40.9 | 324.8 | NO
[11 empty] | Jan 18 2023 | 96.31% | 1.24% | 0% | 2.45% | 0% | 4 | 24 | 3.4 | 14.3 | NO | 24 | 18.4 | 241.6 | NO | 24 | 46.5 | 310.2 | NO
[11 empty] | Jan 19 2023 | 96.09% | 1.5% | 0% | 2.41% | 0% | 0 | 24 | 2.9 | 14.5 | NO | 24 | 88.9 | 253 | NO | 24 | 58.8 | 326.4 | NO
[11 empty] | Jan 20 2023 | 95.8% | 1.76% | 0% | 2.44% | 0% | 0 | 23 | 5.5 | 12.6 | NO | 24 | 41.5 | 233.9 | NO | 24 | 43 | 325.7 | NO
[11 empty] | Jan 21 2023 | 95.6% | 2.01% | 0% | 2.39% | 0% | 0 | 24 | 4.6 | 13 | NO | 24 | 23.5 | 235.7 | NO | 24 | 33.5 | 322.2 | NO
[11 empty] | Jan 22 2023 | 95.42% | 2.26% | 0% | 2.32% | 0% | 0 | 24 | 3.2 | 13.6 | NO | 24 | 56.6 | 238.2 | NO | 24 | 52 | 317.1 | NO
[11 empty] | Jan 23 2023 | 95.22% | 2.51% | 0% | 2.27% | 0% | 0 | 24 | 4.5 | 14.9 | NO | 24 | 77.5 | 249.2 | NO | 24 | 58.7 | 313.6 | NO
[11 empty] | Jan 24 2023 | 95.11% | 2.76% | 0% | 2.13% | 0% | 8 | 24 | 2.6 | 18 | NO | 24 | 46.8 | 269 | NO | 24 | 45.9 | 294.2 | NO
[11 empty] | Jan 25 2023 | 95.07% | 2.95% | 0% | 1.98% | 0% | 0 | 24 | 3 | 12.1 | NO | 24 | 31.9 | 217.6 | NO | 24 | 46.4 | 306.3 | NO
[11 empty] | Jan 26 2023 | 94.95% | 3.08% | 0% | 1.97% | 0% | 0 | 24 | 2.5 | 12.8 | NO | 24 | 24.4 | 217.5 | NO | 24 | 40.6 | 293.6 | NO
[11 empty] | Jan 27 2023 | 94.83% | 3.21% | 0% | 1.97% | 0% | 0 | 24 | 2.1 | 14.9 | NO | 24 | 36.6 | 236.6 | NO | 24 | 59.1 | 291.5 | NO
[11 empty] | Jan 28 2023 | 94.7% | 3.42% | 0% | 1.89% | 0% | 0 | 24 | 1.3 | 12.2 | NO | 24 | 26.7 | 225.9 | NO | 24 | 34.7 | 318.9 | NO
[11 empty] | Jan 29 2023 | 94.43% | 3.66% | 0% | 1.9% | 0% | 0 | 24 | 1.3 | 11.1 | NO | 24 | 33 | 210.1 | NO | 24 | 39 | 310.6 | NO
[11 empty] | Jan 30 2023 | 94.26% | 3.92% | 0% | 1.81% | 0% | 0 | 24 | 2 | 11.5 | NO | 24 | 29.4 | 217.8 | NO | 24 | 38.4 | 317.8 | NO
[11 empty] | Jan 31 2023 | 94.01% | 4.18% | 0% | 1.81% | 0% | 0 | 24 | 1.7 | 11.6 | NO | 24 | 26.9 | 222.5 | NO | 24 | 43 | 324.1 | NO
[11 empty] | Feb 01 2023 | 92.53% | 5.3% | 0% | 2.17% | 0% | 0 | 24 | 1.4 | 12 | NO | 24 | 24.8 | 227.7 | NO | 24 | 38.2 | 325.4 | NO
[11 empty] | Feb 02 2023 | 92.61% | 5.23% | 0% | 2.16% | 0% | 0 | 24 | 1.6 | 11.8 | NO | 24 | 23.5 | 225.7 | NO | 24 | 36.3 | 325.7 | NO
[11 empty] | Feb 03 2023 | 92.71% | 5.15% | 0% | 2.13% | 0% | 0 | 24 | 1.6 | 11.9 | NO | 24 | 21.3 | 226.6 | NO | 24 | 36.5 | 325.5 | NO
[11 empty] | Feb 04 2023 | 92.78% | 5.08% | 0% | 2.15% | 0% | 0 | 24 | 1.8 | 11.9 | NO | 24 | 16.4 | 226.9 | NO | 24 | 36.4 | 325.8 | NO
[11 empty] | Feb 05 2023 | 92.83% | 4.99% | 0% | 2.18% | 0% | 0 | 24 | 1.4 | 12.1 | NO | 24 | 15.2 | 227.8 | NO | 24 | 32.4 | 323.3 | NO
[11 empty] | Feb 06 2023 | 92.88% | 4.95% | 0% | 2.17% | 0% | 2 | 23 | 6 | 12.1 | NO | 24 | 32.5 | 210.9 | NO | 24 | 39.9 | 293.1 | NO
[11 empty] | Feb 07 2023 | 92.86% | 4.97% | 0% | 2.17% | 0% | 0 | 24 | 2.7 | 12.7 | NO | 24 | 16.8 | 220.8 | NO | 24 | 32.6 | 301.2 | NO
[11 empty] | Feb 08 2023 | 92.82% | 5% | 0% | 2.19% | 0% | 0 | 24 | 1.9 | 12.5 | NO | 24 | 20.7 | 206.9 | NO | 24 | 38.6 | 280.7 | NO
[11 empty] | Feb 09 2023 | 92.87% | 4.96% | 0% | 2.17% | 0% | 0 | 24 | 2.3 | 13 | NO | 24 | 27.2 | 218.4 | NO | 24 | 42.8 | 292.8 | NO
[11 empty] | Feb 10 2023 | 92.96% | 4.9% | 0% | 2.14% | 0% | 0 | 24 | 2.7 | 13.2 | NO | 24 | 16 | 213.9 | NO | 24 | 31.9 | 281.4 | NO
[11 empty] | Feb 11 2023 | 93.04% | 4.84% | 0% | 2.12% | 0% | 0 | 24 | 1.7 | 13.5 | NO | 24 | 25.2 | 218.4 | NO | 24 | 47.2 | 284.1 | NO
[11 empty] | Feb 12 2023 | 93.04% | 4.85% | 0% | 2.11% | 0% | 0 | 24 | 1 | 14.2 | NO | 24 | 16.3 | 249.6 | NO | 24 | 44.7 | 326 | NO
[11 empty] | Feb 13 2023 | 92.95% | 4.85% | 0% | 2.19% | 0% | 0 | 24 | 2.4 | 14.8 | NO | 24 | 17.8 | 247.9 | NO | 24 | 40.8 | 312 | NO
[11 empty] | Feb 14 2023 | 92.85% | 4.92% | 0% | 2.23% | 0% | 0 | 24 | 2.5 | 14.3 | NO | 24 | 46.6 | 229.6 | NO | 24 | 59.6 | 288.6 | NO
[11 empty] | Feb 15 2023 | 92.78% | 5.03% | 0% | 2.2% | 0% | 0 | 24 | 1.8 | 14.5 | NO | 24 | 25.9 | 232.4 | NO | 24 | 51.6 | 291 | NO
[11 empty] | Feb 16 2023 | 92.74% | 5.13% | 0% | 2.13% | 0% | 0 | 24 | 1.2 | 14.7 | NO | 24 | 27.4 | 238.7 | NO | 24 | 47.4 | 297.6 | NO
[11 empty] | Feb 17 2023 | 92.67% | 5.26% | 0% | 2.08% | 0% | 0 | 24 | 1 | 14.8 | NO | 24 | 22.6 | 240 | NO | 24 | 50.3 | 299.2 | NO
[11 empty] | Feb 18 2023 | 92.57% | 5.38% | 0% | 2.05% | 0% | 0 | 24 | 1 | 14.9 | NO | 24 | 28.8 | 241.8 | NO | 24 | 46.9 | 300.9 | NO
[11 empty] | Feb 19 2023 | 92.43% | 5.54% | 0% | 2.03% | 0% | 0 | 24 | 1.8 | 15.4 | NO | 24 | 21.7 | 247.7 | NO | 24 | 38.9 | 300.9 | NO
[11 empty] | Feb 20 2023 | 92.33% | 5.66% | 0% | 2.01% | 0% | 0 | 24 | 1.7 | 14.9 | NO | 24 | 34.1 | 236.8 | NO | 24 | 46.1 | 292.1 | NO
[11 empty] | Feb 21 2023 | 92.2% | 5.83% | 0% | 1.97% | 0% | 0 | 24 | 1 | 14.7 | NO | 24 | 27.3 | 237 | NO | 24 | 40.1 | 295 | NO
[11 empty] | Feb 22 2023 | 92.2% | 5.9% | 0% | 1.9% | 0% | 0 | 24 | 1.3 | 15.2 | NO | 24 | 14 | 234.9 | NO | 24 | 45.1 | 283.7 | NO
[11 empty] | Feb 23 2023 | 92.16% | 5.92% | 0% | 1.91% | 0% | 0 | 24 | 1.8 | 15.1 | NO | 24 | 49.6 | 240 | NO | 24 | 48.4 | 292.8 | NO
[11 empty] | Feb 24 2023 | 92.21% | 5.9% | 0% | 1.9% | 0% | 0 | 24 | 1.7 | 15.7 | NO | 24 | 25.9 | 253.1 | NO | 24 | 44.2 | 305.3 | NO
[11 empty] | Feb 25 2023 | 92.25% | 5.89% | 0% | 1.86% | 0% | 0 | 24 | 1.6 | 16 | NO | 24 | 21.9 | 255.4 | NO | 24 | 48.5 | 304.3 | NO
[11 empty] | Feb 26 2023 | 92.21% | 5.92% | 0% | 1.88% | 0% | 0 | 24 | 1.5 | 16.2 | NO | 24 | 16.4 | 256.4 | NO | 24 | 48.2 | 302.9 | NO
[11 empty] | Feb 27 2023 | 92.17% | 5.95% | 0% | 1.88% | 0% | 0 | 24 | 1.4 | 16.4 | NO | 24 | 17.7 | 257.4 | NO | 24 | 42.6 | 301.4 | NO
[11 empty] | Feb 28 2023 | 92.14% | 5.99% | 0% | 1.87% | 0% | 0 | 24 | 1.1 | 16.7 | NO | 24 | 20.3 | 260.8 | NO | 24 | 51.5 | 302.4 | NO
[11 empty] | Mar 01 2023 | 59.24% | 28.98% | 0% | 11.79% | 0% | 0 | 24 | 1 | 16.7 | NO | 24 | 22.4 | 262.4 | NO | 24 | 45.9 | 304.4 | NO
[11 empty] | Mar 02 2023 | 59.26% | 28.97% | 0% | 11.77% | 0% | 0 | 24 | 0.9 | 16.6 | NO | 24 | 21.1 | 263 | NO | 24 | 42.6 | 307.4 | NO
[11 empty] | Mar 03 2023 | 59.33% | 28.93% | 0% | 11.74% | 0% | 0 | 24 | 2.1 | 16.9 | NO | 24 | 14.6 | 264.2 | NO | 24 | 42.1 | 305 | NO
[11 empty] | Mar 04 2023 | 59.45% | 28.87% | 0% | 11.69% | 0% | 0 | 24 | 3.3 | 15.7 | NO | 24 | 21 | 259.2 | NO | 24 | 46.2 | 316.6 | NO
[11 empty] | Mar 05 2023 | 59.53% | 28.83% | 0% | 11.64% | 0% | 0 | 24 | 1 | 12.2 | NO | 24 | 96.2 | 229 | NO | 24 | 60.8 | 324 | NO
[11 empty] | Mar 06 2023 | 59.47% | 28.86% | 0% | 11.66% | 0% | 0 | 24 | 1 | 12.2 | NO | 24 | 54.8 | 227.8 | NO | 24 | 51.1 | 321.3 | NO
[11 empty] | Mar 07 2023 | 59.62% | 28.67% | 0% | 11.71% | 0% | 0 | 24 | 1.2 | 12.7 | NO | 24 | 49.3 | 234.6 | NO | 24 | 48.2 | 326.1 | NO
[11 empty] | Mar 08 2023 | 59.9% | 28.39% | 0% | 11.71% | 0% | 0 | 24 | 1.2 | 13.5 | NO | 24 | 51.8 | 243.2 | NO | 24 | 46.5 | 326.1 | NO
[11 empty] | Mar 09 2023 | 60.39% | 27.93% | 0% | 11.68% | 0% | 0 | 24 | 1.4 | 15 | NO | 24 | 50 | 255.5 | NO | 24 | 58.6 | 321.7 | NO
[11 empty] | Mar 10 2023 | 60.78% | 27.57% | 0% | 11.65% | 0% | 0 | 24 | 2.6 | 14.2 | NO | 24 | 28.8 | 248.5 | NO | 24 | 41.6 | 324.4 | NO
[11 empty] | Mar 11 2023 | 60.93% | 27.39% | 0% | 11.68% | 0% | 0 | 24 | 1.8 | 13.8 | NO | 24 | 26.2 | 235.7 | NO | 24 | 43.2 | 308.3 | NO
[11 empty] | Mar 12 2023 | 60.9% | 27.39% | 0% | 11.71% | 0% | 0 | 24 | 2.2 | 15.6 | NO | 24 | 61.1 | 260.1 | NO | 24 | 48.4 | 319.2 | NO
[11 empty] | Mar 13 2023 | 60.66% | 27.56% | 0% | 11.78% | 0% | 0 | 24 | 2.1 | 14.5 | NO | 24 | 47.8 | 252.1 | NO | 24 | 51.2 | 325.2 | NO
[11 empty] | Mar 14 2023 | 60.39% | 27.75% | 0% | 11.86% | 0% | 0 | 24 | 1.3 | 13.9 | NO | 24 | 80.4 | 245 | NO | 24 | 55.5 | 323.3 | NO
[11 empty] | Mar 15 2023 | 60.05% | 27.99% | 0% | 11.96% | 0% | 0 | 24 | 0.9 | 14.5 | NO | 24 | 40.9 | 252.9 | NO | 24 | 52.8 | 325.8 | NO
[11 empty] | Mar 16 2023 | 59.74% | 28.22% | 0% | 12.04% | 0% | 0 | 24 | 0.4 | 16.4 | NO | 24 | 78.3 | 270.5 | NO | 24 | 60.5 | 324.3 | NO
[11 empty] | Mar 17 2023 | 59.59% | 28.46% | 0% | 11.95% | 0% | 0 | 24 | 0.8 | 17.4 | NO | 24 | 66 | 280.7 | NO | 24 | 63 | 323.7 | NO
[11 empty] | Mar 18 2023 | 59.13% | 28.95% | 0% | 11.92% | 0% | 0 | 24 | 1.2 | 14.1 | NO | 24 | 87.8 | 248 | NO | 24 | 57.3 | 324.1 | NO
[11 empty] | Mar 19 2023 | 58.53% | 30.14% | 0% | 11.33% | 0% | 0 | 24 | 0.7 | 14.5 | NO | 24 | 52.1 | 251.8 | NO | 24 | 50.5 | 324.8 | NO
[11 empty] | Mar 20 2023 | 58.04% | 30.56% | 0% | 11.4% | 0% | 0 | 24 | 1.1 | 14 | NO | 24 | 44.1 | 246.4 | NO | 24 | 51.7 | 324.1 | NO
[11 empty] | Mar 21 2023 | 58.01% | 30.67% | 0% | 11.33% | 0% | 0 | 24 | 0.6 | 12.5 | NO | 24 | 36.1 | 231 | NO | 24 | 49 | 323.8 | NO
[11 empty] | Mar 22 2023 | 57.99% | 30.77% | 0% | 11.24% | 0% | 0 | 24 | 0.6 | 11.8 | NO | 24 | 16.8 | 225 | NO | 24 | 43.7 | 324.1 | NO
[11 empty] | Mar 23 2023 | 58.13% | 30.77% | 0% | 11.1% | 0% | 0 | 24 | 1.4 | 12.4 | NO | 24 | 21.5 | 230.9 | NO | 24 | 44.3 | 324.5 | NO
[11 empty] | Mar 24 2023 | 58.22% | 30.77% | 0% | 11.01% | 0% | 0 | 24 | 0.8 | 13.4 | NO | 24 | 16.3 | 240.7 | NO | 24 | 39.7 | 324.7 | NO
[11 empty] | Mar 25 2023 | 59.17% | 30.05% | 0% | 10.78% | 0% | 0 | 24 | 0.8 | 13.8 | NO | 24 | 21.5 | 244.2 | NO | 24 | 52.2 | 323.8 | NO
[11 empty] | Mar 26 2023 | 59.61% | 29.8% | 0% | 10.59% | 0% | 0 | 24 | 1 | 13.4 | NO | 24 | 67.7 | 240 | NO | 24 | 57.7 | 323 | NO
[11 empty] | Mar 27 2023 | 59.69% | 29.76% | 0% | 10.55% | 0% | 0 | 24 | 0.9 | 12.8 | NO | 24 | 74.3 | 226.5 | NO | 24 | 68.5 | 310.2 | NO
[11 empty] | Mar 28 2023 | 59.86% | 29.66% | 0% | 10.48% | 0% | 0 | 24 | 0.9 | 13.1 | NO | 24 | 56.1 | 219.5 | NO | 24 | 69.5 | 293.1 | NO
[11 empty] | Mar 29 2023 | 59.88% | 29.66% | 0% | 10.46% | 0% | 0 | 24 | 1.5 | 13.6 | NO | 24 | 31.2 | 222.6 | NO | 24 | 70.3 | 288.5 | NO
[11 empty] | Mar 30 2023 | 59.89% | 29.67% | 0% | 10.45% | 0% | 1 | 24 | 1.6 | 13 | NO | 24 | 44.7 | 206.5 | NO | 24 | 67.2 | 272 | NO
[11 empty] | Mar 31 2023 | 59.95% | 29.63% | 0% | 10.42% | 0% | 7 | 24 | 2.5 | 14.6 | NO | 24 | 39.6 | 231.8 | NO | 24 | 49.7 | 288 | NO

## A51 Boiler 5
|  | Concentrations in mg/m³ at reference conditions after subtracting uncertainty | [9 empty] | Daily means, excluding hours outside normal operating conditions
|  | 2023-01-01 |  |  | 2023-02-01 |  |  | 2023-03-01 |  |  | Date | Fuel mix |  |  |  |  | Particulate Matter concentration (mg/m³) after subtracting uncertainty
|  | PM | SO2 | NOx | PM | SO2 | NOx | PM | SO2 | NOx |  | % BFG | % COG | % BOSg | % NG | % HFO | No.valid hours | No.hours OTNOC | Measured | Limit | Breach?
Daily means | Minimum | 0.7 | Discontinuous monitoring only |  | 0.7 | Discontinuous monitoring only |  | 0.6 | Discontinuous monitoring only |  | Jan 01 2023 | 86.45% | 12.5% | 0% | 1.05% | 0% | 0 | 24 | 0.7 | 14.5 | NO
| Maximum | 3.3 |  |  | 3.2 |  |  | 2.7 |  |  | Jan 02 2023 | 86.41% | 12.55% | 0% | 1.04% | 0% | 0 | 24 | 0.7 | 14.5 | NO
| No. > Limit | 0 |  |  | 0 |  |  | 0 |  |  | Jan 03 2023 | 88.32% | 10.65% | 0% | 1.04% | 0% | 0 | 24 | 0.7 | 14.1 | NO
Monthly mean |  | 1.1 |  |  | 1 |  |  | 1 |  |  | Jan 04 2023 | 88.96% | 10.1% | 0% | 0.94% | 0% | 0 | 24 | 0.7 | 13.9 | NO
Monthly mean limit |  | 14.1 |  |  | 10.5 |  |  | 11.8 |  |  | Jan 05 2023 | 88.76% | 10.16% | 0% | 1.08% | 0% | 0 | 24 | 0.7 | 14 | NO
[11 empty] | Jan 06 2023 | 86.49% | 12.09% | 0% | 1.42% | 0% | 0 | 24 | 0.7 | 14.7 | NO
[11 empty] | Jan 07 2023 | 86.8% | 11.92% | 0% | 1.29% | 0% | 0 | 24 | 0.7 | 14.5 | NO
[11 empty] | Jan 08 2023 | 87.21% | 11.64% | 0% | 1.15% | 0% | 0 | 24 | 0.8 | 14.4 | NO
[11 empty] | Jan 09 2023 | 87.53% | 11.44% | 0% | 1.03% | 0% | 0 | 24 | 0.8 | 14.3 | NO
[11 empty] | Jan 10 2023 | 84.72% | 13.22% | 0% | 2.06% | 0% | 0 | 24 | 1.1 | 15.1 | NO
[11 empty] | Jan 11 2023 | 86.58% | 8.83% | 0% | 4.58% | 0% | 0 | 24 | 0.9 | 13.7 | NO
[11 empty] | Jan 12 2023 | 29.67% | 0% | 0% | 41.65% | 28.7% | 15 | 24 | 2.8 | 26.5 | NO
[11 empty] | Jan 13 2023 | 61.66% | 6.84% | 0% | 13.67% | 17.8% | 0 | 24 | 3.3 | 20.4 | NO
[11 empty] | Jan 14 2023 | 67.68% | 14.59% | 0% | 1.31% | 16.4% | 0 | 24 | 0.9 | 22.3 | NO
[11 empty] | Jan 15 2023 | 66.86% | 9.85% | 0% | 5.76% | 17.5% | 0 | 24 | 1 | 21.3 | NO
[11 empty] | Jan 16 2023 | 72.84% | 8.56% | 0% | 2.74% | 15.9% | 0 | 24 | 0.9 | 20.5 | NO
[11 empty] | Jan 17 2023 | 71.87% | 9.41% | 0% | 2.76% | 16% | 0 | 24 | 1.1 | 20.7 | NO
[11 empty] | Jan 18 2023 | 70.13% | 12.22% | 0% | 8.78% | 8.9% | 0 | 24 | 1.3 | 17.8 | NO
[11 empty] | Jan 19 2023 | 69.54% | 12.85% | 0% | 16.81% | 0.8% | 0 | 24 | 1.8 | 14.1 | NO
[11 empty] | Jan 20 2023 | 86.95% | 12.13% | 0% | 0.92% | 0% | 0 | 24 | 0.9 | 14.3 | NO
[11 empty] | Jan 21 2023 | 86.03% | 12.82% | 0% | 1.14% | 0% | 0 | 24 | 0.9 | 14.6 | NO
[11 empty] | Jan 22 2023 | 83.08% | 15.4% | 0% | 1.52% | 0% | 0 | 24 | 1.1 | 15.3 | NO
[11 empty] | Jan 23 2023 | 86.22% | 12.8% | 0% | 0.97% | 0% | 0 | 24 | 0.9 | 14.5 | NO
[11 empty] | Jan 24 2023 | 74.79% | 14.79% | 0% | 10.42% | 0% | 0 | 24 | 1.1 | 14.6 | NO
[11 empty] | Jan 25 2023 | 76.27% | 9.34% | 0% | 14.39% | 0% | 0 | 24 | 2.6 | 13.6 | NO
[11 empty] | Jan 26 2023 | 78.2% | 0% | 0% | 21.8% | 0% | 0 | 24 | 0.9 | 10.7 | NO
[11 empty] | Jan 27 2023 | 78.94% | 2.9% | 0% | 18.16% | 0% | 0 | 24 | 0.9 | 11.6 | NO
[11 empty] | Jan 28 2023 | 83.6% | 8.48% | 0% | 7.92% | 0% | 0 | 24 | 1 | 15.7 | NO
[11 empty] | Jan 29 2023 | 82.02% | 1.49% | 0% | 16.48% | 0% | 0 | 24 | 0.9 | 11.4 | NO
[11 empty] | Jan 30 2023 | 83.73% | 1.35% | 0% | 14.92% | 0% | 0 | 24 | 0.8 | 11.3 | NO
[11 empty] | Jan 31 2023 | 84.32% | 0.77% | 0% | 14.91% | 0% | 0 | 24 | 0.9 | 11.2 | NO
[11 empty] | Feb 01 2023 | 83.3% | 0% | 0% | 16.7% | 0% | 0 | 24 | 0.8 | 11 | NO
[11 empty] | Feb 02 2023 | 82.95% | 0% | 0% | 17.05% | 0% | 0 | 24 | 0.7 | 11 | NO
[11 empty] | Feb 03 2023 | 78.64% | 0% | 0% | 21.36% | 0% | 0 | 24 | 0.9 | 10.9 | NO
[11 empty] | Feb 04 2023 | 82.03% | 0% | 0% | 17.97% | 0% | 0 | 24 | 0.7 | 11 | NO
[11 empty] | Feb 05 2023 | 84.9% | 0% | 0% | 15.1% | 0% | 0 | 24 | 0.7 | 11 | NO
[11 empty] | Feb 06 2023 | 83.95% | 0% | 0% | 16.05% | 0% | 0 | 24 | 0.8 | 10.9 | NO
[11 empty] | Feb 07 2023 | 82.91% | 0% | 0% | 17.09% | 0% | 0 | 24 | 0.8 | 10.8 | NO
[11 empty] | Feb 08 2023 | 86.84% | 0% | 0% | 13.16% | 0% | 0 | 24 | 1.1 | 11.3 | NO
[11 empty] | Feb 09 2023 | 91.61% | 0% | 0% | 8.39% | 0% | 0 | 24 | 1.3 | 11.5 | NO
[11 empty] | Feb 10 2023 | 82.37% | 0% | 0% | 17.63% | 0% | 0 | 24 | 2.3 | 11.1 | NO
[11 empty] | Feb 11 2023 | 86.32% | 0% | 0% | 13.68% | 0% | 0 | 24 | 0.7 | 11.1 | NO
[11 empty] | Feb 12 2023 | 87.03% | 0% | 0% | 12.97% | 0% | 0 | 24 | 0.7 | 11.1 | NO
[11 empty] | Feb 13 2023 | 84.72% | 0% | 0% | 15.28% | 0% | 0 | 24 | 1.9 | 11.1 | NO
[11 empty] | Feb 14 2023 | 86.7% | 0% | 0% | 13.3% | 0% | 0 | 24 | 0.9 | 11.3 | NO
[11 empty] | Feb 15 2023 | 93.56% | 0% | 0% | 6.44% | 0% | 0 | 24 | 0.7 | 11.6 | NO
[11 empty] | Feb 16 2023 | 93.67% | 0% | 0% | 6.33% | 0% | 0 | 24 | 0.8 | 11.6 | NO
[11 empty] | Feb 17 2023 | 94.62% | 0% | 0% | 5.38% | 0% | 0 | 24 | 0.7 | 11.5 | NO
[11 empty] | Feb 18 2023 | 94.53% | 0% | 0% | 5.47% | 0% | 0 | 24 | 0.8 | 11.5 | NO
[11 empty] | Feb 19 2023 | 93.23% | 0% | 0% | 6.77% | 0% | 0 | 24 | 0.8 | 11.6 | NO
[11 empty] | Feb 20 2023 | 87.02% | 0% | 0% | 12.98% | 0% | 2 | 23 | 3.2 | 11.3 | NO
[11 empty] | Feb 21 2023 | 87.89% | 0% | 0% | 12.11% | 0% | 0 | 24 | 1.4 | 11.4 | NO
[11 empty] | Feb 22 2023 | 87% | 0% | 0% | 13% | 0% | 0 | 24 | 1 | 11.4 | NO
[11 empty] | Feb 23 2023 | 87.81% | 0% | 0% | 12.19% | 0% | 0 | 24 | 0.9 | 11.3 | NO
[11 empty] | Feb 24 2023 | 91.54% | 0% | 0% | 8.46% | 0% | 0 | 24 | 0.9 | 11.4 | NO
[11 empty] | Feb 25 2023 | 90.29% | 0% | 0% | 9.71% | 0% | 0 | 24 | 0.8 | 11.5 | NO
[11 empty] | Feb 26 2023 | 90.43% | 0% | 0% | 9.57% | 0% | 0 | 24 | 0.9 | 11.5 | NO
[11 empty] | Feb 27 2023 | 88.83% | 5.56% | 0% | 5.62% | 0% | 0 | 24 | 1 | 12.9 | NO
[11 empty] | Feb 28 2023 | 86.14% | 12.14% | 0% | 1.72% | 0% | 0 | 24 | 0.7 | 17.1 | NO
[11 empty] | Mar 01 2023 | 81.34% | 16.64% | 0% | 2.02% | 0% | 0 | 24 | 0.9 | 16.1 | NO
[11 empty] | Mar 02 2023 | 83.21% | 14.94% | 0% | 1.85% | 0% | 0 | 24 | 1 | 15.6 | NO
[11 empty] | Mar 03 2023 | 87.51% | 10.52% | 0% | 1.97% | 0% | 0 | 24 | 1 | 14.4 | NO
[11 empty] | Mar 01 2023 | 81.34% | 16.63% | 0% | 2.03% | 0% | 0 | 24 | 0.9 | 16 | NO
[11 empty] | Mar 02 2023 | 81.55% | 16.52% | 0% | 1.93% | 0% | 0 | 24 | 1 | 16 | NO
[11 empty] | Mar 03 2023 | 86.59% | 10.81% | 0% | 2.6% | 0% | 0 | 24 | 1 | 14.6 | NO
[11 empty] | Mar 04 2023 | 90.62% | 8.3% | 0% | 1.08% | 0% | 0 | 24 | 0.7 | 13.5 | NO
[11 empty] | Mar 05 2023 | 90.24% | 7.36% | 0% | 2.4% | 0% | 0 | 24 | 0.9 | 13.3 | NO
[11 empty] | Mar 06 2023 | 88.56% | 9.11% | 0% | 2.33% | 0% | 0 | 24 | 0.7 | 13.8 | NO
[11 empty] | Mar 07 2023 | 87.81% | 11.04% | 0% | 1.14% | 0% | 0 | 24 | 0.8 | 14.2 | NO
[11 empty] | Mar 08 2023 | 87.64% | 11.18% | 0% | 1.17% | 0% | 0 | 24 | 0.9 | 14.3 | NO
[11 empty] | Mar 09 2023 | 94.71% | 0.23% | 0% | 5.06% | 0% | 0 | 24 | 1 | 11.7 | NO
[11 empty] | Mar 10 2023 | 98.38% | 0% | 0% | 1.62% | 0% | 0 | 24 | 0.9 | 12 | NO
[11 empty] | Mar 11 2023 | 89.22% | 0% | 0% | 10.78% | 0% | 0 | 24 | 1 | 11.2 | NO
[11 empty] | Mar 12 2023 | 95.01% | 2.18% | 0% | 2.81% | 0% | 0 | 24 | 0.9 | 12.1 | NO
[11 empty] | Mar 13 2023 | 88.99% | 0% | 0% | 11.01% | 0% | 0 | 24 | 1 | 11.4 | NO
[11 empty] | Mar 14 2023 | 94.52% | 0% | 0% | 5.48% | 0% | 0 | 24 | 0.9 | 11.6 | NO
[11 empty] | Mar 15 2023 | 85.03% | 5.84% | 0% | 9.13% | 0% | 0 | 24 | 1.3 | 12.8 | NO
[11 empty] | Mar 16 2023 | 98.61% | 0% | 0% | 1.39% | 0% | 0 | 24 | 0.7 | 11.8 | NO
[11 empty] | Mar 17 2023 | 95.64% | 2.86% | 0% | 1.5% | 0% | 0 | 24 | 0.6 | 12.5 | NO
[11 empty] | Mar 18 2023 | 97.94% | 0.68% | 0% | 1.38% | 0% | 0 | 24 | 0.7 | 11.9 | NO
[11 empty] | Mar 19 2023 | 98.8% | 0% | 0% | 1.2% | 0% | 0 | 24 | 0.7 | 11.7 | NO
[11 empty] | Mar 20 2023 | 98.53% | 0% | 0% | 1.47% | 0% | 0 | 24 | 0.8 | 11.7 | NO
[11 empty] | Mar 21 2023 | 98.8% | 0% | 0% | 1.2% | 0% | 0 | 24 | 0.9 | 11.8 | NO
[11 empty] | Mar 22 2023 | 98.79% | 0% | 0% | 1.21% | 0% | 0 | 24 | 0.9 | 11.8 | NO
[11 empty] | Mar 23 2023 | 97.08% | 1.61% | 0% | 1.31% | 0% | 0 | 24 | 1 | 12.1 | NO
[11 empty] | Mar 24 2023 | 98.73% | 0% | 0% | 1.27% | 0% | 0 | 24 | 0.9 | 11.8 | NO
[11 empty] | Mar 25 2023 | 92.99% | 5.21% | 0% | 1.8% | 0% | 0 | 24 | 1 | 13.2 | NO
[11 empty] | Mar 26 2023 | 98.51% | 0% | 0% | 1.49% | 0% | 0 | 24 | 0.7 | 11.9 | NO
[11 empty] | Mar 27 2023 | 96.52% | 1.68% | 0% | 1.81% | 0% | 0 | 24 | 0.9 | 12.3 | NO
[11 empty] | Mar 28 2023 | 88.95% | 9.51% | 0% | 1.54% | 0% | 0 | 24 | 1.1 | 16.9 | NO
[11 empty] | Mar 29 2023 | 85.29% | 8.12% | 0% | 6.58% | 0% | 0 | 24 | 2.3 | 13.6 | NO
[11 empty] | Mar 30 2023 | 80.49% | 14.64% | 0% | 4.88% | 0% | 0 | 24 | 1.1 | 14.6 | NO
[11 empty] | Mar 31 2023 | 82.86% | 10.31% | 0% | 6.83% | 0% | 0 | 24 | 2.7 | 13.7 | NO
[11 empty] | 0 | 84.56% | 11.42% | 0% | 4.022% | 0% | 24 | 0 | 1.0763 | 13.9727 | NO

## A52A Boiler 6
|  | Concentrations in mg/m³ at reference conditions after subtracting uncertainty | [9 empty] | Daily means, excluding hours outside normal operating conditions
|  | 2023-01-01 |  |  | 2023-02-01 |  |  | 2023-03-01 |  |  | Date | Fuel mix |  |  |  |  | No. hours OTNOC | Particulate Matter concentration (mg/m³) after subtracting uncertainty |  |  |  | Sulphur dioxide concentration (mg/m³) after subtracting uncertainty |  |  |  | Oxides of nitrogen concentration (mg/m³) after subtracting uncertainty
|  | PM | SO2 | NOx | PM | SO2 | NOx | PM | SO2 | NOx |  | % BFG | % COG | % BOSg | % NG | % HFO |  | No.valid hours | Measured | Limit | Breach? | No.valid hours | Measured | Limit | Breach? | No.valid hours | Measured | Limit | Breach?
Daily means | Minimum | 1.4 | 30.7 | 41 | 1.5 | 32 | 38 | 0.3 | 42.3 | 42 | Jan 01 2023 | 73.4% | 12.3% | 10.84% | 3.46% | 0% | 0 | 24 | 1.4 | 15.9 | NO | 24 | 58.4 | 240.7 | NO | 24 | 51 | 322.3 | NO
| Maximum | 4.8 | 100 | 176 | 4.3 | 64.8 | 116 | 5.8 | 74.8 | 246 | Jan 02 2023 | 72.91% | 9.66% | 15.33% | 2.1% | 0% | 0 | 24 | 1.6 | 16.4 | NO | 24 | 50.3 | 237.5 | NO | 24 | 53.3 | 325.4 | NO
| No. > Limit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Jan 03 2023 | 74.13% | 8.87% | 15.14% | 1.87% | 0% | 0 | 24 | 1.6 | 16.2 | NO | 24 | 46.7 | 236 | NO | 24 | 45.5 | 325.9 | NO
Monthly mean |  | 2 | 47.5 | 62 | 1.9 | 44.8 | 63 | 1.3 | 59.4 | 79 | Jan 04 2023 | 77.32% | 9.49% | 11.28% | 1.91% | 0% | 0 | 24 | 1.6 | 15.5 | NO | 24 | 56.6 | 237.3 | NO | 24 | 51.6 | 325.8 | NO
Monthly mean limit |  | 13.2 | 192.6 | 270.8 | 11.9 | 174.6 | 261.1 | 13.3 | 198.4 | 276.2 | Jan 05 2023 | 72.51% | 11.72% | 5.42% | 10.34% | 0% | 0 | 24 | 1.6 | 14.1 | NO | 24 | 54.8 | 226.4 | NO | 24 | 57 | 306.6 | NO
[11 empty] | Jan 06 2023 | 77.99% | 12.41% | 1.15% | 8.45% | 0% | 0 | 24 | 1.6 | 13.5 | NO | 24 | 55.8 | 231.9 | NO | 24 | 54.9 | 311.3 | NO
[11 empty] | Jan 07 2023 | 78.18% | 11.17% | 7.35% | 3.3% | 0% | 0 | 24 | 1.6 | 14.9 | NO | 24 | 61.3 | 238.7 | NO | 24 | 47.6 | 322.7 | NO
[11 empty] | Jan 08 2023 | 68.14% | 8.68% | 18.94% | 4.24% | 0% | 1 | 24 | 1.9 | 16.7 | NO | 24 | 47.7 | 230.9 | NO | 24 | 63.2 | 319.7 | NO
[11 empty] | Jan 09 2023 | 65.16% | 12.33% | 8.16% | 14.14% | 0.2% | 0 | 24 | 1.7 | 14.7 | NO | 24 | 47 | 221.4 | NO | 24 | 83 | 298.4 | NO
[11 empty] | Jan 10 2023 | 52.2% | 15.4% | 14.12% | 18.28% | 0% | 13 | 24 | 1.8 | 16.2 | NO | 24 | 50.5 | 219.7 | NO | 24 | 87.9 | 287.2 | NO
[11 empty] | Jan 11 2023 | 72.99% | 8.2% | 9.68% | 9.13% | 0% | 0 | 24 | 1.8 | 14.5 | NO | 24 | 63 | 222.1 | NO | 24 | 47.5 | 310.3 | NO
[11 empty] | Jan 12 2023 | 25.8% | 4.4% | 2.51% | 29.24% | 38% | 16 | 24 | 4.8 | 17.1 | NO | 24 | 100 | 197.3 | NO | 24 | 176.4 | 222.4 | NO
[11 empty] | Jan 13 2023 | 58.51% | 4.7% | 6.89% | 28.8% | 1.1% | 5 | 24 | 1.7 | 12.1 | NO | 24 | 43.1 | 178.7 | NO | 24 | 49.5 | 265.3 | NO
[11 empty] | Jan 14 2023 | 74.08% | 6.67% | 7.46% | 11.79% | 0% | 0 | 24 | 1.6 | 13.4 | NO | 24 | 47.2 | 213.2 | NO | 24 | 52 | 303.9 | NO
[11 empty] | Jan 15 2023 | 71.21% | 7.51% | 13.48% | 7.79% | 0% | 1 | 24 | 1.7 | 15.1 | NO | 24 | 49.3 | 222.1 | NO | 24 | 54.5 | 312.5 | NO
[11 empty] | Jan 16 2023 | 68.49% | 8.46% | 16.08% | 6.97% | 0% | 0 | 24 | 1.9 | 16.1 | NO | 24 | 51.4 | 226.4 | NO | 24 | 40.9 | 315.3 | NO
[11 empty] | Jan 17 2023 | 72.86% | 7.4% | 11.75% | 7.98% | 0% | 0 | 24 | 1.8 | 14.8 | NO | 24 | 42.2 | 222.2 | NO | 24 | 43.2 | 312.8 | NO
[11 empty] | Jan 18 2023 | 54.82% | 7.25% | 8.85% | 25.15% | 3.9% | 9 | 24 | 2.9 | 13.8 | NO | 24 | 44.5 | 192.7 | NO | 24 | 101.2 | 270.4 | NO
[11 empty] | Jan 19 2023 | 56.39% | 7.38% | 17.06% | 15.9% | 3.3% | 6 | 24 | 2.2 | 16.1 | NO | 24 | 34.4 | 209.1 | NO | 24 | 55.3 | 292.1 | NO
[11 empty] | Jan 20 2023 | 64.24% | 4.22% | 15.59% | 15.94% | 0% | 0 | 24 | 1.9 | 14.5 | NO | 24 | 46.2 | 200.9 | NO | 24 | 50.1 | 295.3 | NO
[11 empty] | Jan 21 2023 | 64.46% | 5.9% | 15.91% | 13.73% | 0% | 0 | 24 | 2 | 15.1 | NO | 24 | 45.4 | 208.7 | NO | 24 | 49.5 | 300.1 | NO
[11 empty] | Jan 22 2023 | 64.75% | 8.39% | 13.74% | 13.13% | 0% | 0 | 24 | 2.2 | 15.1 | NO | 24 | 40.1 | 214.5 | NO | 24 | 68.2 | 300.9 | NO
[11 empty] | Jan 23 2023 | 71.39% | 5.81% | 1.43% | 21.36% | 0% | 0 | 24 | 2 | 12.4 | NO | 24 | 43.9 | 198.9 | NO | 24 | 57.6 | 290.9 | NO
[11 empty] | Jan 24 2023 | 57.16% | 1.68% | 6.89% | 25.12% | 9.1% | 7 | 24 | 3.3 | 13 | NO | 24 | 33.9 | 182.5 | NO | 24 | 66.5 | 264.6 | NO
[11 empty] | Jan 25 2023 | 57.49% | 3.13% | 10.22% | 25.43% | 3.7% | 4 | 24 | 2.1 | 13.2 | NO | 24 | 38.1 | 182.9 | NO | 24 | 54.6 | 270.3 | NO
[11 empty] | Jan 26 2023 | 67.02% | 2.45% | 7.64% | 22.89% | 0% | 0 | 24 | 1.8 | 11.9 | NO | 24 | 36.6 | 183.7 | NO | 24 | 69.7 | 279.4 | NO
[11 empty] | Jan 27 2023 | 66.96% | 3.46% | 9.43% | 20.15% | 0% | 0 | 24 | 1.8 | 12.8 | NO | 24 | 30.7 | 191.5 | NO | 24 | 75.9 | 286.2 | NO
[11 empty] | Jan 28 2023 | 72.02% | 3.64% | 11.49% | 12.84% | 0% | 0 | 24 | 1.8 | 13.6 | NO | 24 | 36.9 | 205 | NO | 24 | 56.2 | 301.9 | NO
[11 empty] | Jan 29 2023 | 72.66% | 2.14% | 11.03% | 14.17% | 0% | 0 | 24 | 1.7 | 13.1 | NO | 24 | 36.3 | 198.9 | NO | 24 | 52.5 | 298.8 | NO
[11 empty] | Jan 30 2023 | 69.21% | 2.05% | 14.55% | 14.19% | 0% | 0 | 24 | 1.6 | 13.9 | NO | 24 | 35.6 | 198.8 | NO | 24 | 56.9 | 298.8 | NO
[11 empty] | Jan 31 2023 | 65.92% | 2.67% | 15.99% | 15.41% | 0% | 0 | 24 | 1.6 | 14.2 | NO | 24 | 44.7 | 197.7 | NO | 24 | 48.3 | 295.5 | NO
[11 empty] | Feb 01 2023 | 74.31% | 0.53% | 6.84% | 18.32% | 0% | 0 | 24 | 1.5 | 11.6 | NO | 24 | 35.5 | 187.9 | NO | 24 | 52.1 | 289.7 | NO
[11 empty] | Feb 02 2023 | 75.44% | 0.91% | 8.61% | 15.03% | 0% | 0 | 24 | 1.5 | 12.3 | NO | 24 | 41 | 194.7 | NO | 24 | 48.8 | 297 | NO
[11 empty] | Feb 03 2023 | 69.65% | 0.87% | 14.79% | 14.69% | 0% | 0 | 24 | 1.5 | 13.6 | NO | 24 | 42 | 195.2 | NO | 24 | 52.2 | 297.7 | NO
[11 empty] | Feb 04 2023 | 70.03% | 0.39% | 13.19% | 16.39% | 0% | 0 | 24 | 1.6 | 13.1 | NO | 24 | 38.2 | 191.1 | NO | 24 | 50.3 | 294 | NO
[11 empty] | Feb 05 2023 | 68.59% | 0.82% | 15.66% | 14.93% | 0% | 0 | 24 | 1.5 | 13.8 | NO | 24 | 35.4 | 194.7 | NO | 24 | 49.5 | 297.1 | NO
[11 empty] | Feb 06 2023 | 66.38% | 1.22% | 12.23% | 20.17% | 0% | 0 | 24 | 1.7 | 12.9 | NO | 24 | 37.8 | 186.4 | NO | 24 | 46.7 | 286.1 | NO
[11 empty] | Feb 07 2023 | 63.33% | 1.58% | 18.06% | 17.03% | 0% | 1 | 24 | 1.8 | 14.4 | NO | 24 | 42.3 | 192.6 | NO | 24 | 44.4 | 292.5 | NO
[11 empty] | Feb 08 2023 | 60.78% | 1.95% | 12.49% | 24.78% | 0% | 0 | 24 | 1.9 | 12.9 | NO | 24 | 43.3 | 179.5 | NO | 24 | 63.9 | 275.8 | NO
[11 empty] | Feb 09 2023 | 68.65% | 0.05% | 6.16% | 25.14% | 0% | 0 | 24 | 1.8 | 11 | NO | 24 | 32 | 174.6 | NO | 24 | 57.1 | 274.9 | NO
[11 empty] | Feb 10 2023 | 60.94% | 0.12% | 3.31% | 33% | 2.6% | 2 | 24 | 2.8 | 10.2 | NO | 23 | 41.3 | 160.8 | NO | 23 | 83 | 252.9 | NO
[11 empty] | Feb 11 2023 | 67.41% | 0.17% | 18.68% | 13.74% | 0% | 0 | 24 | 1.6 | 14.4 | NO | 23 | 50.6 | 195.4 | NO | 23 | 37.5 | 299.8 | NO
[11 empty] | Feb 12 2023 | 66.76% | 0.59% | 16.78% | 15.87% | 0% | 0 | 24 | 1.6 | 14 | NO | 24 | 58.5 | 192.5 | NO | 24 | 41.2 | 295.1 | NO
[11 empty] | Feb 13 2023 | 56.22% | 0.37% | 15.23% | 23.48% | 4.7% | 4 | 24 | 3 | 13.7 | NO | 24 | 52 | 179.5 | NO | 24 | 68.6 | 270.8 | NO
[11 empty] | Feb 14 2023 | 62.65% | 0.37% | 7.1% | 29.87% | 0% | 2 | 24 | 1.8 | 10.9 | NO | 24 | 50.9 | 166.2 | NO | 24 | 56.4 | 263.7 | NO
[11 empty] | Feb 15 2023 | 68.58% | 1.11% | 7.77% | 22.54% | 0% | 0 | 24 | 1.6 | 11.7 | NO | 24 | 42 | 181.3 | NO | 24 | 53.8 | 280.2 | NO
[11 empty] | Feb 16 2023 | 64.95% | 2.02% | 12.48% | 20.55% | 0% | 0 | 24 | 1.6 | 13.1 | NO | 24 | 43.3 | 187.1 | NO | 24 | 53.3 | 284.7 | NO
[11 empty] | Feb 17 2023 | 67.05% | 2.17% | 13.27% | 17.5% | 0% | 0 | 24 | 1.7 | 13.4 | NO | 24 | 39.5 | 193 | NO | 24 | 51.1 | 291.5 | NO
[11 empty] | Feb 18 2023 | 57.63% | 2.11% | 16.71% | 23.54% | 0% | 1 | 24 | 1.8 | 13.9 | NO | 24 | 42.6 | 182 | NO | 24 | 51.6 | 278.3 | NO
[11 empty] | Feb 19 2023 | 63.73% | 2.93% | 13.73% | 19.6% | 0% | 0 | 24 | 2 | 13.5 | NO | 24 | 36.1 | 190.4 | NO | 24 | 69.8 | 286.3 | NO
[11 empty] | Feb 20 2023 | 61.91% | 1.44% | 14.07% | 22.58% | 0% | 4 | 24 | 1.8 | 12.9 | NO | 24 | 45.7 | 180.5 | NO | 24 | 73.9 | 278.2 | NO
[11 empty] | Feb 21 2023 | 69.95% | 1.79% | 7.75% | 20.51% | 0% | 0 | 24 | 1.5 | 12 | NO | 24 | 47.2 | 186.6 | NO | 24 | 63.6 | 284.8 | NO
[11 empty] | Feb 22 2023 | 56.53% | 1.9% | 1.88% | 29.22% | 10.5% | 7 | 24 | 2.8 | 12 | NO | 24 | 50.9 | 176.7 | NO | 24 | 111 | 254.6 | NO
[11 empty] | Feb 23 2023 | 66.65% | 9.69% | 1.53% | 19.66% | 2.5% | 3 | 24 | 2.5 | 12.7 | NO | 24 | 42.7 | 200.4 | NO | 24 | 90.9 | 282.8 | NO
[11 empty] | Feb 24 2023 | 64.73% | 12.43% | 8.88% | 7.72% | 6.2% | 4 | 24 | 4.3 | 16 | NO | 24 | 64.8 | 236.8 | NO | 24 | 116.3 | 303.3 | NO
[11 empty] | Feb 25 2023 | 75.63% | 8.41% | 10.7% | 5.26% | 0% | 0 | 24 | 1.6 | 14.9 | NO | 24 | 47.4 | 228.8 | NO | 24 | 68.8 | 318.3 | NO
[11 empty] | Feb 26 2023 | 77.38% | 6.42% | 10.2% | 6.01% | 0% | 0 | 24 | 1.6 | 14.3 | NO | 24 | 40 | 223.1 | NO | 24 | 64 | 316.6 | NO
[11 empty] | Feb 27 2023 | 65.52% | 6.35% | 6.27% | 21.86% | 0% | 2 | 24 | 1.7 | 12.7 | NO | 24 | 57 | 195.4 | NO | 24 | 57.2 | 282.9 | NO
[11 empty] | Feb 28 2023 | 76.26% | 8.46% | 7.73% | 7.55% | 0% | 0 | 24 | 1.7 | 14.1 | NO | 24 | 54.6 | 224.4 | NO | 24 | 81.8 | 312.8 | NO
[11 empty] | Mar 01 2023 | 72.98% | 10.98% | 6.69% | 9.36% | 0% | 0 | 24 | 1.7 | 14.3 | NO | 24 | 43.2 | 227.1 | NO | 24 | 74.5 | 309.2 | NO
[11 empty] | Mar 02 2023 | 66.55% | 9.76% | 4.08% | 19.61% | 0% | 0 | 24 | 1.9 | 12.9 | NO | 24 | 60.1 | 206 | NO | 24 | 80.9 | 286.4 | NO
[11 empty] | Mar 03 2023 | 66.17% | 8.38% | 14.99% | 10.46% | 0% | 0 | 24 | 1.8 | 15.5 | NO | 24 | 51.9 | 219.3 | NO | 24 | 56.6 | 306.8 | NO
[11 empty] | Mar 04 2023 | 73.17% | 6.85% | 12.6% | 7.37% | 0% | 0 | 24 | 1.6 | 14.9 | NO | 24 | 55 | 221.9 | NO | 24 | 55.7 | 313.9 | NO
[11 empty] | Mar 05 2023 | 70.39% | 2.51% | 17.86% | 9.24% | 0% | 0 | 24 | 1.5 | 15 | NO | 24 | 46 | 208.8 | NO | 24 | 51.8 | 309.7 | NO
[11 empty] | Mar 06 2023 | 69.82% | 0.94% | 17.63% | 11.61% | 0% | 0 | 24 | 1.5 | 14.4 | NO | 24 | 47.9 | 201 | NO | 24 | 48 | 304.4 | NO
[11 empty] | Mar 07 2023 | 71.31% | 4.64% | 16.27% | 7.78% | 0% | 0 | 24 | 1.6 | 15.2 | NO | 24 | 57.3 | 216.3 | NO | 24 | 41.9 | 313 | NO
[11 empty] | Mar 08 2023 | 68.04% | 5.66% | 18.14% | 8.15% | 0% | 0 | 24 | 1.7 | 15.8 | NO | 24 | 54.4 | 218 | NO | 24 | 44.7 | 312.3 | NO
[11 empty] | Mar 09 2023 | 70.53% | 1.63% | 11.21% | 16.62% | 0% | 0 | 24 | 1.7 | 12.9 | NO | 24 | 42.3 | 193.5 | NO | 24 | 45.6 | 293.5 | NO
[11 empty] | Mar 10 2023 | 64.58% | 6.3% | 20.11% | 9% | 0% | 0 | 24 | 1.8 | 16.4 | NO | 24 | 45.6 | 218.1 | NO | 8 | 61 | 310.5 | NO
[11 empty] | Mar 11 2023 | 53.49% | 7.01% | 8.13% | 20.4% | 11% | 7 | 24 | 5.8 | 15.1 | NO | 24 | 62.7 | 207.3 | NO | 8 | 100.3 | 272.9 | NO
[11 empty] | Mar 12 2023 | 74.85% | 5.59% | 12.42% | 7.14% | 0% | 0 | 24 | 1.5 | 14.6 | NO | 24 | 54.8 | 219.5 | NO | 24 | 51.8 | 314.4 | NO
[11 empty] | Mar 13 2023 | 65.56% | 6.56% | 11.81% | 16.04% | 0% | 4 | 24 | 1.6 | 14 | NO | 24 | 73.2 | 204.9 | NO | 24 | 75.3 | 293.2 | NO
[11 empty] | Mar 14 2023 | 70.31% | 5.45% | 11.03% | 13.2% | 0% | 0 | 24 | 1.7 | 13.9 | NO | 24 | 68 | 208.1 | NO | 24 | 62.5 | 300.8 | NO
[11 empty] | Mar 15 2023 | 73.09% | 6.86% | 10.2% | 9.85% | 0% | 2 | 24 | 1.6 | 14.1 | NO | 24 | 71.2 | 216.7 | NO | 24 | 49.3 | 307.6 | NO
[11 empty] | Mar 16 2023 | 80.19% | 8.33% | 8.87% | 2.61% | 0% | 0 | 24 | 1.5 | 14.6 | NO | 24 | 67.9 | 233.6 | NO | 24 | 42.9 | 324.3 | NO
[11 empty] | Mar 17 2023 | 71.52% | 7.57% | 13% | 6.99% | 0.9% | 0 | 24 | 2 | 15.2 | NO | 24 | 62.6 | 224.3 | NO | 24 | 64.6 | 313.2 | NO
[11 empty] | Mar 18 2023 | 77.54% | 7.69% | 11.65% | 3.12% | 0% | 0 | 24 | 1.5 | 15.1 | NO | 24 | 59.6 | 231.2 | NO | 24 | 48.9 | 323.1 | NO
[11 empty] | Mar 19 2023 | 70.35% | 9.61% | 13.25% | 6.8% | 0% | 0 | 24 | 1.6 | 15.6 | NO | 24 | 74.8 | 228.6 | NO | 24 | 55.2 | 314.7 | NO
[11 empty] | Mar 20 2023 | 78.22% | 8.13% | 8.91% | 4.74% | 0% | 0 | 24 | 1.5 | 14.5 | NO | 24 | 66.6 | 229.1 | NO | 24 | 52.9 | 319.4 | NO
[11 empty] | Mar 21 2023 | 79.66% | 8.69% | 6.32% | 5.33% | 0% | 0 | 24 | 0.9 | 14 | NO | 24 | 72.3 | 229.5 | NO | 24 | 47.4 | 318.3 | NO
[11 empty] | Mar 22 2023 | 78.97% | 9.37% | 7.1% | 4.56% | 0% | 0 | 24 | 0.3 | 14.4 | NO | 24 | 46.1 | 232.4 | NO | 24 | 48.2 | 320 | NO
[11 empty] | Mar 23 2023 | 79.77% | 11.28% | 5.01% | 3.94% | 0% | 0 | 24 | 0.3 | 14.4 | NO | 24 | 62.4 | 236 | NO | 24 | 70.5 | 321.4 | NO
[11 empty] | Mar 24 2023 | 80.34% | 9.76% | 7.99% | 1.91% | 0% | 0 | 24 | 0.3 | 14.8 | NO | 24 | 63.8 | 237.9 | NO | 24 | 80.8 | 325.8 | NO
[11 empty] | Mar 25 2023 | 76.86% | 11.17% | 7.77% | 4.2% | 0% | 0 | 24 | 0.3 | 14.9 | NO | 24 | 74.1 | 237 | NO | 24 | 99.2 | 320.8 | NO
[11 empty] | Mar 26 2023 | 76.86% | 10.45% | 9.26% | 3.43% | 0% | 0 | 24 | 0.4 | 15.1 | NO | 24 | 70.1 | 236.7 | NO | 24 | 102 | 322.4 | NO
[11 empty] | Mar 27 2023 | 66.23% | 11.54% | 14.06% | 8.17% | 0% | 3 | 24 | 0.4 | 16 | NO | 24 | 52.1 | 229.6 | NO | 24 | 131.9 | 310.8 | NO
[11 empty] | Mar 28 2023 | 33.3% | 24.99% | 12.12% | 29.59% | 0% | 16 | 24 | 0.5 | 16.7 | NO | 24 | 70.4 | 219.5 | NO | 15 | 246.1 | 258.4 | NO
[11 empty] | Mar 29 2023 | 47.5% | 17.56% | 7.39% | 27.55% | 0% | 10 | 24 | 0.3 | 14.6 | NO | 24 | 62.4 | 207.4 | NO | 23 | 145.9 | 266.5 | NO
[11 empty] | Mar 30 2023 | 51.75% | 14.37% | 6.93% | 26.94% | 0% | 10 | 24 | 0.3 | 13.8 | NO | 24 | 50.7 | 201 | NO | 24 | 149.1 | 267.7 | NO
[11 empty] | Mar 31 2023 | 46.45% | 6.19% | 14.32% | 33.03% | 0% | 9 | 24 | 0.4 | 12 | NO | 24 | 50.7 | 164.9 | NO | 20 | 171.6 | 244 | NO

## A52B Boiler 7
|  | Concentrations in mg/m³ at reference conditions after subtracting uncertainty | [9 empty] | Daily means, excluding hours outside normal operating conditions
|  | 2023-01-01 |  |  | 2023-02-01 |  |  | 2023-03-01 |  |  | Date | Fuel mix |  |  |  |  | No. hours OTNOC | Particulate Matter concentration (mg/m³) after subtracting uncertainty |  |  |  | Sulphur dioxide concentration (mg/m³) after subtracting uncertainty |  |  |  | Oxides of nitrogen concentration (mg/m³) after subtracting uncertainty
|  | PM | SO2 | NOx | PM | SO2 | NOx | PM | SO2 | NOx |  | % BFG | % COG | % BOSg | % NG | % HFO |  | No.valid hours | Measured | Limit | Breach? | No.valid hours | Measured | Limit | Breach? | No.valid hours | Measured | Limit | Breach?
Daily means | Minimum | 1.4 | 2.8 | 1 | 1.5 | 4 | 1 | 1.5 | -0.1 | 1 | Jan 01 2023 | 75.59% | 12.87% | 8% | 3.55% | 0% | 0 | 24 | 1.4 | 16.4 | NO | 24 | 10.7 | 248.4 | NO | 24 | 15.7 | 332.5 | NO
| Maximum | 5.8 | 27.7 | 95 | 3.3 | 15.8 | 17 | 2.6 | 23.5 | 64 | Jan 02 2023 | 77.49% | 9.05% | 11.42% | 2.04% | 0% | 0 | 24 | 1.7 | 16.6 | NO | 24 | 5.1 | 244.1 | NO | 24 | 10.3 | 337.4 | NO
| No. > Limit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Jan 03 2023 | 75.21% | 11.9% | 11.06% | 1.83% | 0% | 0 | 24 | 1.5 | 17.1 | NO | 24 | 5.2 | 250.6 | NO | 24 | 15.6 | 337.6 | NO
Monthly mean |  | 2.1 | 8.4 | 15 | 1.9 | 6.9 | 8 | 1.8 | 9.2 | 13 | Jan 04 2023 | 79.49% | 9.86% | 8.74% | 1.91% | 0% | 0 | 24 | 1.5 | 15.8 | NO | 24 | 5.4 | 243.8 | NO | 24 | 14.3 | 334.4 | NO
Monthly mean limit |  | 13.4 | 198.7 | 280.4 | 12.6 | 185.7 | 270.6 | 13.3 | 197.8 | 280.6 | Jan 05 2023 | 71.26% | 13.9% | 3.4% | 11.43% | 0% | 0 | 24 | 1.5 | 14.8 | NO | 24 | 9.3 | 234.1 | NO | 24 | 22.3 | 311.4 | NO
[11 empty] | Jan 06 2023 | 80.02% | 12.71% | -0.41% | 7.68% | 0% | 0 | 24 | 1.5 | 13.8 | NO | 24 | 11.5 | 237.5 | NO | 24 | 13.9 | 318.3 | NO
[11 empty] | Jan 07 2023 | 80.36% | 11.85% | 4.57% | 3.21% | 0% | 0 | 24 | 1.5 | 15.2 | NO | 24 | 10 | 245.8 | NO | 24 | 13.9 | 331 | NO
[11 empty] | Jan 08 2023 | 73.86% | 9.72% | 13.35% | 3.07% | 0% | 0 | 24 | 1.7 | 17.2 | NO | 24 | 7.5 | 244.6 | NO | 24 | 12.2 | 335.9 | NO
[11 empty] | Jan 09 2023 | 67.3% | 14.03% | 6.42% | 11.55% | 0.7% | 2 | 24 | 2.3 | 15.9 | NO | 24 | 10.5 | 236.6 | NO | 24 | 20.6 | 313.1 | NO
[11 empty] | Jan 10 2023 | 60.33% | 13.86% | 11.38% | 12.76% | 1.7% | 6 | 24 | 1.9 | 17.2 | NO | 24 | 6.1 | 236 | NO | 24 | 22.7 | 311.4 | NO
[11 empty] | Jan 11 2023 | 73.45% | 9.1% | 7.19% | 10.26% | 0% | 0 | 24 | 1.6 | 14.9 | NO | 24 | 13.1 | 227.8 | NO | 24 | 11.6 | 316.4 | NO
[11 empty] | Jan 12 2023 | 24.24% | 8.73% | 6.08% | 30.04% | 30.9% | 18 | 24 | 4.1 | 14.2 | NO | 24 | 27.7 | 195.9 | NO | 24 | 95 | 260.2 | NO
[11 empty] | Jan 13 2023 | 58.25% | 2.81% | 5.56% | 31.55% | 1.8% | 5 | 24 | 2.1 | 12.2 | NO | 24 | 12.8 | 175.2 | NO | 24 | 17.5 | 266.5 | NO
[11 empty] | Jan 14 2023 | 76.82% | 6.25% | 5.39% | 11.53% | 0% | 0 | 24 | 1.7 | 13.6 | NO | 24 | 4.8 | 217.1 | NO | 24 | 9.1 | 311.4 | NO
[11 empty] | Jan 15 2023 | 73.16% | 7.46% | 11.77% | 7.61% | 0% | 1 | 24 | 2.2 | 15.7 | NO | 24 | 3.9 | 228.5 | NO | 24 | 11.1 | 322.3 | NO
[11 empty] | Jan 16 2023 | 62.19% | 7.19% | 24.3% | 6.31% | 0% | 3 | 23 | 5.8 | 15.1 | NO | 24 | 10.5 | 208.3 | NO | 24 | 7.5 | 295.5 | NO
[11 empty] | Jan 17 2023 | 75.61% | 7.38% | 8.7% | 8.32% | 0% | 0 | 24 | 2.3 | 15.1 | NO | 24 | 4 | 227.6 | NO | 24 | 12.3 | 321.4 | NO
[11 empty] | Jan 18 2023 | 59.6% | 7.4% | 6.51% | 19.21% | 7.3% | 7 | 24 | 2.4 | 15 | NO | 24 | 6.5 | 210.8 | NO | 24 | 25 | 288.3 | NO
[11 empty] | Jan 19 2023 | 66.4% | 7.86% | 10.98% | 13.39% | 1.4% | 0 | 24 | 2.3 | 15.8 | NO | 24 | 15.2 | 221.8 | NO | 24 | 1 | 311 | NO
[11 empty] | Jan 20 2023 | 71.53% | 7.37% | 12% | 9.09% | 0% | 0 | 24 | 2.4 | 16 | NO | 24 | 5.8 | 227.6 | NO | 24 | 10.1 | 322.1 | NO
[11 empty] | Jan 21 2023 | 66.61% | 7.93% | 13.81% | 11.66% | 0% | 0 | 24 | 2.3 | 16.3 | NO | 24 | 8.8 | 224.2 | NO | 24 | 10.3 | 315.9 | NO
[11 empty] | Jan 22 2023 | 68.08% | 3.18% | 11.66% | 17.08% | 0% | 0 | 24 | 2 | 14.4 | NO | 24 | 7.8 | 203.2 | NO | 24 | 7.9 | 303.3 | NO
[11 empty] | Jan 23 2023 | 70.61% | 4.19% | 8.73% | 16.47% | 0% | 0 | 24 | 2.2 | 12.1 | NO | 24 | 7.8 | 193.6 | NO | 24 | 8.6 | 285.1 | NO
[11 empty] | Jan 24 2023 | 58.37% | 2.97% | 8.27% | 28.04% | 2.3% | 8 | 24 | 2.4 | 12.7 | NO | 24 | 2.8 | 179.5 | NO | 24 | 14.2 | 270.3 | NO
[11 empty] | Jan 25 2023 | 65.32% | 3.79% | 8.01% | 22.89% | 0% | 0 | 24 | 2.2 | 12.9 | NO | 24 | 7.5 | 190.7 | NO | 24 | 7.4 | 285.3 | NO
[11 empty] | Jan 26 2023 | 67.09% | 3.13% | 6% | 23.79% | 0% | 2 | 24 | 2.1 | 12.1 | NO | 24 | 9.1 | 186.4 | NO | 24 | 11.7 | 281.8 | NO
[11 empty] | Jan 27 2023 | 71.22% | 3.35% | 6.63% | 18.81% | 0% | 0 | 24 | 2.1 | 12.9 | NO | 24 | 7.4 | 198 | NO | 24 | 9 | 295.6 | NO
[11 empty] | Jan 28 2023 | 74.32% | 4.41% | 8.94% | 12.32% | 0% | 0 | 24 | 2.1 | 14.3 | NO | 24 | 6.9 | 214.3 | NO | 24 | 6.2 | 312.9 | NO
[11 empty] | Jan 29 2023 | 75.98% | 2.64% | 8.66% | 12.72% | 0% | 0 | 24 | 1.8 | 13.7 | NO | 24 | 4.7 | 208.5 | NO | 24 | 4.9 | 310.7 | NO
[11 empty] | Jan 30 2023 | 74.91% | 2.61% | 10.32% | 12.16% | 0% | 0 | 24 | 1.8 | 14.2 | NO | 24 | 5.9 | 210.3 | NO | 24 | 6.3 | 313.2 | NO
[11 empty] | Jan 31 2023 | 71.7% | 2.4% | 11% | 14.9% | 0% | 0 | 24 | 1.7 | 14.2 | NO | 24 | 6 | 205.6 | NO | 24 | 5 | 308.3 | NO
[11 empty] | Feb 01 2023 | 78.03% | 0.51% | 5.02% | 16.44% | 0% | 0 | 24 | 1.6 | 12 | NO | 24 | 6.8 | 196 | NO | 24 | 5 | 300.9 | NO
[11 empty] | Feb 02 2023 | 80.49% | 0.86% | 5.89% | 12.76% | 0% | 0 | 24 | 1.6 | 12.5 | NO | 24 | 5.1 | 203.7 | NO | 24 | 5 | 309.4 | NO
[11 empty] | Feb 03 2023 | 74.39% | 1.5% | 11.66% | 12.45% | 0% | 0 | 24 | 1.5 | 14.2 | NO | 24 | 5.2 | 207.4 | NO | 24 | 5 | 312.7 | NO
[11 empty] | Feb 04 2023 | 72.9% | 2.9% | 10.13% | 14.07% | 0% | 0 | 24 | 1.5 | 14 | NO | 24 | 5.1 | 206.7 | NO | 24 | 4.9 | 307.9 | NO
[11 empty] | Feb 05 2023 | 69.23% | 5.74% | 12.52% | 12.51% | 0% | 0 | 24 | 1.7 | 15.4 | NO | 24 | 5.2 | 217.1 | NO | 24 | 4.7 | 313.2 | NO
[11 empty] | Feb 06 2023 | 66.42% | 8.26% | 9.06% | 16.26% | 0% | 0 | 24 | 1.8 | 14.9 | NO | 24 | 4.8 | 215.4 | NO | 24 | 4.8 | 304.3 | NO
[11 empty] | Feb 07 2023 | 62.16% | 10.46% | 12.65% | 14.72% | 0% | 0 | 24 | 2 | 16.4 | NO | 24 | 5.6 | 223.8 | NO | 24 | 4.9 | 308.9 | NO
[11 empty] | Feb 08 2023 | 55.24% | 12.53% | 9.61% | 22.62% | 0% | 5 | 24 | 2.4 | 15.3 | NO | 24 | 4 | 210.4 | NO | 24 | 9.1 | 287.5 | NO
[11 empty] | Feb 09 2023 | 67.43% | 0.41% | 5.55% | 26.61% | 0% | 0 | 24 | 1.9 | 11.3 | NO | 24 | 4.8 | 175.9 | NO | 24 | 4.8 | 276.4 | NO
[11 empty] | Feb 10 2023 | 58.54% | 1.12% | 4.17% | 33.86% | 2.3% | 7 | 24 | 3 | 10.3 | NO | 24 | 6.8 | 159.9 | NO | 24 | 9.1 | 249.8 | NO
[11 empty] | Feb 11 2023 | 70.47% | 1.49% | 15.73% | 12.31% | 0% | 0 | 24 | 1.5 | 15.2 | NO | 24 | 6.2 | 208.5 | NO | 24 | 4.8 | 314.2 | NO
[11 empty] | Feb 12 2023 | 70.85% | 2.37% | 13.81% | 12.97% | 0% | 0 | 24 | 1.5 | 14.9 | NO | 24 | 5.5 | 208.9 | NO | 24 | 4.7 | 312.3 | NO
[11 empty] | Feb 13 2023 | 55.01% | 2.93% | 15.23% | 23.11% | 3.7% | 10 | 24 | 3.3 | 14.7 | NO | 24 | 9 | 189.8 | NO | 24 | 17.2 | 279.5 | NO
[11 empty] | Feb 14 2023 | 65.52% | 3.34% | 7.05% | 24.09% | 0% | 0 | 24 | 1.6 | 12.4 | NO | 24 | 15.8 | 186.8 | NO | 24 | 15.1 | 282 | NO
[11 empty] | Feb 15 2023 | 72.31% | 4.28% | 6.22% | 17.19% | 0% | 0 | 24 | 1.5 | 13 | NO | 24 | 6 | 202.6 | NO | 24 | 9.6 | 298.9 | NO
[11 empty] | Feb 16 2023 | 70.31% | 5.49% | 8.61% | 15.59% | 0% | 0 | 24 | 1.5 | 14.2 | NO | 24 | 6.8 | 209.9 | NO | 24 | 8.2 | 304.8 | NO
[11 empty] | Feb 17 2023 | 71.4% | 5.97% | 10.14% | 12.49% | 0% | 0 | 24 | 1.5 | 14.9 | NO | 24 | 6.8 | 217.2 | NO | 24 | 9.8 | 312.7 | NO
[11 empty] | Feb 18 2023 | 64.24% | 6.01% | 11.42% | 18.33% | 0% | 0 | 24 | 1.5 | 14.9 | NO | 24 | 6.2 | 207.3 | NO | 24 | 5.3 | 300.7 | NO
[11 empty] | Feb 19 2023 | 67.9% | 7.63% | 9.32% | 15.15% | 0% | 0 | 24 | 1.9 | 14.5 | NO | 24 | 6.5 | 213.8 | NO | 24 | 1 | 303.4 | NO
[11 empty] | Feb 20 2023 | 58.61% | 7.75% | 12.91% | 20.72% | 0% | 7 | 24 | 1.6 | 14.8 | NO | 24 | 9.9 | 202.6 | NO | 24 | 11.6 | 289 | NO
[11 empty] | Feb 21 2023 | 62.71% | 9.11% | 6.55% | 21.64% | 0% | 1 | 24 | 1.7 | 13.9 | NO | 24 | 9.7 | 205.4 | NO | 24 | 7.2 | 289.3 | NO
[11 empty] | Feb 22 2023 | 59.15% | 10.2% | 1.09% | 29.27% | 0.3% | 2 | 24 | 2.1 | 12.5 | NO | 24 | 5.9 | 193.5 | NO | 24 | 11 | 271.4 | NO
[11 empty] | Feb 23 2023 | 61.24% | 8.46% | 8.64% | 21.66% | 0% | 6 | 24 | 2 | 12.6 | NO | 24 | 8.5 | 193.1 | NO | 24 | 9.7 | 273.1 | NO
[11 empty] | Feb 24 2023 | 72.57% | 9.47% | 6.68% | 11.28% | 0% | 0 | 24 | 1.9 | 14.9 | NO | 24 | 8 | 227 | NO | 24 | 5.6 | 315.1 | NO
[11 empty] | Feb 25 2023 | 77.57% | 8.92% | 7.42% | 6.09% | 0% | 0 | 24 | 1.9 | 14.8 | NO | 24 | 7.2 | 231.9 | NO | 24 | 10.7 | 322 | NO
[11 empty] | Feb 26 2023 | 76.33% | 4.67% | 7.96% | 11.04% | 0% | 0 | 24 | 2.1 | 13.6 | NO | 24 | 8.5 | 212.8 | NO | 24 | 8.9 | 310.2 | NO
[11 empty] | Feb 27 2023 | 70.48% | 4.9% | 3.7% | 20.91% | 0% | 0 | 24 | 2 | 12.5 | NO | 24 | 7.3 | 197.6 | NO | 24 | 5.3 | 291 | NO
[11 empty] | Feb 28 2023 | 72.34% | 2.43% | 6.47% | 18.77% | 0% | 0 | 24 | 2.3 | 12.5 | NO | 24 | 5.8 | 195 | NO | 24 | 11.2 | 294.7 | NO
[11 empty] | Mar 01 2023 | 72.14% | 1.78% | 6.09% | 19.98% | 0% | 0 | 24 | 1.9 | 12.3 | NO | 24 | 7.5 | 192 | NO | 24 | 12.2 | 292.7 | NO
[11 empty] | Mar 02 2023 | 58.68% | 2.49% | 3.03% | 35.79% | 0% | 3 | 24 | 2.2 | 10.4 | NO | 24 | 6 | 161.3 | NO | 24 | 17.4 | 252.5 | NO
[11 empty] | Mar 03 2023 | 57.83% | 1.36% | 14.82% | 25.99% | 0% | 0 | 24 | 2.2 | 13.1 | NO | 24 | 5.3 | 175.8 | NO | 24 | 7 | 272.9 | NO
[11 empty] | Mar 04 2023 | 68.46% | 2.84% | 12.16% | 16.53% | 0% | 0 | 24 | 2 | 13.6 | NO | 24 | 5.5 | 197.9 | NO | 24 | 9.1 | 296.1 | NO
[11 empty] | Mar 05 2023 | 65.4% | 1.74% | 17.76% | 15.1% | 0% | 0 | 24 | 2.1 | 14.9 | NO | 24 | 6.9 | 199.4 | NO | 24 | 6.2 | 301.2 | NO
[11 empty] | Mar 06 2023 | 69.04% | 1.69% | 17% | 12.27% | 0% | 0 | 24 | 1.9 | 15.1 | NO | 24 | 7.1 | 206.1 | NO | 24 | 7.2 | 310 | NO
[11 empty] | Mar 07 2023 | 76.49% | 1.69% | 12.62% | 9.2% | 0% | 0 | 24 | 2 | 14.8 | NO | 24 | 8.8 | 214.5 | NO | 24 | 6.6 | 320.9 | NO
[11 empty] | Mar 08 2023 | 74.07% | 1.34% | 13.04% | 11.54% | 0% | 0 | 24 | 2.1 | 14.8 | NO | 24 | 9.8 | 210.3 | NO | 24 | 4.5 | 317.1 | NO
[11 empty] | Mar 09 2023 | 74.57% | 2.16% | 8.63% | 14.64% | 0% | 0 | 24 | 1.9 | 13.5 | NO | 24 | 7 | 204.5 | NO | 24 | 5 | 307.3 | NO
[11 empty] | Mar 10 2023 | 71.92% | 3.33% | 12.77% | 11.98% | 0% | 0 | 24 | 2 | 15.2 | NO | 24 | 8.3 | 214.1 | NO | 24 | 6.4 | 316.3 | NO
[11 empty] | Mar 11 2023 | [5 empty] | 19 | 16 |  |  | NO | 23 |  |  | NO | 24 |  |  | NO
[11 empty] | Mar 12 2023 | [5 empty] | 24 | 19 |  |  | NO | 24 |  |  | NO | 24 |  |  | NO
[11 empty] | Mar 13 2023 | 65.79% | 1.86% | 11.98% | 20.38% | 0% | 2 | 24 | 2.6 | 13.2 | NO | 24 | 23.5 | 188.9 | NO | 24 | 12.4 | 288.4 | NO
[11 empty] | Mar 14 2023 | 73.16% | 5.35% | 8.65% | 12.84% | 0% | 0 | 24 | 1.9 | 14.3 | NO | 24 | 16.1 | 214.6 | NO | 24 | 12.8 | 310.6 | NO
[11 empty] | Mar 15 2023 | 72.48% | 9.3% | 8.55% | 9.67% | 0% | 2 | 24 | 2 | 15.1 | NO | 24 | 7.6 | 227.5 | NO | 24 | 15.9 | 315.9 | NO
[11 empty] | Mar 16 2023 | 81.16% | 10.19% | 6.08% | 2.56% | 0% | 0 | 24 | 1.6 | 15.2 | NO | 24 | 4.9 | 243 | NO | 24 | 7.5 | 332.2 | NO
[11 empty] | Mar 17 2023 | 68.1% | 9.17% | 11.98% | 10.76% | 0% | 0 | 24 | 1.6 | 15.6 | NO | 24 | 4.4 | 224.2 | NO | 24 | 13.7 | 311.8 | NO
[11 empty] | Mar 18 2023 | 80.39% | 8.9% | 7.83% | 2.88% | 0% | 0 | 24 | 1.6 | 15.4 | NO | 24 | 2.4 | 240.3 | NO | 24 | 5.7 | 332.6 | NO
[11 empty] | Mar 19 2023 | 78.35% | 8.61% | 7.88% | 5.16% | 0% | 0 | 24 | 1.8 | 15.3 | NO | 24 | 1.5 | 235.7 | NO | 24 | 1 | 327.9 | NO
[11 empty] | Mar 20 2023 | 79.92% | 9.69% | 6.2% | 4.19% | 0% | 0 | 24 | 1.6 | 15.1 | NO | 24 | 0.3 | 239 | NO | 24 | 6.1 | 328.7 | NO
[11 empty] | Mar 21 2023 | 80.97% | 9.32% | 4.3% | 5.41% | 0% | 0 | 24 | 1.5 | 14.4 | NO | 24 | -0.1 | 235.7 | NO | 24 | 5 | 325.6 | NO
[11 empty] | Mar 22 2023 | 80.02% | 10.6% | 4.76% | 4.62% | 0% | 0 | 24 | 1.5 | 15 | NO | 24 | 7.1 | 240.4 | NO | 24 | 12.1 | 328.1 | NO
[11 empty] | Mar 23 2023 | 79.08% | 10.58% | 7.12% | 3.22% | 0% | 0 | 24 | 1.6 | 14.5 | NO | 24 | 10.5 | 236.3 | NO | 24 | 15.5 | 320.8 | NO
[11 empty] | Mar 24 2023 | 81.36% | 10.68% | 6.03% | 1.92% | 0% | 0 | 24 | 1.6 | 15.3 | NO | 24 | 12.9 | 245.1 | NO | 24 | 13.5 | 333.5 | NO
[11 empty] | Mar 25 2023 | 79.79% | 11.48% | 5.34% | 3.4% | 0% | 0 | 24 | 1.6 | 15.1 | NO | 24 | 13.4 | 243.2 | NO | 24 | 14.7 | 328.4 | NO
[11 empty] | Mar 26 2023 | 81.04% | 9.63% | 5.98% | 3.36% | 0% | 0 | 24 | 1.7 | 15 | NO | 24 | 12.3 | 240.2 | NO | 24 | 11.6 | 330.2 | NO
[11 empty] | Mar 27 2023 | 72.74% | 8.41% | 10.5% | 8.36% | 0% | 3 | 24 | 1.8 | 15.5 | NO | 24 | 11.7 | 229 | NO | 24 | 14.8 | 320.2 | NO
[11 empty] | Mar 28 2023 | 75.22% | 9% | 10.05% | 5.72% | 0% | 0 | 24 | 1.8 | 18 | NO | 24 | 12 | 250.2 | NO | 24 | 11.3 | 348.2 | NO
[11 empty] | Mar 29 2023 | 33.09% | 16.69% | 7.97% | 30.04% | 12.2% | 18 | 24 | 1.9 | 16.3 | NO | 24 | 11.2 | 206.7 | NO | 24 | 63.8 | 250.3 | NO
[11 empty] | Mar 30 2023 | 45.29% | 10.96% | 6.63% | 30.5% | 6.6% | 12 | 24 | 1.8 | 14.5 | NO | 24 | 21.1 | 194.3 | NO | 24 | 32.1 | 258 | NO
[11 empty] | Mar 31 2023 | 45.78% | 8.64% | 5.49% | 27.25% | 12.8% | 8 | 24 | 1.9 | 14.8 | NO | 24 | 21.4 | 199.9 | NO | 24 | 37.1 | 273 | NO

## A53 Mitchell Boiler
|  | Concentrations in mg/m³ at reference conditions after subtracting uncertainty | [9 empty] | Daily means, excluding hours outside normal operating conditions
|  | 2023-01-01 |  |  | 2023-02-01 |  |  | 2023-03-01 |  |  | Date | Fuel mix |  |  |  |  | Particulate Matter concentration (mg/m³) after subtracting uncertainty
|  | PM | SO2 | NOx | PM | SO2 | NOx | PM | SO2 | NOx |  | % BFG | % COG | % BOSg | % NG | % HFO | No.valid hours | No.hours OTNOC | Measured | Limit | Breach?
Daily means | Minimum | 0 | Discontinuous monitoring only |  | 0 | Discontinuous monitoring only |  | 0 | Discontinuous monitoring only |  | Jan 01 2023 | 95.48% | 3.88% | 0% | 0.64% | 0% | 0 | 24 | 1.4 | 10.8 | NO
| Maximum | 2.7 |  |  | 3 |  |  | 2.5 |  |  | Jan 02 2023 | 97.18% | 2.28% | 0% | 0.54% | 0% | 0 | 24 | 1.4 | 10.4 | NO
| No. > Limit | 0 |  |  | 0 |  |  | 0 |  |  | Jan 03 2023 | 96.13% | 2.74% | 0% | 1.12% | 0% | 0 | 24 | 1.6 | 10.5 | NO
Monthly mean |  | 1.7 |  |  | 1.6 |  |  | 1.6 |  |  | Jan 04 2023 | 97.73% | 1.75% | 0% | 0.51% | 0% | 0 | 24 | 1.4 | 10.3 | NO
Monthly mean limit |  | 9.6 |  |  | 8.9 |  |  | 10.4 |  |  | Jan 05 2023 | 92.45% | 6.08% | 0% | 1.46% | 0% | 0 | 24 | 1.8 | 11.3 | NO
[11 empty] | Jan 06 2023 | 93.49% | 5.76% | 0% | 0.74% | 0% | 0 | 24 | 1.3 | 11.1 | NO
[11 empty] | Jan 07 2023 | 95.46% | 4.02% | 0% | 0.52% | 0% | 0 | 24 | 1.5 | 10.8 | NO
[11 empty] | Jan 08 2023 | 95.59% | 3.92% | 0% | 0.49% | 0% | 0 | 24 | 0 | 10.8 | NO
[11 empty] | Jan 09 2023 | 93.92% | 5.11% | 0% | 0.96% | 0% | 0 | 24 | 1.6 | 11 | NO
[11 empty] | Jan 10 2023 | 93.89% | 5.2% | 0% | 0.91% | 0% | 0 | 24 | 1.5 | 11.1 | NO
[11 empty] | Jan 11 2023 | 95.86% | 2.23% | 0% | 1.91% | 0% | 0 | 24 | 1.6 | 10.4 | NO
[11 empty] | Jan 12 2023 | 52.12% | 2.19% | 0% | 43.54% | 2.1% | 13 | 24 | 2.7 | 10.3 | NO
[11 empty] | Jan 13 2023 | 84.45% | 7.01% | 0% | 8.54% | 0% | 0 | 24 | 1.9 | 11 | NO
[11 empty] | Jan 14 2023 | 94.82% | 4.05% | 0% | 1.13% | 0% | 0 | 24 | 1.7 | 10.9 | NO
[11 empty] | Jan 15 2023 | 96.15% | 3.06% | 0% | 0.79% | 0% | 0 | 24 | 1.9 | 10.6 | NO
[11 empty] | Jan 16 2023 | 96.53% | 2.88% | 0% | 0.59% | 0% | 0 | 24 | 1.6 | 10.5 | NO
[11 empty] | Jan 17 2023 | 96.26% | 3.1% | 0% | 0.64% | 0% | 0 | 24 | 1.7 | 10.6 | NO
[11 empty] | Jan 18 2023 | 86.25% | 3.34% | 0% | 6.69% | 3.7% | 1 | 24 | 2.4 | 11.9 | NO
[11 empty] | Jan 19 2023 | 92.47% | 4.06% | 0% | 3.46% | 0% | 0 | 24 | 1.6 | 10.6 | NO
[11 empty] | Jan 20 2023 | 95.8% | 3.73% | 0% | 0.47% | 0% | 0 | 24 | 1.6 | 10.7 | NO
[11 empty] | Jan 21 2023 | 97.57% | 1.91% | 0% | 0.52% | 0% | 0 | 24 | 1.6 | 10.4 | NO
[11 empty] | Jan 22 2023 | 96.75% | 2.65% | 0% | 0.6% | 0% | 0 | 24 | 1.7 | 10.5 | NO
[11 empty] | Jan 23 2023 | 96.02% | 3.35% | 0% | 0.63% | 0% | 0 | 24 | 1.5 | 10.7 | NO
[11 empty] | Jan 24 2023 | 88.68% | 3.41% | 0% | 7.9% | 0% | 0 | 24 | 1.9 | 10.3 | NO
[11 empty] | Jan 25 2023 | 83.74% | 2.98% | 0% | 13.27% | 0% | 0 | 24 | 2.1 | 10 | NO
[11 empty] | Jan 26 2023 | 92.76% | 1.83% | 0% | 5.41% | 0% | 0 | 24 | 2 | 10.2 | NO
[11 empty] | Jan 27 2023 | 93.64% | 1.15% | 0% | 5.21% | 0% | 0 | 24 | 2 | 10 | NO
[11 empty] | Jan 28 2023 | 98.06% | 1.43% | 0% | 0.51% | 0% | 0 | 24 | 1.8 | 10.3 | NO
[11 empty] | Jan 29 2023 | 96.82% | 2.19% | 0% | 0.99% | 0% | 0 | 24 | 1.9 | 10.4 | NO
[11 empty] | Jan 30 2023 | 92.49% | 0.92% | 0% | 6.58% | 0% | 0 | 24 | 1.7 | 9.9 | NO
[11 empty] | Jan 31 2023 | 92.66% | 0.17% | 0% | 7.17% | 0% | 0 | 24 | 2 | 9.7 | NO
[11 empty] | Feb 01 2023 | 93.82% | 0.05% | 0% | 6.13% | 0% | 0 | 24 | 1.4 | 9.7 | NO
[11 empty] | Feb 02 2023 | 93.85% | 0.1% | 0% | 6.04% | 0% | 0 | 24 | 1.5 | 9.7 | NO
[11 empty] | Feb 03 2023 | 93.32% | 0.17% | 0% | 6.5% | 0% | 0 | 24 | 1.4 | 9.7 | NO
[11 empty] | Feb 04 2023 | 92.75% | 0.25% | 0% | 7% | 0% | 0 | 24 | 1.3 | 9.7 | NO
[11 empty] | Feb 05 2023 | 92.23% | 0.31% | 0% | 7.46% | 0% | 0 | 24 | 1.3 | 9.7 | NO
[11 empty] | Feb 06 2023 | 90.73% | 0.39% | 0% | 8.88% | 0% | 0 | 24 | 2 | 9.6 | NO
[11 empty] | Feb 07 2023 | 92.65% | 0.38% | 0% | 6.97% | 0% | 0 | 24 | 1.3 | 9.7 | NO
[11 empty] | Feb 08 2023 | 90.6% | 0.67% | 0% | 8.73% | 0% | 0 | 24 | 0 | 9.7 | NO
[11 empty] | Feb 09 2023 | 91.07% | 0.7% | 0% | 8.23% | 0% | 0 | 24 | 1.6 | 9.7 | NO
[11 empty] | Feb 10 2023 | 84.32% | 0.86% | 0% | 14.81% | 0% | 0 | 24 | 2.1 | 9.5 | NO
[11 empty] | Feb 11 2023 | 92.85% | 0.57% | 0% | 6.57% | 0% | 0 | 24 | 1.2 | 9.8 | NO
[11 empty] | Feb 12 2023 | 92.84% | 0.63% | 0% | 6.52% | 0% | 0 | 24 | 1.4 | 9.8 | NO
[11 empty] | Feb 13 2023 | 88.07% | 0.91% | 0% | 11.02% | 0% | 0 | 24 | 2.2 | 9.7 | NO
[11 empty] | Feb 14 2023 | 91.56% | 0.96% | 0% | 7.47% | 0% | 0 | 24 | 1.3 | 9.8 | NO
[11 empty] | Feb 15 2023 | 93.05% | 0.9% | 0% | 6.05% | 0% | 0 | 24 | 1.4 | 9.9 | NO
[11 empty] | Feb 16 2023 | 92.37% | 1.11% | 0% | 6.52% | 0% | 0 | 24 | 1.4 | 9.9 | NO
[11 empty] | Feb 17 2023 | 94.12% | 0.93% | 0% | 4.95% | 0% | 0 | 24 | 1.4 | 9.9 | NO
[11 empty] | Feb 18 2023 | 94.71% | 0.9% | 0% | 4.38% | 0% | 0 | 24 | 1.5 | 10 | NO
[11 empty] | Feb 19 2023 | 92.88% | 1.19% | 0% | 5.92% | 0% | 0 | 24 | 1.6 | 10 | NO
[11 empty] | Feb 20 2023 | 91.66% | 1.41% | 0% | 6.92% | 0% | 0 | 24 | 2 | 10 | NO
[11 empty] | Feb 21 2023 | 86.54% | 2.23% | 0% | 11.22% | 0% | 0 | 24 | 2 | 9.9 | NO
[11 empty] | Feb 22 2023 | 86.29% | 2.32% | 0% | 11.38% | 0% | 0 | 24 | 1.7 | 9.9 | NO
[11 empty] | Feb 23 2023 | 89.27% | 1.79% | 0% | 8.94% | 0% | 0 | 24 | 1.6 | 9.9 | NO
[11 empty] | Feb 24 2023 | 93.01% | 1.46% | 0% | 5.52% | 0% | 0 | 24 | 1.3 | 10 | NO
[11 empty] | Feb 25 2023 | 93.33% | 1.39% | 0% | 5.27% | 0% | 0 | 24 | 1.6 | 10 | NO
[11 empty] | Feb 26 2023 | 93.08% | 1.51% | 0% | 5.4% | 0% | 0 | 24 | 1.8 | 10 | NO
[11 empty] | Feb 27 2023 | 90.19% | 1.8% | 0% | 8.01% | 0% | 0 | 24 | 3 | 10 | NO
[11 empty] | Feb 28 2023 | 91.5% | 1.7% | 0% | 6.8% | 0% | 0 | 24 | 1.6 | 10 | NO
[11 empty] | Mar 01 2023 | 90.65% | 2.86% | 0% | 6.49% | 0% | 0 | 24 | 1.5 | 10.3 | NO
[11 empty] | Mar 02 2023 | 95.86% | 3.36% | 0% | 0.77% | 0% | 0 | 24 | 1.8 | 10.6 | NO
[11 empty] | Mar 03 2023 | 95.76% | 3.61% | 0% | 0.63% | 0% | 0 | 24 | 1.7 | 10.7 | NO
[11 empty] | Mar 04 2023 | 96.24% | 2.97% | 0% | 0.79% | 0% | 0 | 24 | 1.4 | 10.6 | NO
[11 empty] | Mar 05 2023 | 96.83% | 1.89% | 0% | 1.28% | 0% | 0 | 24 | 1.4 | 10.3 | NO
[11 empty] | Mar 06 2023 | 95.75% | 3.19% | 0% | 1.06% | 0% | 0 | 24 | 1.6 | 10.6 | NO
[11 empty] | Mar 07 2023 | 95.57% | 3.94% | 0% | 0.48% | 0% | 0 | 24 | 1.6 | 10.8 | NO
[11 empty] | Mar 08 2023 | 96.05% | 3.49% | 0% | 0.46% | 0% | 0 | 24 | 0 | 10.7 | NO
[11 empty] | Mar 09 2023 | 94.88% | 2.16% | 0% | 2.95% | 0% | 0 | 24 | 1.4 | 10.3 | NO
[11 empty] | Mar 10 2023 | 95.92% | 2.59% | 0% | 1.49% | 0% | 0 | 24 | 1.6 | 10.5 | NO
[11 empty] | Mar 11 2023 | 88.45% | 6.5% | 0% | 5.05% | 0% | 0 | 24 | 1.6 | 11.1 | NO
[11 empty] | Mar 12 2023 | 93.19% | 4.82% | 0% | 1.98% | 0% | 0 | 24 | 1.3 | 10.9 | NO
[11 empty] | Mar 13 2023 | 96.11% | 3.36% | 0% | 0.52% | 0% | 0 | 24 | 1.5 | 10.7 | NO
[11 empty] | Mar 14 2023 | 95.54% | 0.92% | 0% | 3.53% | 0% | 0 | 24 | 2 | 10.7 | NO
[11 empty] | Mar 15 2023 | 81.59% | 13.79% | 0% | 4.56% | 0.1% | 2 | 24 | 1.7 | 13.7 | NO
[11 empty] | Mar 16 2023 | 59.31% | 28.04% | 0% | 12.5% | 0.1% | 5 | 24 | 1.5 | 15.4 | NO
[11 empty] | Mar 17 2023 | 92.01% | 6.87% | 0% | 1.11% | 0% | 0 | 24 | 2 | 11.4 | NO
[11 empty] | Mar 18 2023 | 94.96% | 4.25% | 0% | 0.79% | 0% | 0 | 24 | 1.6 | 10.9 | NO
[11 empty] | Mar 19 2023 | 94.77% | 4.46% | 0% | 0.76% | 0% | 0 | 24 | 1.7 | 10.9 | NO
[11 empty] | Mar 20 2023 | 96.83% | 2.38% | 0% | 0.79% | 0% | 0 | 24 | 1.4 | 10.5 | NO
[11 empty] | Mar 21 2023 | 97.42% | 1.87% | 0% | 0.71% | 0% | 0 | 24 | 1.2 | 10.4 | NO
[11 empty] | Mar 22 2023 | 97.8% | 1.64% | 0% | 0.56% | 0% | 0 | 24 | 1.7 | 10.3 | NO
[11 empty] | Mar 23 2023 | 97.01% | 2.12% | 0% | 0.87% | 0% | 0 | 24 | 1.7 | 10.5 | NO
[11 empty] | Mar 24 2023 | 97.01% | 2.18% | 0% | 0.79% | 0% | 0 | 24 | 2 | 10.5 | NO
[11 empty] | Mar 25 2023 | 94.71% | 4.38% | 0% | 0.89% | 0% | 0 | 24 | 1.9 | 10.9 | NO
[11 empty] | Mar 26 2023 | 97.79% | 1.76% | 0% | 0.46% | 0% | 0 | 24 | 1.3 | 10.3 | NO
[11 empty] | Mar 27 2023 | 95.27% | 3.66% | 0% | 1.06% | 0% | 0 | 24 | 1.5 | 10.8 | NO
[11 empty] | Mar 28 2023 | 94.36% | 4.67% | 0% | 0.97% | 0% | 0 | 24 | 2.1 | 11 | NO
[11 empty] | Mar 29 2023 | 64.86% | 6.47% | 0% | 12.61% | 16.1% | 8 | 24 | 2 | 18.6 | NO
[11 empty] | Mar 30 2023 | 54.08% | 10.46% | 0% | 15.3% | 20.2% | 10 | 24 | 2.5 | 20 | NO
[11 empty] | Mar 31 2023 | 89.24% | 6.25% | 0% | 4.51% | 0% | 0 | 24 | 2.2 | 11 | NO
[11 empty] | #VALUE! | 88.2% | 2.909% |  | 8.883% | 0.009417% | 24 | 0 | 2.5381 | 10.1548 | NO
[11 empty] | #VALUE! | 93.44% | 5.539% |  | 1.007% | 0.01513% | 24 | 0 | 2.4416 | 11.1225 | NO
[11 empty] | 0 | 95.9% | 3.61% | 0.48% | 0.01% | 0.006667% | 24 | 0 | 1.4 | 10.7 | NO
[11 empty] | 0 | 92.76% | 5.789% |  | 1.444% | 0.004511% | 24 | 0 | 2.1552 | 11.1145 | NO

## A62 Boiler 3
|  | Concentrations in mg/m³ at reference conditions after subtracting uncertainty | [9 empty] | Daily means, excluding hours outside normal operating conditions
|  | 2023-01-01 |  |  | 2023-02-01 |  |  | 2023-03-01 |  |  | Date | Fuel mix |  |  |  |  | No. hours OTNOC | Particulate Matter concentration (mg/m³) after subtracting uncertainty |  |  |  | Sulphur dioxide concentration (mg/m³) after subtracting uncertainty |  |  |  | Oxides of nitrogen concentration (mg/m³) after subtracting uncertainty
|  | PM | SO2 | NOx | PM | SO2 | NOx | PM | SO2 | NOx |  | % BFG | % COG | % BOSg | % NG | % HFO |  | No.valid hours | Measured | Limit | Breach? | No.valid hours | Measured | Limit | Breach? | No.valid hours | Measured | Limit | Breach?
Daily means | Minimum | 1.2 | 19.9 | Monitor out of calibration (Part A - S5N_21_76A) | 1 | 26.2 | Monitor out of calibration (Part A - S5N_21_76A) | 1.2 | 2.3 | Monitor out of calibration (Part A - S5N_21_76A) | Jan 01 2023 | 91.26% | 0.05% | 0% | 8.68% | 0% | 0 | 24 | 2.3 | 10.5 | NO | 24 | 25.7 | 204.4 | NO | 0 |  | 210.4 | -
| Maximum | 5 | 60.1 |  | 5.8 | 60.5 |  | 4.8 | 58 |  | Jan 02 2023 | 99.86% | 0.05% | 0% | 0.09% | 0% | 0 | 24 | 1.4 | 11 | NO | 24 | 37.6 | 220 | NO | 0 |  | 219.9 | -
| No. > Limit | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | Jan 03 2023 | 99.81% | 0.09% | 0% | 0.1% | 0% | 0 | 24 | 1.6 | 11 | NO | 24 | 30.5 | 220 | NO | 0 |  | 219.9 | -
Monthly mean |  | 2.2 | 37.8 |  | 2.1 | 42.7 |  | 2.4 | 42.2 |  | Jan 04 2023 | 99.74% | 0.23% | 0% | 0.03% | 0% | 0 | 24 | 1.2 | 11 | NO | 24 | 42.2 | 220.4 | NO | 0 |  | 220 | -
Monthly mean limit |  | 9.5 | 172.6 | 180.4 | 9.5 | 183.8 | 184.2 | 10 | 187 | 188 | Jan 05 2023 | 39.8% | 15.51% | 0% | 44.7% | 0% | 16 | 24 | 1.5 | 12 | NO | 24 | 29.8 | 173 | NO | 0 |  | 170.8 | -
[11 empty] | Jan 06 2023 | 66.86% | 8.9% | 0% | 24.24% | 0% | 4 | 24 | 2.8 | 11.6 | NO | 24 | 36.3 | 195.6 | NO | 0 |  | 193.3 | -
[11 empty] | Jan 07 2023 | 92.37% | 0.05% | 0% | 7.58% | 0% | 0 | 24 | 2.1 | 10.6 | NO | 24 | 36.6 | 206.4 | NO | 0 |  | 211.7 | -
[11 empty] | Jan 08 2023 | 92.14% | 0% | 0% | 7.86% | 0% | 0 | 24 | 2.2 | 10.6 | NO | 24 | 41.7 | 205.7 | NO | 0 |  | 211.4 | -
[11 empty] | Jan 09 2023 | 80.84% | 4.83% | 0% | 14.33% | 0% | 0 | 24 | 1.9 | 11.3 | NO | 24 | 36.1 | 204.6 | NO | 0 |  | 204.2 | -
[11 empty] | Jan 10 2023 | 46.72% | 4.41% | 0% | 48.88% | 0% | 14 | 24 | 2.6 | 9.3 | NO | 24 | 33.7 | 141 | NO | 0 |  | 166.2 | -
[11 empty] | Jan 11 2023 | 92.94% | 3.02% | 0% | 4.05% | 0% | 0 | 24 | 2.9 | 11.4 | NO | 24 | 35.2 | 219.3 | NO | 0 |  | 215.5 | -
[11 empty] | Jan 12 2023 | 19.69% | 0.17% | 0% | 80.14% | 0% | 21 | 24 | 1.9 | 6.6 | NO | 24 | 23.1 | 74.9 | NO | 0 |  | 131.8 | -
[11 empty] | Jan 13 2023 | 16.39% | 17.2% | 0% | 66.41% | 0% | 23 | 24 | 4.7 | 11.1 | NO | 24 | 19.9 | 137.3 | NO | 0 |  | 146.9 | -
[11 empty] | Jan 14 2023 | 63.17% | 16.48% | 0% | 20.36% | 0% | 8 | 24 | 5 | 13.5 | NO | 24 | 48.4 | 219.3 | NO | 0 |  | 197.6 | -
[11 empty] | Jan 15 2023 | 73.5% | 1.01% | 0% | 25.49% | 0% | 7 | 24 | 2 | 9.8 | NO | 24 | 43.6 | 175.9 | NO | 0 |  | 192 | -
[11 empty] | Jan 16 2023 | 97.67% | 0.06% | 0% | 2.27% | 0% | 0 | 24 | 1.5 | 10.9 | NO | 24 | 50.3 | 216 | NO | 0 |  | 217.5 | -
[11 empty] | Jan 17 2023 | 94.21% | 1.58% | 0% | 4.2% | 0% | 0 | 24 | 1.8 | 11.1 | NO | 24 | 42.6 | 215.9 | NO | 0 |  | 215.4 | -
[11 empty] | Jan 18 2023 | 65.86% | 0.26% | 0% | 33.88% | 0% | 6 | 24 | 2.3 | 9.2 | NO | 24 | 32 | 159.1 | NO | 0 |  | 182.7 | -
[11 empty] | Jan 19 2023 | 84.49% | 0.07% | 0% | 15.44% | 0% | 3 | 24 | 4.1 | 10.2 | NO | 24 | 27.6 | 192.1 | NO | 0 |  | 203 | -
[11 empty] | Jan 20 2023 | 98.64% | 0.06% | 0% | 1.3% | 0% | 0 | 24 | 2.4 | 10.9 | NO | 24 | 42.7 | 217.8 | NO | 0 |  | 218.6 | -
[11 empty] | Jan 21 2023 | 98.22% | 0.08% | 0% | 1.71% | 0% | 0 | 24 | 2.3 | 10.9 | NO | 24 | 38.4 | 217.1 | NO | 0 |  | 218.1 | -
[11 empty] | Jan 22 2023 | 75.56% | 0.14% | 0% | 24.3% | 0% | 7 | 24 | 1.7 | 9.7 | NO | 24 | 42.1 | 176.2 | NO | 0 |  | 193.3 | -
[11 empty] | Jan 23 2023 | 76.65% | 0.13% | 0% | 23.22% | 0% | 0 | 24 | 2.1 | 9.8 | NO | 24 | 30.9 | 178.1 | NO | 0 |  | 194.5 | -
[11 empty] | Jan 24 2023 | 47.21% | 0.22% | 0% | 52.57% | 0% | 13 | 24 | 1.9 | 8.2 | NO | 24 | 46.2 | 125.1 | NO | 0 |  | 162.2 | -
[11 empty] | Jan 25 2023 | 16.49% | 0.26% | 0% | 83.25% | 0% | 19 | 24 | 2.3 | 6.5 | NO | 24 | 35.2 | 69.5 | NO | 0 |  | 128.4 | -
[11 empty] | Jan 26 2023 | 88.83% | 0.2% | 0% | 10.96% | 0% | 0 | 24 | 2.6 | 10.4 | NO | 24 | 26 | 200.5 | NO | 0 |  | 207.9 | -
[11 empty] | Jan 27 2023 | 99.69% | 0.21% | 0% | 0.1% | 0% | 0 | 24 | 2.1 | 11 | NO | 24 | 42.7 | 220.3 | NO | 0 |  | 219.9 | -
[11 empty] | Jan 28 2023 | 99.77% | 0.13% | 0% | 0.11% | 0% | 0 | 24 | 1.6 | 11 | NO | 24 | 39.7 | 220.1 | NO | 0 |  | 219.9 | -
[11 empty] | Jan 29 2023 | 99.78% | 0.14% | 0% | 0.08% | 0% | 0 | 24 | 1.4 | 11 | NO | 24 | 49.8 | 220.2 | NO | 0 |  | 219.9 | -
[11 empty] | Jan 30 2023 | 99.87% | 0.11% | 0% | 0.02% | 0% | 0 | 24 | 1.2 | 11 | NO | 24 | 60.1 | 220.2 | NO | 0 |  | 220 | -
[11 empty] | Jan 31 2023 | 99.85% | 0.1% | 0% | 0.04% | 0% | 0 | 24 | 1.3 | 11 | NO | 24 | 46.8 | 220.2 | NO | 0 |  | 220 | -
[11 empty] | Feb 01 2023 | 99.91% | 0.05% | 0% | 0.04% | 0% | 0 | 24 | 1.4 | 11 | NO | 24 | 47.8 | 220 | NO | 0 |  | 220 | -
[11 empty] | Feb 02 2023 | 99.89% | 0.05% | 0% | 0.05% | 0% | 0 | 24 | 1.2 | 11 | NO | 24 | 60.5 | 220 | NO | 0 |  | 219.9 | -
[11 empty] | Feb 03 2023 | 99.93% | 0.05% | 0% | 0.02% | 0% | 0 | 24 | 1.1 | 11 | NO | 24 | 51.9 | 220.1 | NO | 0 |  | 220 | -
[11 empty] | Feb 04 2023 | 99.98% | 0.01% | 0% | 0.01% | 0% | 0 | 24 | 1.2 | 11 | NO | 24 | 47.7 | 220 | NO | 0 |  | 220 | -
[11 empty] | Feb 05 2023 | 99.92% | 0.03% | 0% | 0.05% | 0% | 0 | 24 | 1.2 | 11 | NO | 24 | 48.5 | 220 | NO | 0 |  | 220 | -
[11 empty] | Feb 06 2023 | 94.64% | 0.06% | 0% | 5.31% | 0% | 0 | 24 | 1.8 | 10.7 | NO | 24 | 40.6 | 210.5 | NO | 0 |  | 214.2 | -
[11 empty] | Feb 07 2023 | 92.35% | 0.05% | 0% | 7.6% | 0% | 0 | 24 | 2 | 10.6 | NO | 24 | 30.1 | 206.3 | NO | 0 |  | 211.6 | -
[11 empty] | Feb 08 2023 | 94.41% | 1.16% | 0% | 4.43% | 0% | 0 | 24 | 4.5 | 11 | NO | 24 | 26.2 | 214.5 | NO | 0 |  | 215.1 | -
[11 empty] | Feb 09 2023 | 74.01% | 0.02% | 0% | 25.97% | 0% | 7 | 24 | 5.8 | 9.6 | NO | 24 | 35 | 172.9 | NO | 0 |  | 191.4 | -
[11 empty] | Feb 10 2023 | 41.65% | 0.07% | 0% | 58.28% | 0% | 15 | 24 | 4.3 | 7.8 | NO | 24 | 37 | 114.4 | NO | 0 |  | 155.9 | -
[11 empty] | Feb 11 2023 | 99.87% | 0.04% | 0% | 0.09% | 0% | 0 | 24 | 1.4 | 11 | NO | 24 | 45.1 | 219.9 | NO | 0 |  | 219.9 | -
[11 empty] | Feb 12 2023 | 99.92% | 0.07% | 0% | 0.01% | 0% | 0 | 24 | 1.3 | 11 | NO | 24 | 51.7 | 220.1 | NO | 0 |  | 220 | -
[11 empty] | Feb 13 2023 | 74.79% | 0.16% | 0% | 25.05% | 0% | 6 | 24 | 4.3 | 9.7 | NO | 24 | 27.2 | 174.9 | NO | 0 |  | 192.4 | -
[11 empty] | Feb 14 2023 | 99.66% | 0.16% | 0% | 0.18% | 0% | 0 | 24 | 2.2 | 11 | NO | 24 | 34.1 | 220 | NO | 0 |  | 219.8 | -
[11 empty] | Feb 15 2023 | 99.11% | 0.14% | 0% | 0.75% | 0% | 0 | 24 | 1.5 | 11 | NO | 24 | 38.8 | 219 | NO | 0 |  | 219.2 | -
[11 empty] | Feb 16 2023 | 99.72% | 0.19% | 0% | 0.09% | 0% | 0 | 24 | 1.7 | 11 | NO | 24 | 32.9 | 220.3 | NO | 0 |  | 219.9 | -
[11 empty] | Feb 17 2023 | 99.75% | 0.19% | 0% | 0.06% | 0% | 0 | 24 | 1.5 | 11 | NO | 24 | 38 | 220.3 | NO | 0 |  | 219.9 | -
[11 empty] | Feb 18 2023 | 99.83% | 0.15% | 0% | 0.02% | 0% | 0 | 24 | 1.2 | 11 | NO | 24 | 46.7 | 220.3 | NO | 0 |  | 220 | -
[11 empty] | Feb 19 2023 | 74.61% | 0.26% | 0% | 25.14% | 0% | 7 | 24 | 1 | 9.7 | NO | 24 | 50.9 | 174.9 | NO | 0 |  | 192.4 | -
[11 empty] | Feb 20 2023 | 53.84% | 0.42% | 0% | 45.74% | 0% | 13 | 24 | 2.4 | 8.6 | NO | 24 | 43.7 | 137.9 | NO | 0 |  | 169.7 | -
[11 empty] | Feb 21 2023 | 10.72% | 0.64% | 0% | 88.64% | 0% | 24 | 24 |  |  | - | 24 |  |  | - | 0 |  |  | -
[11 empty] | Feb 22 2023 | 8.27% | 0.68% | 0% | 91.05% | 0% | 24 | 24 |  |  | - | 24 |  |  | - | 0 |  |  | -
[11 empty] | Feb 23 2023 | 74.93% | 0.42% | 0% | 24.65% | 0% | 5 | 24 | 3.3 | 9.7 | NO | 24 | 34 | 176.2 | NO | 0 |  | 192.9 | -
[11 empty] | Feb 24 2023 | 99.68% | 0.29% | 0% | 0.02% | 0% | 0 | 24 | 1.4 | 11.1 | NO | 24 | 46 | 220.6 | NO | 0 |  | 220 | -
[11 empty] | Feb 25 2023 | 96.83% | 0.31% | 0% | 2.86% | 0% | 1 | 24 | 1.5 | 10.9 | NO | 24 | 46.6 | 215.5 | NO | 0 |  | 216.9 | -
[11 empty] | Feb 26 2023 | 86.74% | 0.35% | 0% | 12.91% | 0% | 3 | 24 | 1.6 | 10.4 | NO | 24 | 49.2 | 197.3 | NO | 0 |  | 205.8 | -
[11 empty] | Feb 27 2023 | 94.23% | 1.19% | 0% | 4.58% | 0% | 0 | 24 | 1.8 | 11 | NO | 24 | 47.2 | 214.3 | NO | 0 |  | 215 | -
[11 empty] | Feb 28 2023 | 81.84% | 0.06% | 0% | 18.1% | 0% | 5 | 24 | 1.2 | 10 | NO | 24 | 52 | 187.3 | NO | 0 |  | 200.1 | -
[11 empty] | Mar 01 2023 | 4.27% | 7.48% | 0% | 88.25% | 0% | 24 | 24 |  |  | - | 24 |  |  | - | 0 |  |  | -
[11 empty] | Mar 02 2023 | 13.14% | 20.61% | 0% | 66.25% | 0% | 22 | 24 | 2.6 | 11.9 | NO | 24 | 58 | 145.1 | NO | 0 |  | 147.1 | -
[11 empty] | Mar 03 2023 | 99.67% | 0.24% | 0% | 0.09% | 0% | 0 | 24 | 1.8 | 11 | NO | 24 | 51.7 | 220.4 | NO | 0 |  | 219.9 | -
[11 empty] | Mar 04 2023 | 99.58% | 0.37% | 0% | 0.05% | 0% | 0 | 24 | 1.5 | 11.1 | NO | 24 | 53.9 | 220.7 | NO | 0 |  | 219.9 | -
[11 empty] | Mar 05 2023 | 99.95% | 0.03% | 0% | 0.02% | 0% | 0 | 24 | 1.4 | 11 | NO | 24 | 53.4 | 220 | NO | 0 |  | 220 | -
[11 empty] | Mar 06 2023 | 99.94% | 0.02% | 0% | 0.04% | 0% | 0 | 24 | 1.4 | 11 | NO | 24 | 50 | 220 | NO | 0 |  | 220 | -
[11 empty] | Mar 07 2023 | 99.93% | 0.02% | 0% | 0.05% | 0% | 0 | 24 | 1.7 | 11 | NO | 24 | 43.2 | 220 | NO | 0 |  | 219.9 | -
[11 empty] | Mar 08 2023 | 99.92% | 0.02% | 0% | 0.06% | 0% | 0 | 24 | 2.1 | 11 | NO | 24 | 33.9 | 219.9 | NO | 0 |  | 219.9 | -
[11 empty] | Mar 09 2023 | 99.9% | 0.04% | 0% | 0.06% | 0% | 0 | 24 | 1.6 | 11 | NO | 24 | 46.2 | 220 | NO | 0 |  | 219.9 | -
[11 empty] | Mar 10 2023 | 99.92% | 0.04% | 0% | 0.04% | 0% | 0 | 24 | 2.1 | 11 | NO | 24 | 48 | 220 | NO | 0 |  | 220 | -
[11 empty] | Mar 11 2023 | 76.53% | 0.51% | 0% | 22.96% | 0% | 6 | 24 | 3.3 | 9.8 | NO | 24 | 2.3 | 179.4 | NO | 0 |  | 194.7 | -
[11 empty] | Mar 12 2023 | 99.98% | 0.01% | 0% | 0.01% | 0% | 0 | 24 | 3 | 11 | NO | 24 | 34.9 | 220 | NO | 0 |  | 220 | -
[11 empty] | Mar 13 2023 | 71.49% | 0.13% | 0% | 28.38% | 0% | 8 | 24 | 1.5 | 9.5 | NO | 24 | 45.6 | 168.8 | NO | 0 |  | 188.8 | -
[11 empty] | Mar 14 2023 | 84.67% | 5.14% | 0% | 10.19% | 0% | 4 | 24 | 1.7 | 11.6 | NO | 24 | 54.9 | 212.8 | NO | 0 |  | 208.8 | -
[11 empty] | Mar 15 2023 | 72.08% | 11.04% | 0% | 16.88% | 0% | 7 | 24 | 3 | 12.5 | NO | 24 | 56.8 | 213.7 | NO | 0 |  | 201.4 | -
[11 empty] | Mar 16 2023 | 91.71% | 8.27% | 0% | 0.02% | 0% | 0 | 24 | 1.4 | 12.8 | NO | 24 | 53.5 | 238.2 | NO | 0 |  | 220 | -
[11 empty] | Mar 17 2023 | 55.36% | 0.29% | 0% | 44.35% | 0% | 13 | 24 | 1.2 | 8.6 | NO | 24 | 43.8 | 140.1 | NO | 0 |  | 171.2 | -
[11 empty] | Mar 18 2023 | 91.09% | 0.1% | 0% | 8.81% | 0% | 2 | 24 | 1.6 | 10.5 | NO | 24 | 44.7 | 204.2 | NO | 0 |  | 210.3 | -
[11 empty] | Mar 19 2023 | 99.86% | 0.09% | 0% | 0.05% | 0% | 0 | 24 | 2.6 | 11 | NO | 24 | 24.9 | 220.1 | NO | 0 |  | 219.9 | -
[11 empty] | Mar 20 2023 | 98.74% | 0.09% | 0% | 1.17% | 0% | 0 | 24 | 1.8 | 11 | NO | 24 | 28.8 | 218.1 | NO | 0 |  | 218.7 | -
[11 empty] | Mar 21 2023 | 99.94% | 0.03% | 0% | 0.03% | 0% | 0 | 24 | 3.1 | 11 | NO | 24 | 38 | 220 | NO | 0 |  | 220 | -
[11 empty] | Mar 22 2023 | 99.75% | 0.23% | 0% | 0.03% | 0% | 0 | 24 | 4 | 11 | NO | 24 | 36 | 220.5 | NO | 0 |  | 220 | -
[11 empty] | Mar 23 2023 | 85.79% | 4.44% | 0% | 9.77% | 0% | 3 | 24 | 3 | 11.4 | NO | 24 | 40.6 | 212 | NO | 0 |  | 209.3 | -
[11 empty] | Mar 24 2023 | 95.7% | 1.5% | 0% | 2.8% | 0% | 1 | 24 | 4.2 | 11.2 | NO | 24 | 41.8 | 218.2 | NO | 0 |  | 216.9 | -
[11 empty] | Mar 25 2023 | 49.91% | 5.39% | 0% | 44.7% | 0% | 13 | 24 | 4.8 | 9.7 | NO | 24 | 40.7 | 150.7 | NO | 0 |  | 170.8 | -
[11 empty] | Mar 26 2023 | 99.85% | 0.06% | 0% | 0.09% | 0% | 0 | 24 | 2.3 | 10.1 | NO | 24 | 43.9 | 201.6 | NO | 0 |  | 201.6 | -
[11 empty] | Mar 27 2023 | 76.35% | 7.96% | 0% | 15.7% | 0% | 6 | 24 | 1.8 | 11.9 | NO | 24 | 29.9 | 209 | NO | 0 |  | 202.7 | -
[11 empty] | Mar 28 2023 | 44.58% | 19.92% | 0% | 35.5% | 0% | 15 | 24 | 3.1 | 13.4 | NO | 24 | 41 | 199.4 | NO | 0 |  | 181 | -
[11 empty] | Mar 29 2023 | 8% | 30.67% | 0% | 61.33% | 0% | 24 | 24 |  |  | - | 24 |  |  | - | 0 |  |  | -
[11 empty] | Mar 30 2023 | 38.98% | 15.52% | 0% | 45.5% | 0% | 14 | 24 | 4.8 | 11.9 | NO | 24 | 45 | 171.6 | NO | 0 |  | 169.9 | -
[11 empty] | Mar 31 2023 | 45.21% | 19.96% | 0% | 34.82% | 0% | 13 | 24 | 3.8 | 13.5 | NO | 24 | 46.4 | 200.7 | NO | 0 |  | 181.7 | -