## Notes
Reference conditions
All concentrations in this spreadsheet are reported in dry air at a temperature of 273K, at a pressure of 101.3 kPa and with an oxygen content of 3% dry
Uncertainty
Concentrations in this spreadsheet are reported after having subtracted the value of the 95% confidence interval (see Section 3.6.7 of the permit):
95% confidence interval for nitrogen oxides is taken to be 20%
95% confidence interval for sulphur dioxide is taken to be 20%
95% confidence interval for dust is taken to be 30%
95% confidence interval for carbon monoxide is taken to be 10%
Normal operating conditions
The document "Power Plant Boiler Abnormal Conditions" sets out the criteria for excluding emissions monitoring data from permitting or other reporting obligations:
| Parameter | Plant | Level representing abnormal conditions
| Boiler oxygen | All boilers | >17% oxygen
| Fuel input | A51, A52A, A52B, A53 and A62 | <50% BFG by thermal input
|  | A50 (Service Boilers) | <35% BFG by thermal input

## A50 Service Boilers
|  | Concentrations in mg/m³ at reference conditions after subtracting uncertainty | [9 empty] | Daily means, excluding hours outside normal operating conditions
|  | 2022-10-01 |  |  | 2022-11-01 |  |  | 2022-12-01 |  |  | Date | Fuel mix |  |  |  |  | Particulate Matter concentration (mg/m³) after subtracting uncertainty |  |  |  |  | Sulphur dioxide concentration (mg/m³) after subtracting uncertainty |  |  |  |  | Oxides of nitrogen concentration (mg/m³) after subtracting uncertainty
|  | PM | SO2 | NOx | PM | SO2 | NOx | PM | SO2 | NOx |  | % BFG | % COG | % BOSg | % NG | % HFO | No.valid hours | No.hours OTNOC | Measured | Limit | Breach? | No.valid hours | No.hours OTNOC | Measured | Limit | Breach? | No.valid hours | No.hours OTNOC | Measured | Limit | Breach?
Daily means | Minimum | 0.51689 | 11.0936 | 31.6767 | 0.86305 | 14.086 | 30.254 | 0.37273 | 13.2124 | 7.8045 | 2022-10-01 | 84.91% | 12.96% |  | 2.132% |  | 24 | 0 | 0.7313 | 13.7333 | NO | 24 | 0 | 26.6044 | 244.6336 | NO | 24 | 0 | 34.2054 | 325.3046 | NO
| Maximum | 3.6443 | 143.2417 | 74.6911 | 2.5907 | 122.1848 | 79.0522 | 2.9568 | 158.4603 | 63.3451 | 2022-10-02 | 64.81% | 33.23% |  | 1.962% |  | 24 | 2 | 0.98625 | 18.2016 | NO | 24 | 2 | 49.5875 | 289.5302 | NO | 24 | 2 | 51.3217 | 325.6761 | NO
| No. > Limit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2022-10-03 | 71.04% | 26.73% |  | 2.226% |  | 24 | 3 | 1.3453 | 16.7592 | NO | 24 | 3 | 105.2203 | 274.781 | NO | 24 | 3 | 69.9986 | 325.1117 | NO
Monthly mean |  | 1.3072 | 37.6111 | 46.6771 | 1.3898 | 46.6437 | 47.3609 | 1.7079 | 48.9405 | 41.7669 | 2022-10-04 | 92.45% | 4.98% |  | 2.566% |  | 24 | 0 | 1.6347 | 11.9536 | NO | 24 | 0 | 27.0719 | 226.287 | NO | 24 | 0 | 45.5453 | 324.3487 | NO
Monthly mean limit |  | 15.5449 | 259.0472 | 318.797 | 16.7646 | 271.3003 | 318.8897 | 15.1478 | 256.1099 | 320.5976 | 2022-10-05 | 85.43% | 11.7% |  | 2.873% |  | 24 | 0 | 1.3096 | 13.3749 | NO | 24 | 0 | 11.0936 | 240.2386 | NO | 24 | 0 | 38.5023 | 322.855 | NO
[11 empty] | 2022-10-06 | 78.89% | 18.42% |  | 2.689% |  | 24 | 0 | 0.58768 | 14.8645 | NO | 24 | 0 | 38.6465 | 255.3735 | NO | 24 | 0 | 31.6767 | 323.2701 | NO
[11 empty] | 2022-10-07 | 75.85% | 22.26% |  | 1.893% |  | 24 | 0 | 1.113 | 15.7942 | NO | 24 | 0 | 39.0956 | 265.5531 | NO | 24 | 0 | 39.8791 | 325.8447 | NO
[11 empty] | 2022-10-08 | 51.35% | 39.96% |  | 8.692% |  | 24 | 6 | 1.5238 | 19.3119 | NO | 24 | 6 | 30.3087 | 292.1176 | NO | 24 | 6 | 43.0578 | 310.8674 | NO
[11 empty] | 2022-10-09 | 82.37% | 15.52% |  | 2.114% |  | 24 | 0 | 0.61539 | 14.2969 | NO | 24 | 0 | 22.1561 | 250.2899 | NO | 24 | 0 | 39.5471 | 325.34 | NO
[11 empty] | 2022-10-10 | 44.91% | 45.53% |  | 9.561% |  | 24 | 13 | 1.5821 | 20.4897 | NO | 24 | 13 | 24.7561 | 302.7978 | NO | 24 | 13 | 41.8454 | 308.9571 | NO
[11 empty] | 2022-10-11 | 74.12% | 23.84% |  | 2.037% |  | 24 | 0 | 1.6189 | 16.1319 | NO | 24 | 0 | 26.8882 | 268.7383 | NO | 24 | 0 | 39.6444 | 325.5115 | NO
[11 empty] | 2022-10-12 | 84.08% | 13.67% |  | 2.25% |  | 24 | 0 | 1.1254 | 13.884 | NO | 24 | 0 | 21.9991 | 245.9952 | NO | 24 | 0 | 35.7471 | 325.0524 | NO
[11 empty] | 2022-10-13 | 84.93% | 13% |  | 2.074% |  | 24 | 0 | 0.88177 | 13.747 | NO | 24 | 0 | 61.8448 | 244.8514 | NO | 24 | 0 | 47.2939 | 325.4462 | NO
[11 empty] | 2022-10-14 | 91.19% | 6.38% |  | 2.426% |  | 24 | 0 | 0.70044 | 12.2696 | NO | 24 | 0 | 19.4062 | 229.6245 | NO | 24 | 0 | 35.5814 | 324.658 | NO
[11 empty] | 2022-10-15 | 90.32% | 7.42% |  | 2.262% |  | 24 | 0 | 1.4171 | 12.5068 | NO | 24 | 0 | 65.7714 | 232.2011 | NO | 24 | 0 | 42.6402 | 325.0137 | NO
[11 empty] | 2022-10-16 | 61.13% | 34.78% |  | 4.092% |  | 24 | 6 | 1.1839 | 18.4253 | NO | 24 | 6 | 36.5523 | 289.0705 | NO | 24 | 6 | 65.5829 | 320.9873 | NO
[11 empty] | 2022-10-17 | 91.6% | 4.04% |  | 4.357% |  | 24 | 0 | 0.52254 | 11.6499 | NO | 24 | 0 | 20.4766 | 220.9907 | NO | 24 | 0 | 51.2806 | 320.42 | NO
[11 empty] | 2022-10-18 | 74.52% | 9.21% |  | 16.27% |  | 24 | 0 | 1.6648 | 12.1315 | NO | 24 | 0 | 15.2198 | 210.7298 | NO | 24 | 0 | 44.1669 | 294.1992 | NO
[11 empty] | 2022-10-19 | 71.88% | 14.39% |  | 13.73% |  | 24 | 0 | 0.89338 | 13.4121 | NO | 24 | 0 | 14.5032 | 226.7635 | NO | 24 | 0 | 43.864 | 299.8136 | NO
[11 empty] | 2022-10-20 | 71.02% | 20.15% |  | 8.83% |  | 24 | 0 | 1.1746 | 14.9478 | NO | 24 | 0 | 20.4555 | 248.3096 | NO | 24 | 0 | 45.6364 | 310.5773 | NO
[11 empty] | 2022-10-21 | 80.67% | 17.11% |  | 2.218% |  | 24 | 0 | 0.51689 | 14.6434 | NO | 24 | 0 | 37.0098 | 253.6345 | NO | 24 | 0 | 43.1711 | 325.1309 | NO
[11 empty] | 2022-10-22 | 79.48% | 18.39% |  | 2.126% |  | 24 | 0 | 1.7825 | 14.9282 | NO | 24 | 0 | 53.8575 | 256.5896 | NO | 24 | 0 | 53.6573 | 325.317 | NO
[11 empty] | 2022-10-23 | 73.72% | 24.15% |  | 2.131% |  | 24 | 0 | 1.6656 | 16.1963 | NO | 24 | 0 | 35.2087 | 269.2692 | NO | 24 | 0 | 48.4586 | 325.3156 | NO
[11 empty] | 2022-10-24 | 79.36% | 18.58% |  | 2.057% |  | 24 | 0 | 1.1481 | 14.9753 | NO | 24 | 0 | 30.5865 | 257.1539 | NO | 24 | 0 | 52.3285 | 325.4805 | NO
[11 empty] | 2022-10-25 | 16.97% | 69.52% |  | 13.51% |  | 24 | 21 | 2.4472 | 25.5515 | NO | 24 | 21 | 24.7497 | 348.4302 | NO | 24 | 21 | 53.0006 | 300.2878 | NO
[11 empty] | 2022-10-26 | 9.907% | 73.02% |  | 17.07% |  | 24 | 24
[11 empty] | 2022-10-27 | 57.68% | 33.12% |  | 9.201% |  | 24 | 6 | 3.6443 | 17.7806 | NO | 24 | 6 | 143.2417 | 276.1676 | NO | 24 | 6 | 74.6911 | 309.76 | NO
[11 empty] | 2022-10-28 | 87.12% | 10.35% |  | 2.531% |  | 24 | 0 | 1.7485 | 13.1385 | NO | 24 | 0 | 48.3724 | 238.1865 | NO | 24 | 0 | 47.9437 | 324.438 | NO
[11 empty] | 2022-10-29 | 83.23% | 14.45% |  | 2.316% |  | 24 | 0 | 1.2851 | 14.0503 | NO | 24 | 0 | 16.7231 | 247.5666 | NO | 24 | 0 | 43.0411 | 324.8939 | NO
[11 empty] | 2022-10-30 | 45.05% | 42.35% |  | 12.6% |  | 24 | 8 | 1.1439 | 19.6237 | NO | 24 | 8 | 26.1041 | 290.2946 | NO | 24 | 8 | 40.9139 | 302.2741 | NO
[11 empty] | 2022-10-31 | 59.75% | 31.95% |  | 8.296% |  | 24 | 3 | 1.2215 | 17.5738 | NO | 24 | 3 | 34.8218 | 275.2478 | NO | 24 | 3 | 56.0913 | 311.7564 | NO
[11 empty] | 2022-11-01 | 69.25% | 20.18% |  | 10.57% |  | 24 | 3 | 2.1453 | 14.8582 | NO | 24 | 3 | 30.1716 | 245.2134 | NO | 24 | 3 | 46.1326 | 306.7507 | NO
[11 empty] | 2022-11-02 | 62.4% | 32.53% |  | 5.071% |  | 24 | 3 | 1.1421 | 17.8783 | NO | 24 | 3 | 122.1848 | 282.3714 | NO | 24 | 3 | 71.0341 | 318.8489 | NO
[11 empty] | 2022-11-03 | 76.01% | 21.94% |  | 2.047% |  | 24 | 0 | 1.0684 | 15.7137 | NO | 24 | 0 | 33.0761 | 264.5454 | NO | 24 | 0 | 53.9819 | 325.4922 | NO
[11 empty] | 2022-11-04 | 77.87% | 20.26% |  | 1.873% |  | 24 | 0 | 1.3274 | 15.3539 | NO | 24 | 0 | 44.8125 | 261.1682 | NO | 24 | 0 | 40.716 | 325.8776 | NO
[11 empty] | 2022-11-05 | 72.93% | 24.43% |  | 2.644% |  | 24 | 0 | 1.1901 | 16.1888 | NO | 24 | 0 | 27.5216 | 268.672 | NO | 24 | 0 | 44.8563 | 323.366 | NO
[11 empty] | 2022-11-06 | 76.25% | 20.82% |  | 2.929% |  | 24 | 0 | 1.4293 | 15.3774 | NO | 24 | 0 | 33.9076 | 260.1888 | NO | 24 | 0 | 47.155 | 322.7251 | NO
[11 empty] | 2022-11-07 | 60.82% | 35.21% |  | 3.968% |  | 24 | 5 | 1.2422 | 18.5268 | NO | 24 | 5 | 43.2608 | 290.2424 | NO | 24 | 5 | 52.1665 | 321.2603 | NO
[11 empty] | 2022-11-08 | 32.25% | 49.71% |  | 18.04% |  | 24 | 16 | 1.2595 | 20.945 | NO | 24 | 16 | 34.9994 | 296.6382 | NO | 24 | 16 | 47.0676 | 290.3278 | NO
[11 empty] | 2022-11-09 | 80.64% | 17.32% |  | 2.035% |  | 24 | 0 | 1.1959 | 14.6985 | NO | 24 | 0 | 27.886 | 254.4104 | NO | 24 | 0 | 46.8781 | 325.5228 | NO
[11 empty] | 2022-11-10 | 71.98% | 25.81% |  | 2.214% |  | 24 | 0 | 1.4101 | 16.5572 | NO | 24 | 0 | 45.3514 | 272.7747 | NO | 24 | 0 | 51.4585 | 325.1358 | NO
[11 empty] | 2022-11-11 | 6.555% | 69.64% |  | 23.81% |  | 24 | 23 | 1.5245 | 25.0113 | NO | 24 | 23 | 116.8787 | 329.9982 | NO | 24 | 23 | 79.0522 | 277.6265 | NO
[11 empty] | 2022-11-12 | 11.68% | 63.26% |  | 25.06% |  | 24 | 24 |  |  |  | 24 | 24 |  |  |  | 24 | 24
[11 empty] | 2022-11-13 | 41.98% | 54.1% |  | 3.916% |  | 24 | 12 | 0.95971 | 22.6865 | NO | 24 | 12 | 101.5333 | 331.9107 | NO | 24 | 12 | 72.941 | 321.3836 | NO
[11 empty] | 2022-11-14 | 57.04% | 41.3% |  | 1.665% |  | 24 | 0 | 1.0393 | 19.9933 | NO | 24 | 0 | 102.1888 | 307.8213 | NO | 24 | 0 | 64.8303 | 326.3281 | NO
[11 empty] | 2022-11-15 | 78.39% | 20.05% |  | 1.563% |  | 24 | 0 | 1.1945 | 15.3261 | NO | 24 | 0 | 44.7889 | 261.2884 | NO | 24 | 0 | 34.5663 | 326.5699 | NO
[11 empty] | 2022-11-16 | 59.69% | 37.36% |  | 2.946% |  | 24 | 8 | 2.5907 | 19.0584 | NO | 24 | 8 | 26.117 | 296.8637 | NO | 24 | 8 | 41.8196 | 323.5294 | NO
[11 empty] | 2022-11-17 | 83.18% | 15.48% |  | 1.345% |  | 24 | 0 | 1.6608 | 14.3313 | NO | 24 | 0 | 16.5774 | 251.61 | NO | 24 | 0 | 35.4712 | 327.0386 | NO
[11 empty] | 2022-11-18 | 78.07% | 20.65% |  | 1.275% |  | 24 | 0 | 1.2583 | 15.4731 | NO | 24 | 0 | 23.9784 | 263.1192 | NO | 24 | 0 | 35.399 | 327.1964 | NO
[11 empty] | 2022-11-19 | 72.94% | 25.84% |  | 1.224% |  | 24 | 0 | 0.86305 | 16.6176 | NO | 24 | 0 | 14.086 | 274.6275 | NO | 24 | 0 | 35.5393 | 327.3072 | NO
[11 empty] | 2022-11-20 | 69.31% | 29.58% |  | 1.111% |  | 24 | 0 | 1.2772 | 17.4476 | NO | 24 | 0 | 34.0214 | 283.076 | NO | 24 | 0 | 32.5739 | 327.5654 | NO
[11 empty] | 2022-11-21 | 80.83% | 17.82% |  | 1.349% |  | 24 | 0 | 1.4205 | 14.8462 | NO | 24 | 0 | 19.6 | 256.7548 | NO | 24 | 0 | 32.6082 | 327.0319 | NO
[11 empty] | 2022-11-22 | 83.87% | 14.54% |  | 1.593% |  | 24 | 0 | 1.2161 | 14.1103 | NO | 24 | 0 | 39.4612 | 249.0838 | NO | 24 | 0 | 39.913 | 326.4882 | NO
[11 empty] | 2022-11-23 | 73.55% | 25.06% |  | 1.387% |  | 24 | 0 | 1.7405 | 16.4367 | NO | 24 | 0 | 27.6833 | 272.612 | NO | 24 | 0 | 39.7248 | 326.9473 | NO
[11 empty] | 2022-11-24 | 86.65% | 11.07% |  | 2.277% |  | 24 | 0 | 1.2197 | 13.3094 | NO | 24 | 0 | 42.9531 | 240.2098 | NO | 24 | 0 | 44.5826 | 324.9842 | NO
[11 empty] | 2022-11-25 | 86.53% | 10.71% |  | 2.757% |  | 24 | 1 | 1.3304 | 13.2043 | NO | 24 | 1 | 21.7285 | 238.5537 | NO | 24 | 1 | 30.254 | 323.9322 | NO
[11 empty] | 2022-11-26 | 76.98% | 18.42% |  | 4.604% |  | 24 | 1 | 2.0781 | 14.7993 | NO | 24 | 1 | 66.1012 | 252.1687 | NO | 24 | 1 | 56.2226 | 319.8715 | NO
[11 empty] | 2022-11-27 | 72.92% | 25.15% |  | 1.925% |  | 24 | 0 | 0.95679 | 16.4281 | NO | 24 | 0 | 33.648 | 271.8497 | NO | 24 | 0 | 36.8635 | 325.772 | NO
[11 empty] | 2022-11-28 | 46.39% | 48.26% |  | 5.348% |  | 24 | 10 | 1.4023 | 21.3221 | NO | 24 | 10 | 33.583 | 316.451 | NO | 24 | 10 | 42.0311 | 318.2268 | NO
[11 empty] | 2022-11-29 | 8.704% | 44.01% |  | 47.29% |  | 24 | 24 |  |  |  | 24 | 24 |  |  |  | 24 | 24
[11 empty] | 2022-11-30 | 54.84% | 15.98% |  | 29.18% |  | 24 | 7 | 1.7707 | 12.9097 | NO | 24 | 7 | 97.922 | 202.1848 | NO | 24 | 7 | 70.2663 | 265.8045 | NO
[11 empty] | 2022-12-01 | 68.38% | 10.23% |  | 21.39% |  | 24 | 0 | 1.6467 | 12.0745 | NO | 24 | 0 | 23.4199 | 203.686 | NO | 24 | 0 | 44.6631 | 282.9417 | NO
[11 empty] | 2022-12-02 | 83.5% | 11.29% |  | 5.209% |  | 24 | 0 | 1.5331 | 13.1979 | NO | 24 | 0 | 60.961 | 235.3928 | NO | 24 | 0 | 34.3889 | 318.5453 | NO
[11 empty] | 2022-12-03 | 80.95% | 17.54% |  | 1.506% |  | 24 | 0 | 1.055 | 14.7748 | NO | 24 | 0 | 24.2856 | 255.8378 | NO | 24 | 0 | 35.4937 | 326.6782 | NO
[11 empty] | 2022-12-04 | 87.26% | 10.97% |  | 1.769% |  | 24 | 0 | 1.3066 | 13.315 | NO | 24 | 0 | 29.9814 | 240.9076 | NO | 24 | 0 | 36.3351 | 326.0998 | NO
[11 empty] | 2022-12-05 | 89.66% | 7.78% |  | 2.558% |  | 24 | 0 | 0.95614 | 12.5285 | NO | 24 | 0 | 43.006 | 232.1673 | NO | 24 | 0 | 41.738 | 323.5376 | NO
[11 empty] | 2022-12-06 | 90.43% | 7.15% |  | 2.424% |  | 24 | 0 | 1.3484 | 12.3973 | NO | 24 | 0 | 49.3037 | 231.0245 | NO | 24 | 0 | 45.0003 | 323.8327 | NO
[11 empty] | 2022-12-07 | 94.91% | 3.52% |  | 1.571% |  | 24 | 0 | 1.2092 | 11.6881 | NO | 24 | 0 | 23.6041 | 224.8937 | NO | 24 | 0 | 31.0525 | 326.5445 | NO
[11 empty] | 2022-12-08 | 83.31% | 15.02% |  | 1.674% |  | 24 | 0 | 1.4103 | 14.2115 | NO | 24 | 0 | 17.6149 | 249.9934 | NO | 24 | 0 | 32.8723 | 326.3099 | NO
[11 empty] | 2022-12-09 | 90.37% | 7.84% |  | 1.787% |  | 24 | 0 | 1.4312 | 12.6271 | NO | 24 | 0 | 42.4416 | 234.0133 | NO | 24 | 0 | 32.3063 | 326.0728 | NO
[11 empty] | 2022-12-10 | 75.31% | 23.35% |  | 1.338% |  | 24 | 0 | 1.6273 | 16.0626 | NO | 24 | 0 | 61.426 | 268.9294 | NO | 24 | 0 | 40.3083 | 327.0495 | NO
[11 empty] | 2022-12-11 | 81.52% | 16.93% |  | 1.554% |  | 24 | 0 | 1.4172 | 14.6387 | NO | 24 | 0 | 57.6409 | 254.4189 | NO | 24 | 0 | 43.9925 | 326.5772 | NO
[11 empty] | 2022-12-12 | 77.35% | 19.95% |  | 2.697% |  | 24 | 0 | 1.5227 | 15.2402 | NO | 24 | 0 | 33.7724 | 258.9889 | NO | 24 | 0 | 58.1989 | 324.0636 | NO
[11 empty] | 2022-12-13 | 27% | 55.08% |  | 17.92% |  | 24 | 18 | 1.4963 | 22.132 | NO | 24 | 18 | 47.3503 | 308.649 | NO | 24 | 18 | 58.7292 | 290.5724 | NO
[11 empty] | 2022-12-14 | 32.13% | 54.96% |  | 12.91% |  | 24 | 11 | 1.8102 | 22.3813 | NO | 24 | 11 | 158.4603 | 317.4787 | NO | 24 | 11 | 61.3762 | 301.5929 | NO
[11 empty] | 2022-12-15 | 80.2% | 17.68% |  | 2.124% |  | 24 | 0 | 1.9879 | 14.774 | NO | 24 | 0 | 97.8965 | 255.0582 | NO | 24 | 0 | 48.7427 | 325.3363 | NO
[11 empty] | 2022-12-16 | 66.49% | 31.18% |  | 2.333% |  | 24 | 0 | 2.1713 | 17.7308 | NO | 24 | 0 | 44.1844 | 284.3553 | NO | 24 | 0 | 43.4116 | 324.8642 | NO
[11 empty] | 2022-12-17 | 55.31% | 43.28% |  | 1.413% |  | 24 | 0 | 2.9568 | 20.4433 | NO | 24 | 0 | 98.3967 | 312.6439 | NO | 24 | 0 | 62.2254 | 326.8877 | NO
[11 empty] | 2022-12-18 | 56.73% | 41.89% |  | 1.382% |  | 24 | 0 | 2.357 | 20.1402 | NO | 24 | 0 | 107.8404 | 309.6566 | NO | 24 | 0 | 63.3451 | 326.9639 | NO
[11 empty] | 2022-12-19 | 67.05% | 24.86% |  | 8.094% |  | 24 | 0 | 0.37273 | 16.025 | NO | 24 | 0 | 13.2124 | 260.0157 | NO | 24 | 0 | 7.8045 | 312.2013 | NO
[11 empty] | 2022-12-20 | 92.7% | 5.54% |  | 1.762% |  | 24 | 0 | 2.8486 | 12.1223 | NO | 24 | 0 | 28.4252 | 228.9961 | NO | 24 | 0 | 35.0827 | 326.1274 | NO
[11 empty] | 2022-12-21 | 78.32% | 18.27% |  | 3.415% |  | 24 | 0 | 2.3009 | 14.8312 | NO | 24 | 0 | 42.7556 | 253.9907 | NO | 24 | 0 | 37.0618 | 322.4845 | NO
[11 empty] | 2022-12-22 | 83.73% | 14.48% |  | 1.787% |  | 24 | 0 | 1.7507 | 14.086 | NO | 24 | 0 | 52.534 | 248.5929 | NO | 24 | 0 | 37.2457 | 326.0572 | NO
[11 empty] | 2022-12-23 | 64.25% | 30.71% |  | 5.041% |  | 24 | 0 | 1.934 | 17.4801 | NO | 24 | 0 | 31.2069 | 278.4296 | NO | 24 | 0 | 35.7875 | 318.9197 | NO
[11 empty] | 2022-12-24 | 89.68% | 8.32% |  | 2.001% |  | 24 | 0 | 1.2551 | 12.7216 | NO | 24 | 0 | 34.4964 | 234.6908 | NO | 24 | 0 | 47.2943 | 325.6085 | NO
[11 empty] | 2022-12-25 | 67.16% | 31.2% |  | 1.636% |  | 24 | 0 | 1.1355 | 17.7727 | NO | 24 | 0 | 74.8287 | 285.652 | NO | 24 | 0 | 48.5547 | 326.3906 | NO
[11 empty] | 2022-12-26 | 82.12% | 16.28% |  | 1.597% |  | 24 | 0 | 1.7986 | 14.4943 | NO | 24 | 0 | 35.5069 | 252.9256 | NO | 24 | 0 | 35.3785 | 326.4911 | NO
[11 empty] | 2022-12-27 | 89.1% | 9.12% |  | 1.784% |  | 24 | 0 | 2.3548 | 12.9079 | NO | 24 | 0 | 30.3415 | 236.8199 | NO | 24 | 0 | 33.595 | 326.0718 | NO
[11 empty] | 2022-12-28 | 82.75% | 15.46% |  | 1.794% |  | 24 | 0 | 1.5858 | 14.3038 | NO | 24 | 0 | 39.1565 | 250.7744 | NO | 24 | 0 | 48.4918 | 326.0634 | NO
[11 empty] | 2022-12-29 | 92.84% | 5.29% |  | 1.868% |  | 24 | 0 | 2.4784 | 12.0624 | NO | 24 | 0 | 28.3412 | 228.2674 | NO | 24 | 0 | 34.9784 | 325.9016 | NO
[11 empty] | 2022-12-30 | 60.43% | 30.29% |  | 9.28% |  | 24 | 0 | 2.2499 | 17.1528 | NO | 24 | 0 | 40.5373 | 269.7851 | NO | 24 | 0 | 35.3553 | 309.5784 | NO
[11 empty] | 2022-12-31 | 79.58% | 12.31% |  | 8.111% |  | 24 | 0 | 1.6376 | 13.2628 | NO | 24 | 0 | 44.226 | 232.37 | NO | 24 | 0 | 43.9638 | 312.1604 | NO
[11 empty] | 0 | 0% | 0% |  | 0% |  | 24 | 0 | 0.7 | 13.7 | NO | 0 | 0 | 26.6 | 243.5 | NO | 24 | 0 | 34.2 | 324.1 | NO
[11 empty] | 0 | 0% | 0% |  | 0% |  | 0 | 0 | 0 | 0 | NO | 0 | 0 | 0 | 0 | NO | 24 | 0 | 99.7316 | 281.2178 | NO

## A51 Boiler 5
|  | Concentrations in mg/m³ at reference conditions after subtracting uncertainty | [9 empty] | Daily means, excluding hours outside normal operating conditions
|  | 2022-10-01 |  |  | 2022-11-01 |  |  | 2022-12-01 |  |  | Date | Fuel mix |  |  |  |  | Particulate Matter concentration (mg/m³) after subtracting uncertainty
|  | PM | SO2 | NOx | PM | SO2 | NOx | PM | SO2 | NOx |  | % BFG | % COG | % BOSg | % NG | % HFO | No.valid hours | No.hours OTNOC | Measured | Limit | Breach?
Daily means | Minimum | 0.47596 | Discontinuous monitoring only |  | 0.5331 | Discontinuous monitoring only |  | 0.53762 | Discontinuous monitoring only |  | 2022-10-01 | 89.95% | 9.018% |  | 1.036% | 0% | 24 | 0 | 0.55803 | 13.6476 | NO
| Maximum | 1.2342 |  |  | 2.0299 |  |  | 7.7763 |  |  | 2022-10-02 | 87.13% | 9.007% |  | 3.861% | 0% | 24 | 0 | 0.51475 | 13.6446 | NO
| No. > Limit | 0 |  |  | 0 |  |  | 0 |  |  | 2022-10-03 | 86.87% | 10.06% |  | 3.071% | 0% | 24 | 0 | 0.59256 | 13.8869 | NO
Monthly mean |  | 0.66857 |  |  | 0.80806 |  |  | 1.2845 |  |  | 2022-10-04 | 89.56% | 9.39% |  | 1.055% | 0% | 24 | 0 | 0.48963 | 13.7405 | NO
Monthly mean limit |  | 13.5436 |  |  | 13.4383 |  |  | 14.4375 |  |  | 2022-10-05 | 90.7% | 8.213% |  | 1.083% | 0% | 24 | 0 | 0.5549 | 13.4978 | NO
[11 empty] | 2022-10-06 | 91.38% | 7.563% |  | 1.053% | 0% | 24 | 0 | 0.6226 | 13.3284 | NO
[11 empty] | 2022-10-07 | 91.37% | 7.522% |  | 1.106% | 0% | 24 | 0 | 0.65055 | 13.3797 | NO
[11 empty] | 2022-10-08 | 89.32% | 8.734% |  | 1.945% | 0% | 24 | 0 | 0.89074 | 13.987 | NO
[11 empty] | 2022-10-09 | 91.61% | 7.175% |  | 1.216% | 0% | 24 | 0 | 1.1487 | 13.4151 | NO
[11 empty] | 2022-10-10 | 82.51% | 10.55% |  | 6.933% | 0% | 24 | 3 | 1.0669 | 13.926 | NO
[11 empty] | 2022-10-11 | 94.26% | 4.665% |  | 1.074% | 0% | 24 | 0 | 1.2342 | 12.6752 | NO
[11 empty] | 2022-10-12 | 94.08% | 4.807% |  | 1.113% | 0% | 24 | 0 | 0.6469 | 12.7363 | NO
[11 empty] | 2022-10-13 | 93.61% | 5.171% |  | 1.216% | 0% | 24 | 0 | 0.59901 | 12.8623 | NO
[11 empty] | 2022-10-14 | 93.08% | 5.641% |  | 1.278% | 0% | 24 | 0 | 0.62331 | 13.0196 | NO
[11 empty] | 2022-10-15 | 89.89% | 9.154% |  | 0.9538% | 0% | 24 | 0 | 0.6909 | 13.722 | NO
[11 empty] | 2022-10-16 | 89.49% | 9.196% |  | 1.318% | 0% | 24 | 0 | 0.59315 | 13.8578 | NO
[11 empty] | 2022-10-17 | 84.93% | 1.565% |  | 13.51% | 0% | 24 | 0 | 0.60392 | 11.406 | NO
[11 empty] | 2022-10-18 | 82.17% | 0% |  | 17.83% | 0% | 24 | 0 | 0.60883 | 11.0259 | NO
[11 empty] | 2022-10-19 | 70.41% | 0% |  | 29.59% | 0% | 24 | 0 | 0.6051 | 10.4353 | NO
[11 empty] | 2022-10-20 | 70.11% | 0% |  | 29.89% | 0% | 24 | 0 | 0.47596 | 10.2564 | NO
[11 empty] | 2022-10-21 | 85.55% | 11.04% |  | 3.413% | 0% | 24 | 0 | 0.59707 | 14.261 | NO
[11 empty] | 2022-10-22 | 83.39% | 15.6% |  | 1.012% | 0% | 24 | 0 | 0.6094 | 15.3198 | NO
[11 empty] | 2022-10-23 | 79.53% | 19.48% |  | 0.9949% | 0% | 24 | 0 | 0.53501 | 16.1818 | NO
[11 empty] | 2022-10-24 | 85.18% | 13.7% |  | 1.115% | 0% | 24 | 0 | 0.78153 | 14.9103 | NO
[11 empty] | 2022-10-25 | 87.61% | 7.746% |  | 4.645% | 0% | 24 | 0 | 0.71115 | 13.5261 | NO
[11 empty] | 2022-10-26 | 89.97% | 8.622% |  | 1.405% | 0% | 24 | 0 | 0.64867 | 13.8915 | NO
[11 empty] | 2022-10-27 | 87.73% | 10.9% |  | 1.377% | 0% | 24 | 0 | 0.53136 | 14.3767 | NO
[11 empty] | 2022-10-28 | 88.31% | 10.29% |  | 1.406% | 0% | 24 | 0 | 0.67105 | 14.239 | NO
[11 empty] | 2022-10-29 | 88.7% | 9.873% |  | 1.429% | 0% | 24 | 0 | 0.55492 | 14.1608 | NO
[11 empty] | 2022-10-30 | 77.15% | 14.43% |  | 8.418% | 0% | 24 | 0 | 0.66805 | 14.7864 | NO
[11 empty] | 2022-10-31 | 81.8% | 16.75% |  | 1.45% | 0% | 24 | 0 | 0.64684 | 15.7475 | NO
[11 empty] | 2022-11-01 | 81.75% | 16.42% |  | 1.83% | 0% | 24 | 0 | 0.9932 | 15.7633 | NO
[11 empty] | 2022-11-02 | 85.05% | 13.5% |  | 1.456% | 0% | 24 | 0 | 0.74144 | 14.936 | NO
[11 empty] | 2022-11-03 | 88.41% | 10.54% |  | 1.05% | 0% | 24 | 0 | 0.60664 | 14.0488 | NO
[11 empty] | 2022-11-04 | 89.85% | 9.242% |  | 0.9115% | 0% | 24 | 0 | 0.68122 | 13.6928 | NO
[11 empty] | 2022-11-05 | 90.59% | 8.479% |  | 0.9277% | 0% | 24 | 0 | 0.59367 | 13.5245 | NO
[11 empty] | 2022-11-06 | 90.39% | 8.578% |  | 1.029% | 0% | 24 | 0 | 1.6795 | 13.6025 | NO
[11 empty] | 2022-11-07 | 90.8% | 7.724% |  | 1.473% | 0% | 24 | 0 | 0.71331 | 13.4234 | NO
[11 empty] | 2022-11-08 | 87.2% | 7.194% |  | 5.609% | 0% | 24 | 0 | 0.74737 | 13.1057 | NO
[11 empty] | 2022-11-09 | 92.18% | 6.748% |  | 1.077% | 0% | 24 | 0 | 0.59942 | 13.1562 | NO
[11 empty] | 2022-11-10 | 91.96% | 6.866% |  | 1.17% | 0% | 24 | 0 | 0.59704 | 13.2298 | NO
[11 empty] | 2022-11-11 | 89.38% | 8.167% |  | 2.456% | 0% | 24 | 0 | 0.60333 | 13.5684 | NO
[11 empty] | 2022-11-12 | 73.92% | 6.888% |  | 19.19% | 0% | 24 | 0 | 0.5331 | 12.2106 | NO
[11 empty] | 2022-11-13 | 90.84% | 6.423% |  | 2.733% | 0% | 24 | 0 | 0.72749 | 12.9763 | NO
[11 empty] | 2022-11-14 | 92.33% | 6.589% |  | 1.083% | 0% | 24 | 0 | 0.68846 | 13.1264 | NO
[11 empty] | 2022-11-15 | 92.45% | 6.484% |  | 1.069% | 0% | 24 | 0 | 2.0299 | 13.0895 | NO
[11 empty] | 2022-11-16 | 90.79% | 7.88% |  | 1.325% | 0% | 24 | 0 | 0.5774 | 13.5497 | NO
[11 empty] | 2022-11-17 | 91.79% | 6.962% |  | 1.245% | 0% | 24 | 0 | 0.59908 | 13.2753 | NO
[11 empty] | 2022-11-18 | 92.54% | 6.404% |  | 1.058% | 0% | 24 | 0 | 0.66565 | 13.0637 | NO
[11 empty] | 2022-11-19 | 92.51% | 6.445% |  | 1.047% | 0% | 24 | 0 | 0.67776 | 13.0706 | NO
[11 empty] | 2022-11-20 | 92.7% | 6.254% |  | 1.049% | 0% | 24 | 0 | 0.59294 | 13.0302 | NO
[11 empty] | 2022-11-21 | 92.87% | 6.078% |  | 1.051% | 0% | 24 | 0 | 0.68546 | 12.9866 | NO
[11 empty] | 2022-11-22 | 92.94% | 6.028% |  | 1.032% | 0% | 24 | 0 | 0.78637 | 12.9665 | NO
[11 empty] | 2022-11-23 | 89.04% | 5.923% |  | 5.042% | 0% | 24 | 0 | 0.95353 | 12.7743 | NO
[11 empty] | 2022-11-24 | 92.19% | 6.416% |  | 1.397% | 0% | 24 | 0 | 0.94899 | 13.2335 | NO
[11 empty] | 2022-11-25 | 92.28% | 6.581% |  | 1.138% | 0% | 24 | 0 | 0.82019 | 13.1588 | NO
[11 empty] | 2022-11-26 | 92.25% | 6.601% |  | 1.147% | 0% | 24 | 0 | 0.74014 | 13.1723 | NO
[11 empty] | 2022-11-27 | 92.67% | 6.173% |  | 1.158% | 0% | 24 | 0 | 1.1162 | 13.072 | NO
[11 empty] | 2022-11-28 | 69.25% | 13.93% |  | 16.82% | 0.006287% | 24 | 5 | 0.92686 | 15.4641 | NO
[11 empty] | 2022-11-29 | OFF
[11 empty] | 2022-11-30 | OFF
[11 empty] | 2022-12-01 | OFF
[11 empty] | 2022-12-02 | OFF
[11 empty] | 2022-12-03 | OFF
[11 empty] | 2022-12-04 | OFF
[11 empty] | 2022-12-05 | 19.11% | 28.81% |  | 32.41% | 19.67% | 23 | 18 | 7.7763 | 26.7267 | NO
[11 empty] | 2022-12-06 | 81.52% | 17.43% |  | 1.048% | 0% | 24 | 0 | 1.3401 | 15.8328 | NO
[11 empty] | 2022-12-07 | 82.09% | 16.85% |  | 1.058% | 0% | 24 | 0 | 0.93324 | 17.0441 | NO
[11 empty] | 2022-12-08 | 81.05% | 17.98% |  | 0.9715% | 0% | 24 | 0 | 1.0947 | 16.3192 | NO
[11 empty] | 2022-12-09 | 83.9% | 15.37% |  | 0.7384% | 0% | 23 | 0 | 3.1493 | 15.5619 | NO
[11 empty] | 2022-12-10 | 86.19% | 2.547% |  | 11.27% | 0% | 24 | 0 | 0.99076 | 12.1898 | NO
[11 empty] | 2022-12-11 | 88.76% | 0% |  | 11.24% | 0% | 24 | 0 | 0.95944 | 11.9948 | NO
[11 empty] | 2022-12-12 | 87.41% | 0% |  | 12.59% | 0% | 24 | 0 | 1.1666 | 11.117 | NO
[11 empty] | 2022-12-13 | 86.19% | 0% |  | 13.81% | 0% | 24 | 0 | 1.6228 | 11.0844 | NO
[11 empty] | 2022-12-14 | 87% | 0% |  | 13% | 0% | 24 | 0 | 1.1597 | 11.061 | NO
[11 empty] | 2022-12-15 | 88.14% | 0% |  | 11.86% | 0% | 24 | 0 | 1.0985 | 11.0534 | NO
[11 empty] | 2022-12-16 | 82.81% | 0% |  | 17.19% | 0% | 24 | 0 | 1.1531 | 10.8496 | NO
[11 empty] | 2022-12-17 | 73.78% | 7.157% |  | 19.07% | 0% | 24 | 0 | 1.1922 | 12.5533 | NO
[11 empty] | 2022-12-18 | 76.74% | 22.02% |  | 1.237% | 0% | 24 | 0 | 1.0068 | 16.7289 | NO
[11 empty] | 2022-12-19 | 77.15% | 21.68% |  | 1.164% | 0% | 24 | 0 | 0.58044 | 16.6226 | NO
[11 empty] | 2022-12-20 | 86.82% | 11.81% |  | 1.369% | 0% | 24 | 0 | 0.75031 | 14.5094 | NO
[11 empty] | 2022-12-21 | 90.43% | 8.276% |  | 1.294% | 0% | 24 | 0 | 0.68061 | 13.5955 | NO
[11 empty] | 2022-12-22 | 91.44% | 7.473% |  | 1.088% | 0% | 24 | 0 | 0.58228 | 13.3279 | NO
[11 empty] | 2022-12-23 | 92.18% | 6.801% |  | 1.019% | 0% | 24 | 0 | 0.57808 | 13.1793 | NO
[11 empty] | 2022-12-24 | 92.71% | 6.258% |  | 1.029% | 0% | 24 | 0 | 0.53762 | 13.0764 | NO
[11 empty] | 2022-12-25 | 85.55% | 13.13% |  | 1.313% | 0% | 24 | 0 | 0.58316 | 14.7292 | NO
[11 empty] | 2022-12-26 | 82.32% | 16.58% |  | 1.095% | 0% | 24 | 0 | 0.69125 | 15.4796 | NO
[11 empty] | 2022-12-27 | 80.86% | 18.11% |  | 1.025% | 0% | 24 | 0 | 0.84497 | 15.7852 | NO
[11 empty] | 2022-12-28 | 82.61% | 16.34% |  | 1.045% | 0% | 24 | 0 | 1.5122 | 15.3964 | NO
[11 empty] | 2022-12-29 | 85.33% | 13.63% |  | 1.044% | 0% | 24 | 0 | 1.2254 | 14.7419 | NO
[11 empty] | 2022-12-30 | 81.12% | 13.89% |  | 4.997% | 0% | 24 | 0 | 0.75353 | 14.669 | NO
[11 empty] | 2022-12-31 | 82.77% | 13.31% |  | 3.923% | 0% | 24 | 0 | 0.71942 | 14.5839 | NO
[11 empty] | 0 | 84.28% | 11.73% | 0% | 3.991% | 0% | 24 | 0 | 0.6 | 13.6 | NO
[11 empty] | 0 | 84.56% | 11.42% | 0% | 4.022% | 0% | 24 | 0 | 1.0763 | 13.9727 | NO

## A53 Mitchell Boiler
|  | Concentrations in mg/m³ at reference conditions after subtracting uncertainty | [9 empty] | Daily means, excluding hours outside normal operating conditions
|  | 2022-10-01 |  |  | 2022-11-01 |  |  | 2022-12-01 |  |  | Date | Fuel mix |  |  |  |  | Particulate Matter concentration (mg/m³) after subtracting uncertainty
|  | PM | SO2 | NOx | PM | SO2 | NOx | PM | SO2 | NOx |  | % BFG | % COG | % BOSg | % NG | % HFO | No.valid hours | No.hours OTNOC | Measured | Limit | Breach?
Daily means | Minimum | 0 | Discontinuous monitoring only |  | 0 | Discontinuous monitoring only |  | 0 | Discontinuous monitoring only |  | 2022-10-01 | 95.9% | 3.607% |  | 0.4819% | 0.008967% | 24 | 0 | 1.4386 | 10.7023 | NO
| Maximum | 2.2056 |  |  | 5.5455 |  |  | 2.5381 |  |  | 2022-10-02 | 95.38% | 3.972% |  | 0.6449% | 0.005757% | 24 | 0 | 1.1995 | 10.7952 | NO
| No. > Limit | 0 |  |  | 0 |  |  | 0 |  |  | 2022-10-03 | 95.2% | 4.237% |  | 0.5568% | 0.008241% | 24 | 0 | 1.1923 | 10.8305 | NO
Monthly mean |  | 1.5409 |  |  | 1.8866 |  |  | 1.856 |  |  | 2022-10-04 | 94.7% | 4.651% |  | 0.632% | 0.0142% | 24 | 0 | 1.908 | 10.9186 | NO
Monthly mean limit |  | 10.4466 |  |  | 11.0843 |  |  | 10.3185 |  |  | 2022-10-05 | 96.08% | 3.435% |  | 0.473% | 0.008329% | 24 | 0 | 1.8268 | 10.6673 | NO
[11 empty] | 2022-10-06 | 96.48% | 2.982% |  | 0.53% | 0.004857% | 24 | 0 | 1.5611 | 10.5725 | NO
[11 empty] | 2022-10-07 | 95.83% | 3.548% |  | 0.6084% | 0.008719% | 24 | 0 | 1.8588 | 10.6933 | NO
[11 empty] | 2022-10-08 | 95.97% | 3.082% |  | 0.9329% | 0.009737% | 24 | 0 | 0 | 10.6063 | NO
[11 empty] | 2022-10-09 | 96.65% | 2.869% |  | 0.4806% | 0.003413% | 24 | 0 | 1.3212 | 10.5515 | NO
[11 empty] | 2022-10-10 | 96.69% | 2.59% |  | 0.7143% | 0.003618% | 24 | 0 | 1.8379 | 10.5098 | NO
[11 empty] | 2022-10-11 | 97.45% | 2.066% |  | 0.4762% | 0.00494% | 24 | 0 | 1.9912 | 10.3901 | NO
[11 empty] | 2022-10-12 | 96.91% | 2.601% |  | 0.4771% | 0.009961% | 24 | 0 | 2.2056 | 10.4998 | NO
[11 empty] | 2022-10-13 | 97.35% | 2.138% |  | 0.5093% | 0.004124% | 24 | 0 | 1.5436 | 10.409 | NO
[11 empty] | 2022-10-14 | 96.51% | 2.918% |  | 0.5707% | 0.002037% | 24 | 0 | 1.5661 | 10.5644 | NO
[11 empty] | 2022-10-15 | 97.24% | 2.238% |  | 0.5191% | 0.007067% | 24 | 0 | 1.9752 | 10.4323 | NO
[11 empty] | 2022-10-16 | 96.92% | 2.528% |  | 0.552% | 0.001805% | 24 | 0 | 1.534 | 10.4886 | NO
[11 empty] | 2022-10-17 | 93.92% | 1.415% |  | 4.656% | 0.004944% | 24 | 0 | 1.3055 | 10.0523 | NO
[11 empty] | 2022-10-18 | 83.77% | 1.38% |  | 14.85% | 0.004223% | 24 | 0 | 1.8372 | 9.5404 | NO
[11 empty] | 2022-10-19 | 79.12% | 1.812% |  | 19.06% | 0.006121% | 24 | 0 | 1.9294 | 9.4125 | NO
[11 empty] | 2022-10-20 | 88.02% | 1.536% |  | 10.43% | 0.0149% | 24 | 0 | 1.3419 | 9.7932 | NO
[11 empty] | 2022-10-21 | 92.96% | 2.08% |  | 4.948% | 0.01349% | 24 | 0 | 1.3264 | 10.1823 | NO
[11 empty] | 2022-10-22 | 97.74% | 1.689% |  | 0.5641% | 0.005514% | 24 | 0 | 0.99143 | 10.3081 | NO
[11 empty] | 2022-10-23 | 97.91% | 1.573% |  | 0.5072% | 0.007649% | 24 | 0 | 1.2471 | 10.2945 | NO
[11 empty] | 2022-10-24 | 97.75% | 1.744% |  | 0.4993% | 0.00867% | 24 | 0 | 1.4744 | 10.3271 | NO
[11 empty] | 2022-10-25 | 88.95% | 2.426% |  | 5.231% | 3.398% | 24 | 2 | 1.9844 | 11.5325 | NO
[11 empty] | 2022-10-26 | OFF
[11 empty] | 2022-10-27 | OFF
[11 empty] | 2022-10-28 | OFF
[11 empty] | 2022-10-29 | OFF
[11 empty] | 2022-10-30 | OFF
[11 empty] | 2022-10-31 | 88.8% | 11.05% |  | 0.1453% | 0.0105% | 24 | 0 | 1.665 | 10.5376 | NO
[11 empty] | 2022-11-01 | 91.77% | 7.358% |  | 0.8624% | 0.009007% | 24 | 0 | 2.1159 | 11.4603 | NO
[11 empty] | 2022-11-02 | 94.45% | 4.704% |  | 0.8305% | 0.01295% | 24 | 0 | 1.4511 | 10.9322 | NO
[11 empty] | 2022-11-03 | 95.29% | 3.813% |  | 0.8759% | 0.01811% | 24 | 0 | 1.9613 | 10.7453 | NO
[11 empty] | 2022-11-04 | 95.2% | 3.946% |  | 0.8498% | 0.006341% | 24 | 0 | 1.8307 | 10.7641 | NO
[11 empty] | 2022-11-05 | 94.39% | 4.812% |  | 0.7846% | 0.01102% | 24 | 0 | 1.8395 | 10.9264 | NO
[11 empty] | 2022-11-06 | 95.23% | 4.002% |  | 0.7658% | 0.003681% | 24 | 0 | 2.0002 | 10.7651 | NO
[11 empty] | 2022-11-07 | 96.47% | 2.763% |  | 0.7625% | 0.007154% | 24 | 0 | 2.1689 | 10.5165 | NO
[11 empty] | 2022-11-08 | 86.2% | 11.49% |  | 1.431% | 0.8808% | 24 | 0 | 0 | 11.5395 | NO
[11 empty] | 2022-11-09 | 94.01% | 5.158% |  | 0.8222% | 0.009126% | 24 | 0 | 1.931 | 11.0118 | NO
[11 empty] | 2022-11-10 | 94.84% | 4.31% |  | 0.8413% | 0.01129% | 24 | 0 | 1.8528 | 10.8635 | NO
[11 empty] | 2022-11-11 | 88.95% | 8.595% |  | 2.443% | 0.01518% | 24 | 0 | 1.3111 | 11.6715 | NO
[11 empty] | 2022-11-12 | 78.12% | 8.432% |  | 13.44% | 0.0089% | 24 | 0 | 1.4643 | 11.0222 | NO
[11 empty] | 2022-11-13 | 96.63% | 2.861% |  | 0.5042% | 0.002029% | 24 | 0 | 1.2262 | 10.555 | NO
[11 empty] | 2022-11-14 | 96.15% | 3.423% |  | 0.4183% | 0.009681% | 24 | 0 | 1.3265 | 10.6437 | NO
[11 empty] | 2022-11-15 | 97.1% | 2.362% |  | 0.5378% | 0.004229% | 24 | 0 | 2.5224 | 10.445 | NO
[11 empty] | 2022-11-16 | 96.09% | 3.129% |  | 0.7682% | 0.008549% | 24 | 0 | 1.6513 | 10.6321 | NO
[11 empty] | 2022-11-17 | 97.14% | 2.358% |  | 0.5026% | 0.003891% | 24 | 0 | 1.58 | 10.4524 | NO
[11 empty] | 2022-11-18 | 97.59% | 1.876% |  | 0.5322% | 0.0005054% | 24 | 0 | 1.5974 | 10.3517 | NO
[11 empty] | 2022-11-19 | 97.98% | 1.51% |  | 0.5022% | 0.003122% | 24 | 0 | 1.6806 | 10.2778 | NO
[11 empty] | 2022-11-20 | 97.23% | 2.159% |  | 0.6113% | 0.003593% | 24 | 0 | 1.5908 | 10.4024 | NO
[11 empty] | 2022-11-21 | 97.73% | 1.715% |  | 0.5502% | 0.003247% | 24 | 0 | 2.1505 | 10.3234 | NO
[11 empty] | 2022-11-22 | 96.69% | 2.238% |  | 1.064% | 0.005228% | 24 | 0 | 1.5962 | 10.4053 | NO
[11 empty] | 2022-11-23 | 97.65% | 1.723% |  | 0.621% | 0.003357% | 23 | 0 | 3.1726 | 10.3261 | NO
[11 empty] | 2022-11-24 | 96.18% | 3.22% |  | 0.597% | 0.003906% | 24 | 0 | 1.5945 | 10.6286 | NO
[11 empty] | 2022-11-25 | 95.96% | 3.523% |  | 0.5014% | 0.01162% | 24 | 0 | 1.5975 | 10.6908 | NO
[11 empty] | 2022-11-26 | 96.31% | 3.201% |  | 0.4835% | 0.001825% | 24 | 0 | 1.3656 | 10.623 | NO
[11 empty] | 2022-11-27 | 96.54% | 2.987% |  | 0.4662% | 0.004616% | 24 | 0 | 1.6611 | 10.5767 | NO
[11 empty] | 2022-11-28 | 79.85% | 3.897% |  | 15.06% | 1.198% | 24 | 1 | 2.0117 | 10.7487 | NO
[11 empty] | 2022-11-29 | 24.43% | 12.24% |  | 34.66% | 28.67% | 24 | 19 | 5.5455 | 22.9176 | NO
[11 empty] | 2022-11-30 | 75.66% | 2.018% |  | 22.32% | 0.005439% | 24 | 0 | 2.7997 | 9.3094 | NO
[11 empty] | 2022-12-01 | 81.42% | 1.095% |  | 17.48% | 0.002136% | 24 | 0 | 2.8425 | 9.3415 | NO
[11 empty] | 2022-12-02 | 92.79% | 2.373% |  | 4.835% | 0.001092% | 24 | 0 | 1.6584 | 10.2256 | NO
[11 empty] | 2022-12-03 | 96.17% | 3.351% |  | 0.4774% | 0.002296% | 24 | 0 | 1.5632 | 10.6479 | NO
[11 empty] | 2022-12-04 | 95.4% | 3.998% |  | 0.595% | 0.002617% | 24 | 0 | 1.8327 | 10.7732 | NO
[11 empty] | 2022-12-05 | 95.7% | 3.694% |  | 0.6014% | 0.005125% | 24 | 0 | 1.6383 | 10.7219 | NO
[11 empty] | 2022-12-06 | 96.47% | 2.933% |  | 0.5882% | 0.00556% | 24 | 0 | 1.6366 | 10.5736 | NO
[11 empty] | 2022-12-07 | 96.26% | 2.945% |  | 0.7892% | 0.003953% | 24 | 0 | 1.7362 | 10.5952 | NO
[11 empty] | 2022-12-08 | 95.39% | 3.8% |  | 0.8078% | 0.005645% | 24 | 0 | 0 | 8.3756 | NO
[11 empty] | 2022-12-09 | 96.18% | 2.799% |  | 1.021% | 0.002083% | 24 | 0 | 2.1801 | 10.6151 | NO
[11 empty] | 2022-12-10 | 95.08% | 0.3859% |  | 4.535% | 0.001883% | 24 | 0 | 1.8694 | 9.8548 | NO
[11 empty] | 2022-12-11 | 94.37% | 0.3311% |  | 5.298% | 0.0004671% | 24 | 0 | 1.8677 | 9.8019 | NO
[11 empty] | 2022-12-12 | 93.23% | 0.5729% |  | 6.196% | 0.001333% | 24 | 0 | 1.9884 | 9.8068 | NO
[11 empty] | 2022-12-13 | 88.65% | 1.23% |  | 10.12% | 0.006722% | 24 | 0 | 2.4039 | 9.7609 | NO
[11 empty] | 2022-12-14 | 91.08% | 1.173% |  | 7.737% | 0.006014% | 24 | 0 | 1.9961 | 9.8632 | NO
[11 empty] | 2022-12-15 | 91.64% | 1.36% |  | 7.001% | 0.0005385% | 24 | 0 | 2.0746 | 9.9306 | NO
[11 empty] | 2022-12-16 | 91.8% | 1.741% |  | 6.454% | 0.005257% | 24 | 0 | 2.0624 | 10.04 | NO
[11 empty] | 2022-12-17 | 91.43% | 4.501% |  | 4.066% | 0.006978% | 24 | 0 | 2.2105 | 10.6172 | NO
[11 empty] | 2022-12-18 | 93.17% | 5.9% |  | 0.9229% | 0.007816% | 24 | 0 | 2.0886 | 11.2336 | NO
[11 empty] | 2022-12-19 | 93.52% | 5.765% |  | 0.7005% | 0.01291% | 24 | 0 | 1.3551 | 11.1631 | NO
[11 empty] | 2022-12-20 | 97.26% | 2.2% |  | 0.5347% | 0.001955% | 24 | 0 | 1.6044 | 10.4265 | NO
[11 empty] | 2022-12-21 | 96.1% | 3.108% |  | 0.7864% | 0.00687% | 24 | 0 | 2.0209 | 10.6276 | NO
[11 empty] | 2022-12-22 | 95.66% | 3.848% |  | 0.4851% | 0.00735% | 24 | 0 | 1.4942 | 10.749 | NO
[11 empty] | 2022-12-23 | 93.66% | 3.173% |  | 3.167% | 0.003953% | 24 | 0 | 2.0044 | 10.4916 | NO
[11 empty] | 2022-12-24 | 96.79% | 2.707% |  | 0.5011% | 0.005223% | 24 | 0 | 1.5186 | 10.519 | NO
[11 empty] | 2022-12-25 | 96.79% | 2.701% |  | 0.4967% | 0.007756% | 24 | 0 | 1.2397 | 10.5185 | NO
[11 empty] | 2022-12-26 | 97.9% | 1.568% |  | 0.5294% | 0.003144% | 24 | 0 | 1.7875 | 10.284 | NO
[11 empty] | 2022-12-27 | 97.2% | 2.293% |  | 0.5016% | 0.004038% | 24 | 0 | 1.8845 | 10.4362 | NO
[11 empty] | 2022-12-28 | 97.84% | 1.655% |  | 0.5052% | 0.004576% | 24 | 0 | 1.8707 | 10.3072 | NO
[11 empty] | 2022-12-29 | 97.75% | 1.656% |  | 0.5814% | 0.01177% | 24 | 0 | 2.1253 | 10.294 | NO
[11 empty] | 2022-12-30 | 88.2% | 2.909% |  | 8.883% | 0.009417% | 24 | 0 | 2.5381 | 10.1548 | NO
[11 empty] | 2022-12-31 | 93.44% | 5.539% |  | 1.007% | 0.01513% | 24 | 0 | 2.4416 | 11.1225 | NO
[11 empty] | 0 | 95.9% | 3.61% | 0.48% | 0.01% | 0.006667% | 24 | 0 | 1.4 | 10.7 | NO
[11 empty] | 0 | 92.76% | 5.789% |  | 1.444% | 0.004511% | 24 | 0 | 2.1552 | 11.1145 | NO

## A62 Boiler 3
|  | Concentrations in mg/m³ at reference conditions after subtracting uncertainty | [9 empty] | Daily means, excluding hours outside normal operating conditions
|  | 2022-10-01 |  |  | 2022-11-01 |  |  | 2022-12-01 |  |  | Date | Fuel mix |  |  |  |  | Particulate Matter concentration (mg/m³) after subtracting uncertainty |  |  |  |  | Sulphur dioxide concentration (mg/m³) after subtracting uncertainty |  |  |  |  | Oxides of nitrogen concentration (mg/m³) after subtracting uncertainty
|  | PM | SO2 | NOx | PM | SO2 | NOx | PM | SO2 | NOx |  | % BFG | % COG | % BOSg | % NG | % HFO | No.valid hours | No.hours OTNOC | Measured | Limit | Breach? | No.valid hours | No.hours OTNOC | Measured | Limit | Breach? | No.valid hours | No.hours OTNOC | Measured | Limit | Breach?
Daily means | Minimum | 1.8574 | 20.5876 | Monitor out of calibration (Part A - S5N_21_76A) | 6.4973 | 71.0555 | Monitor out of calibration (Part A - S5N_21_76A) | 1.4214 | 28.5938 | Monitor out of calibration (Part A - S5N_21_76A) | 2022-10-01 | OFF
| Maximum | 10.4294 | 49.4693 |  | 14.6057 | 242.4144 |  | 4.8535 | 54.0578 |  | 2022-10-02 | OFF
| No. > Limit | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 2022-10-03 | OFF
Monthly mean |  | 4.4969 | 36.0626 |  | 2.6458 | 35.9861 |  | 2.3795 | 37.4173 |  | 2022-10-04 | OFF
Monthly mean limit |  | 9.7988 | 180.0283 | 195.6869 | 11.196 | 204.6555 | 204.9525 | 10.6782 | 204.4846 | 209.3114 | 2022-10-05 | OFF
[11 empty] | 2022-10-06 | OFF
[11 empty] | 2022-10-07 | OFF
[11 empty] | 2022-10-08 | OFF
[11 empty] | 2022-10-09 | OFF
[11 empty] | 2022-10-10 | OFF
[11 empty] | 2022-10-11 | OFF
[11 empty] | 2022-10-12 | OFF
[11 empty] | 2022-10-13 | OFF
[11 empty] | 2022-10-14 | OFF
[11 empty] | 2022-10-15 | OFF
[11 empty] | 2022-10-16 | OFF
[11 empty] | 2022-10-17 | OFF
[11 empty] | 2022-10-18 | OFF
[11 empty] | 2022-10-19 | OFF
[11 empty] | 2022-10-20 | OFF
[11 empty] | 2022-10-21 | OFF
[11 empty] | 2022-10-22 | OFF
[11 empty] | 2022-10-23 | OFF
[11 empty] | 2022-10-24 | OFF
[11 empty] | 2022-10-25 | OFF
[11 empty] | 2022-10-26 | OFF
[11 empty] | 2022-10-27 | 43.23% | 0.1087% |  | 56.66% |  | 24 | 15 | 4.1592 | 7.9078 | NO | 24 | 15 | 34.4756 | 117.4074 | NO | 24 | 15 |  | 157.6777 | NO
[11 empty] | 2022-10-28 | 99.81% | 0.02871% |  | 0.1581% |  | 21 | 0 | 10.4294 | 10.9976 | NO | 24 | 0 | 49.4693 | 219.7762 | NO | 24 | 0 |  | 219.8261 | NO
[11 empty] | 2022-10-29 | 99.88% | 0.04241% |  | 0.0729% |  | 24 | 0 | 3.3271 | 11.0053 | NO | 24 | 0 | 41.6272 | 219.961 | NO | 24 | 0 |  | 219.9198 | NO
[11 empty] | 2022-10-30 | 73.54% | 0.04862% |  | 26.41% |  | 24 | 8 | 1.8574 | 9.5583 | NO | 24 | 8 | 34.1533 | 172.1784 | NO | 24 | 8 |  | 190.9524 | NO
[11 empty] | 2022-10-31 | 72.68% | 0.1009% |  | 27.22% |  | 24 | 7 | 2.7113 | 9.5251 | NO | 24 | 7 | 20.5876 | 170.8185 | NO | 24 | 7 |  | 190.0585 | NO
[11 empty] | 2022-11-01 | 12.61% | 0.06168% |  | 87.33% |  | 22 | 24 |  |  |  | 22 | 24 |  |  |  | 22 | 24
[11 empty] | 2022-11-02 | 70.29% | 0.1751% |  | 29.53% |  | 24 | 7 | 4.5117 | 9.4143 | NO | 24 | 7 | 20.4327 | 166.7855 | NO | 24 | 7 |  | 187.5152 | NO
[11 empty] | 2022-11-03 | 98.62% | 1.134% |  | 0.2473% |  | 24 | 0 | 2.5633 | 11.2359 | NO | 24 | 0 | 29.2643 | 222.0462 | NO | 24 | 0 |  | 219.728 | NO
[11 empty] | 2022-11-04 | 95.16% | 4.715% |  | 0.1298% |  | 24 | 0 | 2.2389 | 12.0301 | NO | 24 | 0 | 49.6268 | 230.1371 | NO | 24 | 0 |  | 219.8572 | NO
[11 empty] | 2022-11-05 | 94.73% | 5.153% |  | 0.1158% |  | 24 | 0 | 1.7171 | 12.1274 | NO | 24 | 0 | 39.4376 | 231.1273 | NO | 24 | 0 |  | 219.8726 | NO
[11 empty] | 2022-11-06 | 99.54% | 0.3628% |  | 0.095% |  | 24 | 0 | 1.6059 | 11.0746 | NO | 24 | 0 | 31.9133 | 220.6257 | NO | 24 | 0 |  | 219.8955 | NO
[11 empty] | 2022-11-07 | 80.21% | 0.5237% |  | 19.27% |  | 24 | 5 | 2.2871 | 10.0555 | NO | 24 | 5 | 24.0854 | 186.1803 | NO | 24 | 5 |  | 198.805 | NO
[11 empty] | 2022-11-08 | 39.85% | 2.05% |  | 58.1% |  | 24 | 16 | 5.0895 | 8.2554 | NO | 24 | 16 | 12.7914 | 119.058 | NO | 24 | 16 |  | 156.0903 | NO
[11 empty] | 2022-11-09 | 87.06% | 0.3806% |  | 12.56% |  | 24 | 3 | 3.299 | 10.3928 | NO | 24 | 3 | 23.8329 | 198.0354 | NO | 24 | 3 |  | 206.1807 | NO
[11 empty] | 2022-11-10 | 98.98% | 0.8598% |  | 0.1604% |  | 24 | 0 | 2.4921 | 11.1803 | NO | 24 | 0 | 32.277 | 221.6004 | NO | 24 | 0 |  | 219.8235 | NO
[11 empty] | 2022-11-11 | 20.4% | 26.97% |  | 52.63% |  | 24 | 21 | 3.5465 | 14.0386 | NO | 24 | 21 | 46.1879 | 183.8107 | NO | 24 | 21 |  | 162.1088 | NO
[11 empty] | 2022-11-12 | 8.301% | 31.45% |  | 60.25% |  | 24 | 24 | 5.0061 | 14.6057 | NO | 24 | 24 | 59.6579 | 179.8435 | NO | 24 | 24 |  | 153.7274 | NO
[11 empty] | 2022-11-13 | 81.45% | 13.97% |  | 4.583% |  | 24 | 2 | 2.8872 | 13.8212 | NO | 24 | 2 | 56.6127 | 242.4144 | NO | 24 | 2 |  | 214.9586 | NO
[11 empty] | 2022-11-14 | 96.4% | 3.499% |  | 0.09757% |  | 24 | 0 | 3.283 | 11.7645 | NO | 24 | 0 | 39.3375 | 227.5215 | NO | 24 | 0 |  | 219.8927 | NO
[11 empty] | 2022-11-15 | 99.92% | 0.02867% |  | 0.04694% |  | 24 | 0 | 1.3046 | 11.0037 | NO | 24 | 0 | 50.3447 | 219.9779 | NO | 24 | 0 |  | 219.9484 | NO
[11 empty] | 2022-11-16 | 95.87% | 0.5377% |  | 3.591% |  | 24 | 0 | 2.4393 | 10.9208 | NO | 24 | 0 | 29.5071 | 214.6653 | NO | 24 | 0 |  | 216.0498 | NO
[11 empty] | 2022-11-17 | 99.81% | 0.03116% |  | 0.1553% |  | 24 | 0 | 1.3405 | 10.9983 | NO | 24 | 0 | 31.7914 | 219.7867 | NO | 24 | 0 |  | 219.8292 | NO
[11 empty] | 2022-11-18 | 99.89% | 0.00537% |  | 0.1039% |  | 24 | 0 | 1.3634 | 10.9955 | NO | 24 | 0 | 42.5309 | 219.8232 | NO | 24 | 0 |  | 219.8857 | NO
[11 empty] | 2022-11-19 | 99.88% | 0.03409% |  | 0.09052% |  | 24 | 0 | 1.2904 | 11.0025 | NO | 24 | 0 | 39.466 | 219.9107 | NO | 24 | 0 |  | 219.9004 | NO
[11 empty] | 2022-11-20 | 99.87% | 0.02701% |  | 0.09994% |  | 24 | 0 | 1.131 | 11.0004 | NO | 24 | 0 | 41.8827 | 219.878 | NO | 24 | 0 |  | 219.8901 | NO
[11 empty] | 2022-11-21 | 99.3% | 0.6335% |  | 0.0664% |  | 24 | 0 | 3.2692 | 11.1357 | NO | 24 | 0 | 38.7509 | 221.2732 | NO | 24 | 0 |  | 219.927 | NO
[11 empty] | 2022-11-22 | 96.46% | 1.187% |  | 2.355% |  | 24 | 0 | 1.9464 | 11.1317 | NO | 24 | 0 | 28.5612 | 218.3376 | NO | 24 | 0 |  | 217.4093 | NO
[11 empty] | 2022-11-23 | 94.39% | 0.7896% |  | 4.824% |  | 24 | 0 | 2.7238 | 10.9084 | NO | 24 | 0 | 34.2324 | 212.9823 | NO | 24 | 0 |  | 214.694 | NO
[11 empty] | 2022-11-24 | 97.1% | 0.08193% |  | 2.817% |  | 24 | 0 | 2.21 | 10.8631 | NO | 24 | 0 | 34.6603 | 215.0675 | NO | 24 | 0 |  | 216.9014 | NO
[11 empty] | 2022-11-25 | 99.84% | 0.08809% |  | 0.07593% |  | 24 | 0 | 2.1911 | 11.0152 | NO | 24 | 0 | 35.0993 | 220.056 | NO | 24 | 0 |  | 219.9165 | NO
[11 empty] | 2022-11-26 | 99.43% | 0.5406% |  | 0.03264% |  | 24 | 0 | 1.573 | 11.1171 | NO | 24 | 0 | 42.511 | 221.13 | NO | 24 | 0 |  | 219.9641 | NO
[11 empty] | 2022-11-27 | 92.49% | 7.463% |  | 0.04306% |  | 24 | 0 | 1.1108 | 12.6395 | NO | 24 | 0 | 43.6277 | 236.341 | NO | 24 | 0 |  | 219.9526 | NO
[11 empty] | 2022-11-28 | 33.25% | 17.94% |  | 48.81% |  | 24 | 18 | 3.4297 | 12.2629 | NO | 24 | 18 | 37.9456 | 170.8832 | NO | 24 | 18 |  | 166.3082 | NO
[11 empty] | 2022-11-29 | 11.5% | 3.006% |  | 85.49% |  | 24 | 24 |  |  |  | 24 | 24 |  |  |  | 24 | 24
[11 empty] | 2022-11-30 | 17.78% | 0.07038% |  | 82.15% |  | 24 | 22 | 6.2314 | 6.4973 | NO | 24 | 22 | 11.2416 | 71.0555 | NO | 24 | 22 |  | 129.6368 | NO
[11 empty] | 2022-12-01 | 87.73% | 0.06288% |  | 12.21% |  | 24 | 0 | 2.5457 | 10.3424 | NO | 24 | 0 | 23.5579 | 197.982 | NO | 24 | 0 |  | 206.5719 | NO
[11 empty] | 2022-12-02 | 99.8% | 0.03585% |  | 0.165% |  | 24 | 0 | 2.3323 | 10.9988 | NO | 24 | 0 | 45.6607 | 219.7794 | NO | 24 | 0 |  | 219.8185 | NO
[11 empty] | 2022-12-03 | 99.93% | 0% |  | 0.07026% |  | 24 | 0 | 1.479 | 10.9961 | NO | 24 | 0 | 54.0578 | 219.8725 | NO | 24 | 0 |  | 219.9227 | NO
[11 empty] | 2022-12-04 | 99.89% | 0% |  | 0.1079% |  | 24 | 0 | 1.5062 | 10.9941 | NO | 24 | 0 | 51.2716 | 219.8042 | NO | 24 | 0 |  | 219.8813 | NO
[11 empty] | 2022-12-05 | 99.92% | 0.0009062% |  | 0.07577% |  | 24 | 0 | 1.4214 | 10.996 | NO | 24 | 0 | 49.5903 | 219.8645 | NO | 24 | 0 |  | 219.9167 | NO
[11 empty] | 2022-12-06 | 98.22% | 0.02903% |  | 1.748% |  | 24 | 0 | 1.8972 | 10.9103 | NO | 24 | 0 | 49.966 | 216.8917 | NO | 24 | 0 |  | 218.0774 | NO
[11 empty] | 2022-12-07 | 95.65% | 0.03339% |  | 4.312% |  | 24 | 0 | 1.8106 | 10.7702 | NO | 24 | 0 | 34.6228 | 212.247 | NO | 24 | 0 |  | 215.2567 | NO
[11 empty] | 2022-12-08 | 56.11% | 0.5032% |  | 43.38% |  | 24 | 10 | 3.4737 | 8.7246 | NO | 24 | 10 | 32.7899 | 142.3649 | NO | 24 | 10 |  | 172.2775 | NO
[11 empty] | 2022-12-09 | 93.62% | 0.04168% |  | 6.341% |  | 24 | 1 | 1.8509 | 10.6604 | NO | 24 | 1 | 29.3454 | 208.5825 | NO | 24 | 1 |  | 213.0247 | NO
[11 empty] | 2022-12-10 | 99.87% | 0.03384% |  | 0.0948% |  | 24 | 0 | 1.4963 | 11.0022 | NO | 24 | 0 | 42.0595 | 219.9024 | NO | 24 | 0 |  | 219.8957 | NO
[11 empty] | 2022-12-11 | 99.88% | 0.02652% |  | 0.0889% |  | 24 | 0 | 1.5378 | 11.0009 | NO | 24 | 0 | 44.0535 | 219.897 | NO | 24 | 0 |  | 219.9022 | NO
[11 empty] | 2022-12-12 | 99.82% | 0.04061% |  | 0.1345% |  | 24 | 0 | 2.0014 | 11.0015 | NO | 24 | 0 | 39.2401 | 219.8453 | NO | 24 | 0 |  | 219.8521 | NO
[11 empty] | 2022-12-13 | 49.87% | 0.05458% |  | 50.08% |  | 24 | 10 | 3.2282 | 8.2578 | NO | 24 | 10 | 32.6294 | 129.2314 | NO | 24 | 10 |  | 164.9159 | NO
[11 empty] | 2022-12-14 | 94.33% | 0.05798% |  | 5.608% |  | 24 | 0 | 4.2274 | 10.7043 | NO | 24 | 0 | 34.5733 | 209.9486 | NO | 24 | 0 |  | 213.831 | NO
[11 empty] | 2022-12-15 | 97.42% | 0.05207% |  | 2.524% |  | 24 | 0 | 3.1921 | 10.8727 | NO | 24 | 0 | 33.1721 | 215.534 | NO | 24 | 0 |  | 217.2239 | NO
[11 empty] | 2022-12-16 | 69.7% | 0.03424% |  | 30.27% |  | 24 | 6 | 4.8535 | 9.3427 | NO | 24 | 6 | 28.5938 | 165.1349 | NO | 24 | 6 |  | 186.7028 | NO
[11 empty] | 2022-12-17 | 60.64% | 0.198% |  | 39.16% |  | 24 | 9 | 2.2613 | 8.8896 | NO | 24 | 9 | 38.7438 | 149.355 | NO | 24 | 9 |  | 176.9208 | NO
[11 empty] | 2022-12-18 | 94.53% | 0.007444% |  | 5.462% |  | 24 | 0 | 2.0199 | 10.7012 | NO | 24 | 0 | 40.7649 | 210.1029 | NO | 24 | 0 |  | 213.9919 | NO
[11 empty] | 2022-12-19 | 90.2% | 0.04892% |  | 9.753% |  | 24 | 0 | 2.8703 | 10.4744 | NO | 24 | 0 | 30.1701 | 202.4064 | NO | 24 | 0 |  | 209.272 | NO
[11 empty] | 2022-12-20 | 99.8% | 0.0677% |  | 0.1321% |  | 24 | 0 | 1.4718 | 11.0076 | NO | 24 | 0 | 26.3501 | 219.9092 | NO | 24 | 0 |  | 219.8547 | NO
[11 empty] | 2022-12-21 | 99.34% | 0.3182% |  | 0.3459% |  | 24 | 0 | 3.1701 | 11.051 | NO | 24 | 0 | 20.0044 | 220.0722 | NO | 24 | 0 |  | 219.6195 | NO
[11 empty] | 2022-12-22 | 99.2% | 0.7399% |  | 0.0632% |  | 24 | 0 | 2.1165 | 11.1593 | NO | 24 | 0 | 32.6596 | 221.513 | NO | 24 | 0 |  | 219.9305 | NO
[11 empty] | 2022-12-23 | 91.83% | 0.2923% |  | 7.875% |  | 24 | 0 | 1.5863 | 10.6312 | NO | 24 | 0 | 27.4703 | 206.35 | NO | 24 | 0 |  | 211.3375 | NO
[11 empty] | 2022-12-24 | 93.52% | 1.386% |  | 5.095% |  | 24 | 0 | 1.8751 | 11.0248 | NO | 24 | 0 | 41.5043 | 213.8021 | NO | 24 | 0 |  | 214.3951 | NO
[11 empty] | 2022-12-25 | 93.92% | 6.027% |  | 0.05778% |  | 24 | 0 | 1.6142 | 12.3227 | NO | 24 | 0 | 45.7649 | 233.1539 | NO | 24 | 0 |  | 219.9364 | NO
[11 empty] | 2022-12-26 | 98.34% | 1.548% |  | 0.1132% |  | 24 | 0 | 1.5812 | 11.3344 | NO | 24 | 0 | 45.8849 | 223.2011 | NO | 24 | 0 |  | 219.8755 | NO
[11 empty] | 2022-12-27 | 99.87% | 0.01541% |  | 0.1118% |  | 24 | 0 | 1.4489 | 10.9972 | NO | 24 | 0 | 48.8937 | 219.8309 | NO | 24 | 0 |  | 219.877 | NO
[11 empty] | 2022-12-28 | 99.91% | 0.03412% |  | 0.05129% |  | 24 | 0 | 1.2884 | 11.0047 | NO | 24 | 0 | 42.6508 | 219.982 | NO | 24 | 0 |  | 219.9436 | NO
[11 empty] | 2022-12-29 | 99.85% | 0.04077% |  | 0.1097% |  | 24 | 0 | 1.4088 | 11.0029 | NO | 24 | 0 | 39.3816 | 219.8907 | NO | 24 | 0 |  | 219.8794 | NO
[11 empty] | 2022-12-30 | 55.81% | 8.629% |  | 35.56% |  | 24 | 11 | 1.7065 | 10.9426 | NO | 24 | 11 | 37.13 | 174.4458 | NO | 24 | 11 |  | 180.8864 | NO
[11 empty] | 0 | 69.81% | 5.255% |  |  |  | 24 | 6 | 4.4247 | 10.7848 | NO | 24 | 6 | 27.3949 | 186.309 | NO | 24 | 6 |  | 192.5745 | NO
[11 empty] | 0 | [5 empty] | 24 |  | 4.4247 |  | YES | 24 |  |  |  | NO | 24 |  |  |  | NO
[11 empty] | 2022-12-31 | 69.81% | 5.255% |  | 24.93% |  | 24 | 6 | 4.4 | 10.8 | NO | 24 | 6 | 27.4 | 186.3 | NO | 24 | 6 |  | 192.6 | NO

## A52A Boiler 6
|  | Concentrations in mg/m³ at reference conditions after subtracting uncertainty | [9 empty] | Daily means, excluding hours outside normal operating conditions
|  | 2022-10-01 |  |  | 2022-11-01 |  |  | 2022-12-01 |  |  | Date | Fuel mix |  |  |  |  | Particulate Matter concentration (mg/m³) after subtracting uncertainty |  |  |  |  | Sulphur dioxide concentration (mg/m³) after subtracting uncertainty |  |  |  |  | Oxides of nitrogen concentration (mg/m³) after subtracting uncertainty
|  | PM | SO2 | NOx | PM | SO2 | NOx | PM | SO2 | NOx |  | % BFG | % COG | % BOSg | % NG | % HFO | No.valid hours | No.hours OTNOC | Measured | Limit | Breach? | No.valid hours | No.hours OTNOC | Measured | Limit | Breach? | No.valid hours | No.hours OTNOC | Measured | Limit | Breach?
Daily means | Minimum | 1.2502 | 36.0953 | 39.7235 | 1.3875 | 30.1596 | 34.406 | 1.3678 | 24.5082 | 36.8948 | 2022-10-01 | 87.69% | 10.02% | 1.09% | 1.203% | 0% | 24 | 0 | 2.2908 | 13.3764 | NO | 24 | 0 | 59.5407 | 239.8554 | NO | 24 | 0 | 44.9956 | 327.3449 | NO
| Maximum | 2.8655 | 81.1408 | 135.1357 | 2.1156 | 82.8822 | 92.2521 | 2.3713 | 72.6187 | 78.2464 | 2022-10-02 | 79.95% | 11.62% | 1.984% | 6.451% | 0.001236% | 24 | 2 | 2.8655 | 13.4237 | NO | 24 | 2 | 53.1584 | 232.7186 | NO | 24 | 2 | 78.2766 | 314.0954 | NO
| No. > Limit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2022-10-03 | 81.86% | 10.05% | 1.645% | 6.448% | 0% | 24 | 2 | 1.8925 | 13.0822 | NO | 24 | 2 | 49.5295 | 229.6046 | NO | 24 | 2 | 66.9579 | 314.7228 | NO
Monthly mean |  | 1.9239 | 56.3947 | 66.3115 | 1.747 | 51.4429 | 60.407 | 1.8702 | 51.4477 | 52.7601 | 2022-10-04 | 80.31% | 12.17% | 1.088% | 6.43% | 0% | 24 | 0 | 1.808 | 13.5751 | NO | 24 | 0 | 60.196 | 235.225 | NO | 24 | 0 | 72.2306 | 315.9429 | NO
Monthly mean limit |  | 14.8525 | 230.5774 | 311.9651 | 16.0241 | 229.4246 | 310.2601 | 14.6298 | 219.0245 | 303.2348 | 2022-10-05 | 83.34% | 12.94% | 1.101% | 2.611% | 0% | 24 | 0 | 1.9889 | 13.9435 | NO | 24 | 0 | 62.4288 | 243.7579 | NO | 24 | 0 | 49.7627 | 324.2349 | NO
[11 empty] | 2022-10-06 | 87.47% | 10.11% | 1.171% | 1.248% | 0% | 24 | 0 | 2.0093 | 13.4004 | NO | 24 | 0 | 59.2888 | 240.0567 | NO | 24 | 0 | 50.0123 | 327.1558 | NO
[11 empty] | 2022-10-07 | 84.23% | 9.84% | 1.914% | 4.013% | 0% | 24 | 0 | 1.9457 | 13.1954 | NO | 24 | 0 | 54.0808 | 233.6303 | NO | 24 | 0 | 56.1037 | 319.8154 | NO
[11 empty] | 2022-10-08 | 63.98% | 12.22% | 1.703% | 16.83% | 5.268% | 24 | 5 | 2.1467 | 13.9355 | NO | 24 | 5 | 51.8141 | 219.2429 | NO | 24 | 5 | 63.7756 | 286.4704 | NO
[11 empty] | 2022-10-09 | 78.47% | 13.35% | 1.432% | 6.754% | 0% | 24 | 0 | 1.8318 | 13.8184 | NO | 24 | 0 | 74.633 | 236.9415 | NO | 24 | 0 | 61.5088 | 314.6495 | NO
[11 empty] | 2022-10-10 | 65.18% | 20.3% | 2.831% | 11.69% | 0% | 24 | 5 | 1.9803 | 15.1773 | NO | 24 | 5 | 58.7352 | 243.1205 | NO | 24 | 5 | 97.7664 | 302.1267 | NO
[11 empty] | 2022-10-11 | 81.82% | 13.88% | 1.134% | 3.165% | 0% | 24 | 0 | 2.1406 | 14.1292 | NO | 24 | 0 | 62.6433 | 244.8852 | NO | 24 | 0 | 50.6768 | 323.0432 | NO
[11 empty] | 2022-10-12 | 81.26% | 12.37% | 2.229% | 4.14% | 0% | 24 | 0 | 1.8949 | 14.0383 | NO | 24 | 0 | 57.3044 | 240.2319 | NO | 24 | 0 | 56.484 | 321.3317 | NO
[11 empty] | 2022-10-13 | 79.59% | 9.582% | 9.491% | 1.334% | 0% | 24 | 0 | 1.7936 | 15.1204 | NO | 24 | 0 | 46.0727 | 238.756 | NO | 24 | 0 | 49.9476 | 327.046 | NO
[11 empty] | 2022-10-14 | 71.92% | 9.565% | 15.42% | 3.099% | 0% | 24 | 2 | 2.214 | 16.1888 | NO | 24 | 2 | 51.5229 | 234.7244 | NO | 24 | 2 | 41.4314 | 322.0825 | NO
[11 empty] | 2022-10-15 | 71.83% | 8.687% | 17.16% | 2.327% | 0% | 24 | 0 | 1.9513 | 16.4918 | NO | 24 | 0 | 46.8747 | 234.6649 | NO | 24 | 0 | 85.8145 | 324.3577 | NO
[11 empty] | 2022-10-16 | 67.86% | 11.47% | 17.8% | 2.877% | 0% | 24 | 2 | 2.1507 | 17.1592 | NO | 24 | 2 | 51.7316 | 240.1968 | NO | 24 | 2 | 98.4029 | 322.7071 | NO
[11 empty] | 2022-10-17 | 71.2% | 1.832% | 18.16% | 8.815% | 0% | 24 | 0 | 2.0065 | 14.8959 | NO | 24 | 0 | 53.2739 | 207.7577 | NO | 24 | 0 | 58.1571 | 310.4724 | NO
[11 empty] | 2022-10-18 | 59.96% | 0.5664% | 14.64% | 24.3% | 0.5309% | 24 | 2 | 1.4939 | 12.9314 | NO | 24 | 2 | 36.0953 | 176.4047 | NO | 24 | 2 | 68.3904 | 274.6136 | NO
[11 empty] | 2022-10-19 | 35.36% | 1.03% | 9.888% | 45.79% | 7.933% | 24 | 24
[11 empty] | 2022-10-20 | 61.98% | 1.216% | 7.187% | 28.25% | 1.37% | 24 | 4 | 2.765 | 11.2409 | NO | 24 | 4 | 67.0549 | 170.6384 | NO | 24 | 4 | 45.1679 | 263.879 | NO
[11 empty] | 2022-10-21 | 71.44% | 13.44% | 9.146% | 5.983% | 0% | 24 | 0 | 1.4756 | 15.6726 | NO | 24 | 0 | 63.4897 | 238.9227 | NO | 24 | 0 | 67.6053 | 317.1078 | NO
[11 empty] | 2022-10-22 | 78.06% | 12.42% | 8.547% | 0.973% | 0% | 24 | 0 | 1.599 | 15.5588 | NO | 24 | 0 | 59.8532 | 245.5942 | NO | 24 | 0 | 55.1397 | 327.8479 | NO
[11 empty] | 2022-10-23 | 78.56% | 12.34% | 7.463% | 1.636% | 0% | 24 | 0 | 1.7802 | 15.427 | NO | 24 | 0 | 56.6398 | 240.6629 | NO | 24 | 0 | 72.5464 | 327.6821 | NO
[11 empty] | 2022-10-24 | 74.98% | 10.51% | 13.74% | 0.7751% | 0% | 24 | 0 | 2.501 | 16.2894 | NO | 24 | 0 | 50.9179 | 241.444 | NO | 24 | 0 | 43.0887 | 328.2856 | NO
[11 empty] | 2022-10-25 | 39.49% | 19.22% | 3.315% | 30.9% | 3.245% | 24 | 18 | 1.5963 | 15.6367 | NO | 24 | 18 | 39.8997 | 208.1535 | NO | 24 | 18 | 135.1357 | 258.5047 | NO
[11 empty] | 2022-10-26 | 67.32% | 15.73% | 0% | 13.62% | 0% | 24 | 4 | 1.2502 | 14.6545 | NO | 24 | 4 | 53.4619 | 231.3105 | NO | 24 | 4 | 82.4787 | 301.7139 | NO
[11 empty] | 2022-10-27 | 57.67% | 11.76% | 0% | 17.64% | 0% | 24 | 7 | 1.5401 | 15.2437 | NO | 24 | 7 | 55.9778 | 212.9174 | NO | 24 | 7 | 76.7014 | 289.4436 | NO
[11 empty] | 2022-10-28 | 70.35% | 10.85% | 0% | 1.246% | 0% | 24 | 0 | 1.9278 | 17.1854 | NO | 24 | 0 | 51.3764 | 242.2869 | NO | 24 | 0 | 97.603 | 327.2909 | NO
[11 empty] | 2022-10-29 | 69.4% | 11.26% | 0% | 2.394% | 0% | 24 | 0 | 1.6755 | 17.0839 | NO | 24 | 0 | 63.7346 | 240.4464 | NO | 24 | 0 | 47.955 | 324.8212 | NO
[11 empty] | 2022-10-30 | 57.76% | 16.1% | 0% | 10.51% | 0% | 24 | 8 | 1.8041 | 17.1583 | NO | 24 | 8 | 81.1408 | 235.3931 | NO | 24 | 8 | 39.7235 | 304.923 | NO
[11 empty] | 2022-10-31 | 66.42% | 12.85% | 0% | 5.883% | 0% | 24 | 3 | 1.3966 | 16.542 | NO | 24 | 3 | 59.3702 | 237.777 | NO | 24 | 3 | 75.5036 | 315.2417 | NO
[11 empty] | 2022-11-01 | 70% | 13.28% | 8.858% | 7.861% | 0% | 24 | 0 | 1.3875 | 15.32 | NO | 24 | 0 | 54.764 | 234.6044 | NO | 24 | 0 | 92.2521 | 311.7551 | NO
[11 empty] | 2022-11-02 | 74.06% | 11.18% | 6.677% | 8.085% | 0% | 24 | 1 | 2.0154 | 14.4627 | NO | 24 | 1 | 82.8822 | 230.3989 | NO | 24 | 1 | 79.9622 | 312.0435 | NO
[11 empty] | 2022-11-03 | 73.14% | 7.108% | 11.85% | 7.899% | 0% | 24 | 0 | 1.7823 | 14.8337 | NO | 24 | 0 | 41.5603 | 222.17 | NO | 24 | 0 | 73.5732 | 313.4004 | NO
[11 empty] | 2022-11-04 | 71.94% | 9.476% | 16.82% | 1.767% | 0% | 24 | 0 | 1.7991 | 16.6902 | NO | 24 | 0 | 65.2081 | 237.2928 | NO | 24 | 0 | 38.3873 | 326.1342 | NO
[11 empty] | 2022-11-05 | 74% | 12.77% | 12.38% | 0.8531% | 0% | 24 | 0 | 1.6591 | 16.4819 | NO | 24 | 0 | 68.6493 | 246.5561 | NO | 24 | 0 | 58.808 | 328.0935 | NO
[11 empty] | 2022-11-06 | 73.26% | 11.33% | 14.72% | 0.6911% | 0% | 24 | 0 | 1.6288 | 16.6925 | NO | 24 | 0 | 64.6215 | 243.5069 | NO | 24 | 0 | 52.9827 | 328.4859 | NO
[11 empty] | 2022-11-07 | 62.54% | 16.76% | 13.97% | 6.725% | 0% | 24 | 5 | 1.5729 | 16.8843 | NO | 24 | 5 | 61.5574 | 243.0773 | NO | 24 | 5 | 49.1087 | 311.1443 | NO
[11 empty] | 2022-11-08 | 53.11% | 16.01% | 9.387% | 21.49% | 0% | 24 | 13 | 1.6024 | 15.0582 | NO | 24 | 13 | 51.3886 | 215.1196 | NO | 24 | 13 | 76.5175 | 279.9445 | NO
[11 empty] | 2022-11-09 | 76.97% | 9.665% | 8.09% | 5.275% | 0% | 24 | 0 | 1.6875 | 14.6201 | NO | 24 | 0 | 49.3986 | 231.9739 | NO | 24 | 0 | 59.0929 | 318.4284 | NO
[11 empty] | 2022-11-10 | 72.32% | 10.14% | 13.85% | 3.697% | 0% | 24 | 0 | 1.5976 | 18.3406 | NO | 24 | 0 | 46.7478 | 258.001 | NO | 24 | 0 | 69.3695 | 318.0319 | NO
[11 empty] | 2022-11-11 | OFF
[11 empty] | 2022-11-12 | OFF
[11 empty] | 2022-11-13 | OFF
[11 empty] | 2022-11-14 | 66.19% | 9.572% | -0.2448% | 24.48% | 0% | 24 | 0 | 1.7604 | 12.3187 | NO | 24 | 0 | 73.3899 | 148.3407 | NO | 24 | 0 | 34.406 | 221.4217 | NO
[11 empty] | 2022-11-15 | 74.71% | 8.061% | 14.85% | 2.383% | 0% | 24 | 0 | 1.7763 | 15.9251 | NO | 24 | 0 | 45.6497 | 233.5747 | NO | 24 | 0 | 46.7035 | 324.8823 | NO
[11 empty] | 2022-11-16 | 69.2% | 9.281% | 17.66% | 3.854% | 0% | 24 | 0 | 1.8083 | 16.7063 | NO | 24 | 0 | 47.0207 | 233.2702 | NO | 24 | 0 | 45.985 | 321.4436 | NO
[11 empty] | 2022-11-17 | 72.88% | 10.38% | 15.8% | 0.9385% | 0% | 24 | 0 | 1.7792 | 16.709 | NO | 24 | 0 | 55.3623 | 241.1365 | NO | 24 | 0 | 52.2046 | 327.9378 | NO
[11 empty] | 2022-11-18 | 76.15% | 10.67% | 12.07% | 1.114% | 0% | 24 | 0 | 1.8101 | 15.9413 | NO | 24 | 0 | 55.8349 | 241.2911 | NO | 24 | 0 | 52.3521 | 327.5526 | NO
[11 empty] | 2022-11-19 | 71.8% | 9.215% | 17.55% | 1.433% | 0% | 24 | 0 | 1.869 | 16.811 | NO | 24 | 0 | 46.9856 | 237.668 | NO | 24 | 0 | 52.8296 | 326.8517 | NO
[11 empty] | 2022-11-20 | 70.94% | 9.895% | 16.96% | 2.202% | 0% | 24 | 1 | 1.8227 | 16.7746 | NO | 24 | 1 | 40.0562 | 237.8236 | NO | 24 | 1 | 58.624 | 325.0574 | NO
[11 empty] | 2022-11-21 | 68.68% | 13.76% | 14.74% | 2.819% | 0% | 24 | 1 | 1.8512 | 17.0886 | NO | 24 | 1 | 41.5627 | 245.0552 | NO | 24 | 1 | 71.9353 | 323.5866 | NO
[11 empty] | 2022-11-22 | 64.98% | 11.96% | 14.82% | 7.362% | 0.8731% | 24 | 3 | 1.9383 | 16.6478 | NO | 24 | 3 | 39.8384 | 233.5525 | NO | 24 | 3 | 67.9738 | 313.0118 | NO
[11 empty] | 2022-11-23 | 73.98% | 13.15% | 8.133% | 4.744% | 0% | 24 | 0 | 1.7431 | 15.3908 | NO | 24 | 0 | 54.3222 | 239.2642 | NO | 24 | 0 | 82.4818 | 319.3231 | NO
[11 empty] | 2022-11-24 | 62.3% | 12.14% | 18.42% | 7.135% | 0% | 24 | 2 | 1.6964 | 17.2986 | NO | 24 | 2 | 48.3019 | 233.2762 | NO | 24 | 2 | 60.6097 | 314.0292 | NO
[11 empty] | 2022-11-25 | 63.5% | 11.2% | 17.4% | 7.907% | 0% | 24 | 3 | 1.7056 | 16.8521 | NO | 24 | 3 | 38.4682 | 230.3175 | NO | 24 | 3 | 56.2584 | 312.5781 | NO
[11 empty] | 2022-11-26 | 66.95% | 9.4% | 21.14% | 2.512% | 0% | 24 | 0 | 1.6857 | 17.5865 | NO | 24 | 0 | 43.4697 | 236.3596 | NO | 24 | 0 | 51.9986 | 324.5291 | NO
[11 empty] | 2022-11-27 | 70.03% | 10.61% | 17.93% | 1.435% | 0% | 24 | 0 | 1.6924 | 17.1998 | NO | 24 | 0 | 47.8754 | 240.8032 | NO | 24 | 0 | 61.2355 | 326.8431 | NO
[11 empty] | 2022-11-28 | 33.83% | 12.91% | 16.56% | 23.74% | 12.96% | 24 | 18 | 1.7653 | 17.3692 | NO | 24 | 18 | 42.4391 | 206.3664 | NO | 24 | 18 | 67.773 | 255.2303 | NO
[11 empty] | 2022-11-29 | OFF
[11 empty] | 2022-11-30 | 59.9% | 1.364% | 3.552% | 33.05% | 2.133% | 24 | 1 | 1.9841 | 10.6224 | NO | 24 | 1 | 30.1596 | 164.239 | NO | 24 | 1 | 57.1573 | 255.0234 | NO
[11 empty] | 2022-12-01 | 62.98% | 0.4207% | 13.62% | 22.98% | 0% | 24 | 0 | 2.1156 | 12.8378 | NO | 24 | 0 | 32.7133 | 179.288 | NO | 24 | 0 | 61.4805 | 279.5476 | NO
[11 empty] | 2022-12-02 | 74.93% | 3.205% | 9.933% | 11.93% | 0% | 24 | 0 | 2.1606 | 13.1928 | NO | 24 | 0 | 52.8596 | 205.1139 | NO | 24 | 0 | 46.5959 | 303.427 | NO
[11 empty] | 2022-12-03 | 73.04% | 6.449% | 17.73% | 2.784% | 0% | 24 | 0 | 2.033 | 16.1659 | NO | 24 | 0 | 47.2623 | 229.1454 | NO | 24 | 0 | 50.4013 | 323.88 | NO
[11 empty] | 2022-12-04 | 75.48% | 7.107% | 12.54% | 4.878% | 0% | 24 | 0 | 2.0839 | 15.057 | NO | 24 | 0 | 55.4603 | 226.818 | NO | 24 | 0 | 49.7641 | 319.2975 | NO
[11 empty] | 2022-12-05 | 82.51% | 7.766% | 4.657% | 5.063% | 0% | 24 | 0 | 2.0154 | 13.4707 | NO | 24 | 0 | 56.4006 | 228.0965 | NO | 24 | 0 | 49.8851 | 318.9896 | NO
[11 empty] | 2022-12-06 | 79.19% | 8.273% | 9.449% | 3.086% | 0% | 24 | 0 | 2.0755 | 14.7289 | NO | 24 | 0 | 59.5258 | 232.5935 | NO | 24 | 0 | 48.6176 | 323.2097 | NO
[11 empty] | 2022-12-07 | 75.63% | 7.91% | 11.9% | 4.566% | 0% | 24 | 0 | 2.176 | 15.1019 | NO | 24 | 0 | 53.8789 | 229.0825 | NO | 24 | 0 | 49.0555 | 319.9197 | NO
[11 empty] | 2022-12-08 | 61.04% | 19.53% | 9.519% | 9.915% | 0% | 24 | 8 | 2.2646 | 16.7596 | NO | 24 | 8 | 60.6075 | 245.2686 | NO | 24 | 8 | 78.2464 | 307.5017 | NO
[11 empty] | 2022-12-09 | 79.38% | 8.823% | 7.569% | 4.229% | 0% | 24 | 0 | 2.2383 | 14.3584 | NO | 24 | 0 | 53.5414 | 231.7545 | NO | 24 | 0 | 47.2861 | 320.574 | NO
[11 empty] | 2022-12-10 | 75.3% | 1.283% | 14.1% | 9.322% | 0% | 24 | 0 | 2.2345 | 13.8803 | NO | 23 | 0 | 44.1791 | 206.0032 | NO | 23 | 0 | 36.8948 | 309.5665 | NO
[11 empty] | 2022-12-11 | 76.69% | 0.2716% | 12.96% | 10.07% | 0% | 24 | 0 | 2.2603 | 13.359 | NO | 23 | 0 | 38.7886 | 202.326 | NO | 23 | 0 | 39.112 | 307.8532 | NO
[11 empty] | 2022-12-12 | 74.51% | 0.4839% | 10.1% | 14.91% | 0% | 24 | 1 | 2.3713 | 12.4854 | NO | 24 | 1 | 43.1413 | 193.8548 | NO | 24 | 1 | 40.4337 | 297.0144 | NO
[11 empty] | 2022-12-13 | 66.55% | 0.7344% | 11.7% | 20.26% | 0.7507% | 24 | 7 | 2.3396 | 12.6157 | NO | 24 | 7 | 30.3667 | 184.3864 | NO | 24 | 7 | 61.1223 | 283.5752 | NO
[11 empty] | 2022-12-14 | 73.09% | 0.9254% | 13.74% | 12.24% | 0% | 24 | 0 | 2.3373 | 13.539 | NO | 24 | 0 | 44.0676 | 199.7292 | NO | 24 | 0 | 42.2962 | 302.9564 | NO
[11 empty] | 2022-12-15 | 74.18% | 1.093% | 4.433% | 20.29% | 0% | 24 | 0 | 2.3174 | 11.1306 | NO | 24 | 0 | 31.6635 | 185.7847 | NO | 24 | 0 | 50.7639 | 285.6082 | NO
[11 empty] | 2022-12-16 | 55.37% | 1.434% | 15.63% | 27.57% | 0% | 24 | 9 | 2.1959 | 13.0229 | NO | 24 | 9 | 24.5082 | 171.7372 | NO | 24 | 9 | 51.4713 | 267.6301 | NO
[11 empty] | 2022-12-17 | 66.6% | 4.261% | 10.7% | 18.44% | 0% | 24 | 0 | 1.767 | 13.2912 | NO | 24 | 0 | 44.1586 | 196.0674 | NO | 24 | 0 | 64.4416 | 289.5372 | NO
[11 empty] | 2022-12-18 | 62.69% | 12.52% | 19.86% | 4.935% | 0% | 24 | 5 | 1.6147 | 17.7591 | NO | 24 | 5 | 57.7764 | 238.7984 | NO | 24 | 5 | 47.499 | 318.4035 | NO
[11 empty] | 2022-12-19 | 59.97% | 19.12% | 13.63% | 7.282% | 0% | 24 | 2 | 1.5453 | 17.8169 | NO | 24 | 2 | 65.5073 | 249.5496 | NO | 24 | 2 | 67.1891 | 314.0896 | NO
[11 empty] | 2022-12-20 | 73.15% | 9.299% | 12.53% | 5.012% | 0% | 24 | 0 | 1.4426 | 15.537 | NO | 24 | 0 | 48.688 | 231.4442 | NO | 24 | 0 | 69.2174 | 319.047 | NO
[11 empty] | 2022-12-21 | 67.26% | 13.12% | 10.17% | 9.446% | 0% | 24 | 2 | 1.5128 | 15.5669 | NO | 24 | 2 | 55.7904 | 231.5637 | NO | 24 | 2 | 49.4956 | 308.9153 | NO
[11 empty] | 2022-12-22 | 75.05% | 11.25% | 11.33% | 2.372% | 0% | 24 | 0 | 1.4922 | 15.8227 | NO | 24 | 0 | 56.9325 | 240.3485 | NO | 24 | 0 | 45.3654 | 324.6667 | NO
[11 empty] | 2022-12-23 | 75.13% | 14.05% | 2.553% | 8.263% | 0% | 24 | 1 | 1.6613 | 14.9091 | NO | 24 | 1 | 50.1894 | 235.2987 | NO | 24 | 1 | 65.1982 | 317.5043 | NO
[11 empty] | 2022-12-24 | 74.35% | 12.8% | 10.41% | 2.433% | 0% | 24 | 0 | 1.3678 | 15.9719 | NO | 24 | 0 | 59.178 | 243.6995 | NO | 24 | 0 | 46.4911 | 324.6307 | NO
[11 empty] | 2022-12-25 | 73.79% | 16.95% | 7.735% | 1.52% | 0% | 24 | 0 | 1.464 | 16.3427 | NO | 24 | 0 | 67.455 | 254.3176 | NO | 24 | 0 | 59.659 | 326.6166 | NO
[11 empty] | 2022-12-26 | 71.02% | 16.1% | 9.758% | 3.125% | 0% | 24 | 0 | 1.6717 | 16.5264 | NO | 24 | 0 | 62.031 | 249.0256 | NO | 24 | 0 | 54.6564 | 323.2018 | NO
[11 empty] | 2022-12-27 | 78.04% | 13.32% | 5.896% | 2.746% | 0% | 24 | 0 | 1.5146 | 15.1122 | NO | 24 | 0 | 65.9388 | 244.1074 | NO | 24 | 0 | 51.9268 | 324.2486 | NO
[11 empty] | 2022-12-28 | 74.46% | 12.99% | 10.5% | 2.05% | 0% | 24 | 1 | 1.3688 | 14.9574 | NO | 24 | 1 | 66.262 | 237.7831 | NO | 24 | 1 | 51.6249 | 314.5142 | NO
[11 empty] | 2022-12-29 | 20.22% | 12.09% | 64.86% | 2.83% | 0% | 24 | 18 | 1.4613 | 8.0146 | NO | 24 | 18 | 43.7871 | 109.6735 | NO | 24 | 18 | 59.8196 | 126.1815 | NO
[11 empty] | 2022-12-30 | 56.68% | 15.22% | 11.63% | 11.12% | 5.347% | 24 | 12 | 1.4675 | 17.0263 | NO | 24 | 12 | 49.6011 | 236.0082 | NO | 24 | 12 | 51.276 | 298.3505 | NO
[11 empty] | 2022-12-31 | 57.63% | 17.82% | 5.424% | 10.77% | 8.353% | 24 | 5 | 1.4039 | 17.1649 | NO | 24 | 5 | 72.6187 | 241.0922 | NO | 24 | 5 | 48.2777 | 299.8194 | NO
[11 empty] | 0 | 87.69% | 10.14% | 1.22% | 0.95% | 0% | 24 | 0 | 2.3 | 13.4 | NO | 24 | 0 | 59.5 | 239.9 | NO | 24 | 0 | 45 | 327.3 | NO
[11 empty] | 0 | 68.01% | 14.01% | 9.95% | 8.03% | 0% | 24 | 0 | 1.1695 | 15.3783 | NO | 24 | 0 | 37.1714 | 235.3297 | NO | 24 | 0 | 98.2477 | 326.6528 | NO

## A52B Boiler 7
|  | Concentrations in mg/m³ at reference conditions after subtracting uncertainty | [9 empty] | Daily means, excluding hours outside normal operating conditions
|  | 2022-10-01 |  |  | 2022-11-01 |  |  | 2022-12-01 |  |  | Date | Fuel mix |  |  |  |  | Particulate Matter concentration (mg/m³) after subtracting uncertainty |  |  |  |  | Sulphur dioxide concentration (mg/m³) after subtracting uncertainty |  |  |  |  | Oxides of nitrogen concentration (mg/m³) after subtracting uncertainty
|  | PM | SO2 | NOx | PM | SO2 | NOx | PM | SO2 | NOx |  | % BFG | % COG | % BOSg | % NG | % HFO | No.valid hours | No.hours OTNOC | Measured | Limit | Breach? | No.valid hours | No.hours OTNOC | Measured | Limit | Breach? | No.valid hours | No.hours OTNOC | Measured | Limit | Breach?
Daily means | Minimum | 1.0482 | 5.0087 | 18.1603 | 1.2283 | 2.1943 | 13.2 | 1.4264 | 4.4043 | 10.8166 | 2022-10-01 | 88.22% | 10.8% | -0.2356% | 1.215% | 0% | 24 | 0 | 1.3631 | 13.6956 | NO | 24 | 0 | 12.4365 | 244.4882 | NO | 24 | 0 | 21.3056 | 331.7115 | NO
| Maximum | 2.3734 | 15.8913 | 48.0776 | 2.4876 | 15.2149 | 50.2787 | 3.168 | 16.8553 | 32.3 | 2022-10-02 | 80.52% | 12.31% | 0.2571% | 6.911% | 0% | 24 | 2 | 1.3739 | 13.6645 | NO | 24 | 2 | 5.3914 | 236.2505 | NO | 24 | 2 | 27.2842 | 317.8988 | NO
| No. > Limit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2022-10-03 | 80.51% | 12.99% | 0.1543% | 6.337% | 0% | 24 | 2 | 1.4931 | 13.8597 | NO | 24 | 2 | 5.0087 | 239.0711 | NO | 24 | 2 | 26.725 | 319.4865 | NO
Monthly mean |  | 1.4034 | 9.4095 | 29.5681 | 1.5918 | 8.587 | 25.3831 | 1.9854 | 8.7462 | 18.4919 | 2022-10-04 | 81.05% | 13.5% | 0.03516% | 5.417% | 0% | 24 | 0 | 1.6827 | 14.0746 | NO | 24 | 0 | 5.0812 | 242.704 | NO | 24 | 0 | 33.8475 | 322.0994 | NO
Monthly mean limit |  | 15.5632 | 241.2585 | 321.0482 | 16.827 | 242.5652 | 327.9952 | 15.1818 | 229.9763 | 319.8258 | 2022-10-05 | 85.22% | 12.46% | -0.3355% | 2.648% | 0% | 24 | 0 | 1.1533 | 14.0013 | NO | 24 | 0 | 11.9654 | 245.8501 | NO | 24 | 0 | 26.2032 | 328.9662 | NO
[11 empty] | 2022-10-06 | 89.55% | 9.773% | -0.1749% | 0.8502% | 0% | 24 | 0 | 1.2334 | 13.5034 | NO | 24 | 0 | 8.9449 | 243.0583 | NO | 24 | 0 | 25.3955 | 332.5127 | NO
[11 empty] | 2022-10-07 | 84.15% | 9.435% | 0.1472% | 6.27% | 0% | 24 | 0 | 1.4788 | 13.1214 | NO | 24 | 0 | 6.9475 | 231.9329 | NO | 24 | 0 | 26.4237 | 319.9549 | NO
[11 empty] | 2022-10-08 | 65.25% | 12.26% | -0.4218% | 20.72% | 2.193% | 24 | 5 | 1.7573 | 13.4215 | NO | 24 | 5 | 8.3038 | 214.8927 | NO | 24 | 5 | 25.5207 | 287.97 | NO
[11 empty] | 2022-10-09 | 79.54% | 12.48% | -0.1661% | 8.147% | 0% | 24 | 0 | 1.6458 | 13.6935 | NO | 24 | 0 | 9.0013 | 235.5626 | NO | 24 | 0 | 29.6981 | 316.5068 | NO
[11 empty] | 2022-10-10 | 66.55% | 19.96% | 1.305% | 12.18% | 0% | 24 | 5 | 2.3734 | 15.1965 | NO | 24 | 5 | 12.4935 | 244.1742 | NO | 24 | 5 | 41.0471 | 305.5741 | NO
[11 empty] | 2022-10-11 | 81.13% | 15.91% | -0.2432% | 3.2% | 0% | 24 | 0 | 1.819 | 14.7201 | NO | 24 | 0 | 13.2754 | 252.2706 | NO | 24 | 0 | 29.3924 | 327.4495 | NO
[11 empty] | 2022-10-12 | 82.18% | 14.04% | 0.9313% | 2.847% | 0% | 24 | 0 | 1.4623 | 14.636 | NO | 24 | 0 | 8.7797 | 248.9916 | NO | 24 | 0 | 29.9467 | 328.7042 | NO
[11 empty] | 2022-10-13 | 80.78% | 10.43% | 7.506% | 1.28% | 0% | 24 | 0 | 1.3132 | 15.5189 | NO | 24 | 0 | 8.6567 | 244.9348 | NO | 24 | 0 | 23.1997 | 333.6124 | NO
[11 empty] | 2022-10-14 | 74.1% | 10.72% | 11.99% | 3.192% | 0% | 24 | 2 | 1.2756 | 16.7859 | NO | 24 | 2 | 8.6106 | 244.3189 | NO | 24 | 2 | 24.8642 | 332.9023 | NO
[11 empty] | 2022-10-15 | 74.5% | 9.512% | 13.52% | 2.467% | 0% | 24 | 0 | 1.4867 | 17.0664 | NO | 24 | 0 | 8.339 | 244.1791 | NO | 24 | 0 | 34.1707 | 336.0685 | NO
[11 empty] | 2022-10-16 | 67.78% | 15.11% | 14.45% | 2.671% | 0% | 24 | 5 | 1.7306 | 18.2915 | NO | 24 | 5 | 13.0794 | 257.42 | NO | 24 | 5 | 47.6722 | 333.6945 | NO
[11 empty] | 2022-10-17 | 72.06% | 4.962% | 14.82% | 8.156% | 0% | 24 | 0 | 1.1724 | 15.8501 | NO | 24 | 0 | 5.4315 | 221.9979 | NO | 24 | 0 | 33.7358 | 321.5969 | NO
[11 empty] | 2022-10-18 | 57.18% | 13.15% | 9.925% | 19.22% | 0.5262% | 24 | 3 | 1.5922 | 16.0967 | NO | 24 | 3 | 8.0902 | 221.1426 | NO | 24 | 3 | 18.1603 | 297.1628 | NO
[11 empty] | 2022-10-19 | 31.64% | 22.82% | 5.734% | 33.5% | 6.307% | 24 | 24 |  |  |  | 24 | 24 |  |  | NO | 24 | 24 |  |  | NO
[11 empty] | 2022-10-20 | 48.86% | 24.79% | 3.584% | 21.91% | 0.861% | 24 | 5 | 1.1677 | 16.6244 | NO | 24 | 5 | 5.432 | 238.5913 | NO | 24 | 5 | 26.2627 | 285.5533 | NO
[11 empty] | 2022-10-21 | 71.57% | 17.23% | 6.242% | 4.961% | 0% | 24 | 0 | 1.0482 | 16.7948 | NO | 24 | 0 | 15.8913 | 254.9045 | NO | 24 | 0 | 41.5654 | 328.0913 | NO
[11 empty] | 2022-10-22 | 78.93% | 14.15% | 5.961% | 0.9593% | 0% | 24 | 0 | 1.0555 | 16.198 | NO | 24 | 0 | 10.7419 | 254.9215 | NO | 24 | 0 | 30.6649 | 336.1632 | NO
[11 empty] | 2022-10-23 | 73.21% | 11.75% | 13.96% | 1.076% | 0% | 24 | 0 | 1.0831 | 15.3459 | NO | 24 | 0 | 9.065 | 235.5819 | NO | 24 | 0 | 26.5039 | 315.1018 | NO
[11 empty] | 2022-10-24 | 77.05% | 11.71% | 10.46% | 0.7712% | 0% | 24 | 0 | 1.2096 | 16.931 | NO | 24 | 0 | 8.7063 | 251.4362 | NO | 24 | 0 | 37.6881 | 339.2508 | NO
[11 empty] | 2022-10-25 | 60.02% | 16.02% | 5.142% | 16.25% | 2.563% | 24 | 8 | 1.4026 | 16.4534 | NO | 24 | 8 | 11.9587 | 234.7785 | NO | 24 | 8 | 31.7772 | 305.5177 | NO
[11 empty] | 2022-10-26 | 66.43% | 18.42% | 2.15% | 13% | 0% | 24 | 5 | 1.1723 | 15.4425 | NO | 24 | 5 | 12.7356 | 241.4193 | NO | 24 | 5 | 48.0776 | 307.648 | NO
[11 empty] | 2022-10-27 | 56.14% | 13.32% | 10.09% | 20.46% | 0% | 24 | 9 | 1.1866 | 15.5994 | NO | 24 | 9 | 10.194 | 216.8195 | NO | 24 | 9 | 31.5642 | 291.15 | NO
[11 empty] | 2022-10-28 | 74.78% | 11.29% | 12.83% | 1.102% | 0% | 24 | 0 | 1.6366 | 17.8233 | NO | 24 | 0 | 8.0728 | 253.3852 | NO | 24 | 0 | 22.1054 | 343.3515 | NO
[11 empty] | 2022-10-29 | 73.02% | 11.42% | 13.11% | 2.458% | 0% | 24 | 0 | 1.2407 | 17.6061 | NO | 24 | 0 | 9.8021 | 249.5322 | NO | 24 | 0 | 19.2716 | 338.0366 | NO
[11 empty] | 2022-10-30 | 63.39% | 15.61% | 13.14% | 7.862% | 0% | 24 | 6 | 1.2736 | 17.8548 | NO | 24 | 6 | 9.1091 | 247.2944 | NO | 24 | 6 | 20.5099 | 322.6354 | NO
[11 empty] | 2022-10-31 | 68.72% | 13.77% | 11.33% | 6.179% | 0% | 24 | 3 | 1.2185 | 17.0235 | NO | 24 | 3 | 10.739 | 245.8493 | NO | 24 | 3 | 26.4594 | 325.0757 | NO
[11 empty] | 2022-11-01 | 73.84% | 13.99% | 6.675% | 5.495% | 0% | 24 | 1 | 1.2392 | 16.013 | NO | 24 | 1 | 12.1636 | 246.612 | NO | 24 | 1 | 28.3129 | 325.7316 | NO
[11 empty] | 2022-11-02 | 73.3% | 16.69% | 4.921% | 5.086% | 0% | 24 | 0 | 1.326 | 15.94 | NO | 24 | 0 | 5.1031 | 251.1084 | NO | 24 | 0 | 34.2482 | 323.5116 | NO
[11 empty] | 2022-11-03 | 71.73% | 12.79% | 10.23% | 5.245% | 0% | 24 | 0 | 1.4518 | 16.289 | NO | 24 | 0 | 5.4096 | 242.0949 | NO | 24 | 0 | 26.0397 | 323.5291 | NO
[11 empty] | 2022-11-04 | 74.59% | 9.661% | 13.9% | 1.852% | 0% | 24 | 0 | 1.7991 | 17.1135 | NO | 24 | 0 | 5.2866 | 244.7841 | NO | 24 | 0 | 17.4488 | 336.2528 | NO
[11 empty] | 2022-11-05 | 78.96% | 10.35% | 9.792% | 0.9019% | 0% | 24 | 0 | 1.3882 | 16.4049 | NO | 24 | 0 | 9.2032 | 248.008 | NO | 24 | 0 | 25.7333 | 338.2618 | NO
[11 empty] | 2022-11-06 | 75.92% | 11.64% | 11.71% | 0.728% | 0% | 24 | 0 | 1.3721 | 17.1989 | NO | 24 | 0 | 8.4481 | 251.4857 | NO | 24 | 0 | 27.9862 | 339.4206 | NO
[11 empty] | 2022-11-07 | 70.14% | 13.49% | 11.14% | 5.233% | 0% | 24 | 4 | 1.5419 | 16.9022 | NO | 24 | 4 | 9.4198 | 245.7614 | NO | 24 | 4 | 29.6148 | 327.0634 | NO
[11 empty] | 2022-11-08 | 54.44% | 18.84% | 7.476% | 19.25% | 0% | 24 | 15 | 1.4462 | 16.0681 | NO | 24 | 15 | 15.2149 | 230.3678 | NO | 24 | 15 | 24.015 | 291.6772 | NO
[11 empty] | 2022-11-09 | 79.49% | 11.32% | 5.994% | 3.197% | 0% | 24 | 0 | 1.3617 | 15.357 | NO | 24 | 0 | 9.4346 | 244.0848 | NO | 24 | 0 | 29.6123 | 330.2568 | NO
[11 empty] | 2022-11-10 | 77.85% | 8.351% | 11.57% | 2.223% | 0% | 24 | 0 | 1.3146 | 16.8172 | NO | 24 | 0 | 6.7201 | 244.7163 | NO | 24 | 0 | 30.1505 | 340.6581 | NO
[11 empty] | 2022-11-11 | 65.02% | 21.21% | 6.547% | 7.22% | 0% | 24 | 3 | 1.5843 | 20.7503 | NO | 24 | 3 | 7.9638 | 280.7082 | NO | 24 | 3 | 50.2787 | 354.6391 | NO
[11 empty] | 2022-11-12 | 60.59% | 19.3% | 3.322% | 16.79% | 0% | 24 | 7 | 1.3096 | 17.188 | NO | 24 | 7 | 8.3355 | 246.3612 | NO | 24 | 7 | 48.7247 | 314.5231 | NO
[11 empty] | 2022-11-13 | 76.24% | 15.66% | 5.468% | 2.632% | 0% | 24 | 0 | 1.2283 | 18.9371 | NO | 24 | 0 | 13.5219 | 272.7336 | NO | 24 | 0 | 33.8355 | 358.5797 | NO
[11 empty] | 2022-11-14 | 74.39% | 12.13% | 12.4% | 1.074% | 0% | 24 | 0 | 1.3386 | 19.6357 | NO | 24 | 0 | 8.0231 | 266.6032 | NO | 24 | 0 | 36.0668 | 360.6121 | NO
[11 empty] | 2022-11-15 | 78.43% | 8.602% | 11.74% | 1.232% | 0% | 24 | 0 | 1.5305 | 16.5329 | NO | 24 | 0 | 6.6074 | 244.1536 | NO | 24 | 0 | 21.5961 | 338.5461 | NO
[11 empty] | 2022-11-16 | 73.23% | 8.567% | 14.37% | 3.827% | 0% | 24 | 0 | 1.6095 | 17.0357 | NO | 24 | 0 | 6.5859 | 239.8136 | NO | 24 | 0 | 13.6584 | 333.6203 | NO
[11 empty] | 2022-11-17 | 76.75% | 8.737% | 12.76% | 1.754% | 0% | 24 | 0 | 1.6092 | 16.7142 | NO | 24 | 0 | 6.162 | 242.9936 | NO | 24 | 0 | 15.7448 | 337.0003 | NO
[11 empty] | 2022-11-18 | 81.27% | 7.547% | 9.975% | 1.206% | 0% | 24 | 0 | 1.7275 | 15.7207 | NO | 24 | 0 | 3.6819 | 240.7488 | NO | 24 | 0 | 17.6505 | 336.6696 | NO
[11 empty] | 2022-11-19 | 77.51% | 6.08% | 14.85% | 1.559% | 0% | 24 | 0 | 1.7955 | 16.6737 | NO | 24 | 0 | 6.0574 | 238.2311 | NO | 24 | 0 | 13.2 | 338.12 | NO
[11 empty] | 2022-11-20 | 75.58% | 8.301% | 13.85% | 2.27% | 0% | 24 | 0 | 1.6888 | 16.9212 | NO | 24 | 0 | 6.9649 | 242.0865 | NO | 24 | 0 | 17.5871 | 336.7658 | NO
[11 empty] | 2022-11-21 | 70.79% | 13% | 13.24% | 2.973% | 0% | 24 | 0 | 1.8568 | 17.3253 | NO | 24 | 0 | 5.6925 | 249.1424 | NO | 24 | 0 | 24.5537 | 330.6392 | NO
[11 empty] | 2022-11-22 | 65.25% | 13% | 13.51% | 7.706% | 0.5331% | 24 | 4 | 2.4876 | 16.9927 | NO | 24 | 4 | 9.2569 | 238.4763 | NO | 24 | 4 | 23.189 | 317.344 | NO
[11 empty] | 2022-11-23 | 71.34% | 10.84% | 12.63% | 5.188% | 0% | 24 | 3 | 1.5294 | 14.5046 | NO | 24 | 3 | 10.092 | 224.9676 | NO | 24 | 3 | 21.9341 | 304.7791 | NO
[11 empty] | 2022-11-24 | 66.26% | 11.52% | 14.67% | 7.554% | 0% | 24 | 2 | 1.5128 | 17.6578 | NO | 24 | 2 | 10.0451 | 240.3523 | NO | 24 | 2 | 23.7439 | 326.4645 | NO
[11 empty] | 2022-11-25 | 66.97% | 11.31% | 13.59% | 8.139% | 0% | 24 | 2 | 1.7336 | 17.3248 | NO | 24 | 2 | 12.5981 | 238.8119 | NO | 24 | 2 | 18.1947 | 325.0528 | NO
[11 empty] | 2022-11-26 | 71.37% | 10.51% | 15.86% | 2.254% | 0% | 24 | 0 | 1.5954 | 18.4339 | NO | 24 | 0 | 7.0318 | 250.6667 | NO | 24 | 0 | 16.5668 | 342.6024 | NO
[11 empty] | 2022-11-27 | 74.77% | 11.14% | 12.81% | 1.281% | 0% | 24 | 0 | 1.5362 | 17.8993 | NO | 24 | 0 | 10.0754 | 253.5108 | NO | 24 | 0 | 21.3222 | 344.187 | NO
[11 empty] | 2022-11-28 | 43.21% | 12.02% | 14.05% | 25.73% | 4.994% | 24 | 16 | 2.0317 | 16.9394 | NO | 24 | 16 | 10.4961 | 209.2445 | NO | 24 | 16 | 17.4182 | 276.5973 | NO
[11 empty] | 2022-11-29 | OFF | [13 empty] | NO |  |  |  |  | NO
[11 empty] | 2022-11-30 | 61.24% | 1.022% | 2.631% | 33.01% | 2.099% | 24 | 2 | 2.2173 | 10.6912 | NO | 24 | 2 | 13.4292 | 165.7606 | NO | 24 | 2 | 27.6817 | 258.7557 | NO
[11 empty] | 2022-12-01 | 68.59% | 0.3467% | 10.33% | 20.74% | 0% | 24 | 0 | 2.1166 | 13.4668 | NO | 24 | 0 | 2.1943 | 191.5116 | NO | 24 | 0 | 28.4859 | 296.9129 | NO
[11 empty] | 2022-12-02 | 78.35% | 3.564% | 7.556% | 10.53% | 0% | 24 | 0 | 2.3925 | 13.6871 | NO | 24 | 0 | 5.5772 | 214.0863 | NO | 24 | 0 | 20.3438 | 315.1666 | NO
[11 empty] | 2022-12-03 | 74.91% | 9.643% | 12.99% | 2.449% | 0% | 24 | 0 | 1.9115 | 17.2539 | NO | 24 | 0 | 5.2267 | 245.989 | NO | 24 | 0 | 25.0727 | 338.6912 | NO
[11 empty] | 2022-12-04 | 76.02% | 10.55% | 8.831% | 4.605% | 0% | 24 | 0 | 1.984 | 16.1555 | NO | 24 | 0 | 5.2115 | 242.1866 | NO | 24 | 0 | 23.6531 | 331.3326 | NO
[11 empty] | 2022-12-05 | 84.15% | 8.438% | 2.692% | 4.715% | 0% | 24 | 0 | 1.8674 | 13.856 | NO | 24 | 0 | 9.1626 | 234.4356 | NO | 24 | 0 | 17.3377 | 326.2732 | NO
[11 empty] | 2022-12-06 | 82.13% | 7.936% | 6.891% | 3.041% | 0% | 24 | 0 | 1.9611 | 14.9906 | NO | 24 | 0 | 10.9473 | 237.8906 | NO | 24 | 0 | 20.2028 | 332.2693 | NO
[11 empty] | 2022-12-07 | 77.74% | 9.481% | 8.398% | 4.382% | 0% | 24 | 0 | 2.2026 | 15.757 | NO | 24 | 0 | 11.2135 | 239.7066 | NO | 24 | 0 | 16.3889 | 331.035 | NO
[11 empty] | 2022-12-08 | 65.69% | 13.83% | 7.869% | 12.41% | 0.2047% | 24 | 7 | 2.4501 | 15.8745 | NO | 24 | 7 | 7.7745 | 234.1277 | NO | 24 | 7 | 24.2873 | 310.4142 | NO
[11 empty] | 2022-12-09 | 79.67% | 9.898% | 4.926% | 5.502% | 0% | 24 | 0 | 2.3539 | 14.698 | NO | 24 | 0 | 11.4943 | 236.3226 | NO | 24 | 0 | 18.3103 | 325.3598 | NO
[11 empty] | 2022-12-10 | 79.76% | 1.479% | 11.15% | 7.61% | 0% | 24 | 0 | 2.2432 | 14.459 | NO | 24 | 0 | 6.011 | 216.6992 | NO | 24 | 0 | 10.8166 | 324.2508 | NO
[11 empty] | 2022-12-11 | 80.91% | 0.8433% | 10.28% | 7.966% | 0% | 24 | 0 | 2.3137 | 14.0097 | NO | 24 | 0 | 7.145 | 214.0721 | NO | 24 | 0 | 11.2806 | 322.4872 | NO
[11 empty] | 2022-12-12 | 79.11% | 1.508% | 7.851% | 11.53% | 0% | 24 | 0 | 2.5336 | 13.2582 | NO | 24 | 0 | 5.9473 | 207.9541 | NO | 24 | 0 | 13.7689 | 313.0324 | NO
[11 empty] | 2022-12-13 | 70.17% | 2.19% | 8.857% | 17.96% | 0.8241% | 24 | 1 | 3.168 | 13.5152 | NO | 24 | 1 | 4.4043 | 198.9142 | NO | 24 | 1 | 15.6206 | 299.0761 | NO
[11 empty] | 2022-12-14 | 75.59% | 2.742% | 10.52% | 11.15% | 0% | 24 | 0 | 2.5299 | 14.3812 | NO | 24 | 0 | 5.5238 | 212.9969 | NO | 24 | 0 | 13.6829 | 316.1933 | NO
[11 empty] | 2022-12-15 | 73.37% | 3.281% | 2.616% | 20.73% | 0% | 24 | 0 | 2.5221 | 11.7839 | NO | 24 | 0 | 4.6045 | 193.7798 | NO | 24 | 0 | 19.1677 | 290.5364 | NO
[11 empty] | 2022-12-16 | 58.04% | 4.636% | 13.84% | 23.49% | 0% | 24 | 9 | 2.7958 | 14.3384 | NO | 24 | 9 | 5.4299 | 191.658 | NO | 24 | 9 | 16.6881 | 284.5212 | NO
[11 empty] | 2022-12-17 | 68.68% | 6.954% | 8.096% | 16.27% | 0% | 24 | 0 | 2.1274 | 14.3012 | NO | 24 | 0 | 16.0191 | 211.7141 | NO | 24 | 0 | 11.5012 | 303.0544 | NO
[11 empty] | 2022-12-18 | 68.2% | 10.96% | 15.7% | 5.138% | 0% | 24 | 3 | 1.8954 | 18.0217 | NO | 24 | 3 | 11.7177 | 244.7058 | NO | 24 | 3 | 14.5465 | 333.1823 | NO
[11 empty] | 2022-12-19 | 65.17% | 18.33% | 9.918% | 6.577% | 0% | 24 | 0 | 1.446 | 18.2006 | NO | 24 | 0 | 16.8553 | 257.6681 | NO | 24 | 0 | 32.3 | 329.0206 | NO
[11 empty] | 2022-12-20 | 74.89% | 10.63% | 9.475% | 5.002% | 0% | 24 | 0 | 1.4835 | 16.1544 | NO | 24 | 0 | 8.1726 | 241.0405 | NO | 24 | 0 | 17.9409 | 329.0515 | NO
[11 empty] | 2022-12-21 | 72.3% | 12.37% | 7.377% | 7.956% | 0% | 24 | 0 | 1.7963 | 15.9078 | NO | 24 | 0 | 7.3706 | 239.5655 | NO | 24 | 0 | 20.4649 | 322.5556 | NO
[11 empty] | 2022-12-22 | 78.87% | 10.63% | 8.501% | 2.005% | 0% | 24 | 0 | 1.5625 | 16.0817 | NO | 24 | 0 | 8.8471 | 246.3338 | NO | 24 | 0 | 21.4675 | 335.4189 | NO
[11 empty] | 2022-12-23 | 71.09% | 11.78% | 12.33% | 4.808% | 0% | 24 | 2 | 1.8401 | 14.5991 | NO | 24 | 2 | 7.8507 | 228.2413 | NO | 24 | 2 | 23.551 | 305.3921 | NO
[11 empty] | 2022-12-24 | 76.44% | 11.65% | 9.269% | 2.642% | 0% | 24 | 0 | 1.4331 | 15.9114 | NO | 24 | 0 | 12.1665 | 243.9716 | NO | 24 | 0 | 17.0727 | 328.76 | NO
[11 empty] | 2022-12-25 | 80.94% | 10.69% | 6.495% | 1.88% | 0% | 24 | 0 | 1.4264 | 15.312 | NO | 24 | 0 | 10.3071 | 244.2374 | NO | 24 | 0 | 16.2203 | 332.1931 | NO
[11 empty] | 2022-12-26 | 78.05% | 11.02% | 7.707% | 3.225% | 0% | 24 | 0 | 1.7837 | 15.9773 | NO | 24 | 0 | 9.9562 | 245.3408 | NO | 24 | 0 | 15.1021 | 333.2496 | NO
[11 empty] | 2022-12-27 | 81.36% | 11.84% | 4.041% | 2.758% | 0% | 24 | 0 | 1.6077 | 15.1176 | NO | 24 | 0 | 7.7092 | 246.2496 | NO | 24 | 0 | 15.8209 | 331.6716 | NO
[11 empty] | 2022-12-28 | 78.86% | 13.59% | 5.396% | 2.148% | 0% | 24 | 0 | 1.4967 | 15.6573 | NO | 24 | 0 | 8.243 | 250.2083 | NO | 24 | 0 | 19.382 | 331.2479 | NO
[11 empty] | 2022-12-29 | 82.68% | 11.6% | 2.872% | 2.845% | 0% | 24 | 0 | 1.8834 | 14.7449 | NO | 24 | 0 | 12.525 | 245.1402 | NO | 24 | 0 | 14.3648 | 330.9099 | NO
[11 empty] | 2022-12-30 | 61.3% | 13.06% | 9.953% | 14.31% | 1.382% | 24 | 9 | 1.5835 | 16.2589 | NO | 24 | 9 | 7.9054 | 229.0158 | NO | 24 | 9 | 17.6207 | 304.989 | NO
[11 empty] | 0 | 66.42% | 15.3% | 6.435% | 11.85% | 0% | 24 | 4 | 1.4112 | 16.043 | NO | 24 | 4 | 13.1817 | 236.7395 | NO | 24 | 4 | 19.6379 | 313.0886 | NO
[11 empty] | 0 | [9 empty] | NO | 24 |  |  |  | NO | 24 |  |  |  | NO
[11 empty] | 2022-12-31 | 66.42% | 15.3% | 6.435% | 11.85% | 0% | 24 | 4 | 1.4112 | 16.043 | NO | 24 | 4 | 13.1817 | 236.7395 | NO | 24 | 4 | 19.6379 | 313.0886 | NO