## Notes
Reference conditions
All concentrations in this spreadsheet are reported in dry air at a temperature of 273K, at a pressure of 101.3 kPa and with an oxygen content of 3% dry
Uncertainty
Concentrations in this spreadsheet are reported after having subtracted the value of the 95% confidence interval (see Section 3.6.7 of the permit):
95% confidence interval for nitrogen oxides is taken to be 20%
95% confidence interval for sulphur dioxide is taken to be 20%
95% confidence interval for dust is taken to be 30%
95% confidence interval for carbon monoxide is taken to be 10%
Normal operating conditions
The document "Power Plant Boiler Abnormal Conditions" sets out the criteria for excluding emissions monitoring data from permitting or other reporting obligations:
| Parameter | Plant | Level representing abnormal conditions
| Boiler oxygen | All boilers | >17% oxygen
| Fuel input | A51, A52A, A52B, A53 and A62 | <50% BFG by thermal input
|  | A50 (Service Boilers) | <35% BFG by thermal input

## Summary
Dust concentrations in mg/m³ (except A55 as % obscuration), reported as measured (uncertainty not taken into account)
| Source | A1 | A2 | A8A | A8B | A9 | A10 | A10A | A14 | A15 | A16 | A55 | A63 | A1 | A1
| Description | Sinter plant main stack (particulate) | Sinter plant deduster stack | BF4 casthouse fume extraction North | BF4 casthouse fume extraction South | BF5 casthouse fume extraction | Iron desulphurisation/hot metal pouring fume extraction plant stack | Hot metal fume extraction no. 2 | Secondary fume extraction stack North | Secondary fume extraction stack Centre | Secondary fume extraction stack South | Morfa main stack | CASOB/ desulph fume extraction plant | Sinter plant main stack (SO2) | Sinter plant main stack (NOX)
Daily means | Minimum | 0 | 0.20885 | 0.54584 | 0.34922 | 0.21042 | 0.18103 | 1.5202 | 0.65728 | 0.9755 | 1.2519 |  | 0.0002561 | 27.4506 | 2.953
| Maximum | 80.2 | 1.5428 | 4.2529 | 1.1774 | 3.1469 | 7.5727 | 15.0486 | 16.0801 | 15.579 | 4.9015 |  | 0.25196 | 576.4615 | 203.1876
| Limit | 40 | 10 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 500 | 500
| No. > Limit | 43 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 |  | 0 | 6 | 0
| No. > Limit w Uncert | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
Weekly mean | Minimum | [10 empty] | 21.2021
| Maximum | [10 empty] | 36.449
| Limit | [10 empty] | 25
| No. > Limit | [10 empty] | 6
| No. > Limit w Uncert | [10 empty] | 1

## Plots
NOTES

## Data
| Measured concentrations - daily means (mg/m³) | [25 empty] | Limits |  |  |  |  | Obscuration %
Source | A1 | A1 | A1 | A1 | A1 | A1 | A2 | A2 | A8A | A8A | A8B | A8B | A9 | A9 | A10 | A10 | A10A | A10A | A14 | A14 | A15 | A15 | A16 | A16 | A63 | A63 | A1 | A2 | BF and BOS plant sources | A1 | Source | A55
Description | Sinter plant main stack (Particulate) | Sinter plant main stack (Particulate) Uncertainty Applied | Sinter plant main stack (SO2) | Sinter plant main stack (SO2) Uncertainty Applied | Sinter plant main stack (NOX) | Sinter plant main stack (NOx) Uncertainty Applied | Sinter plant deduster stack | Sinter plant deduster stack Uncertainty Applied | BF4 casthouse fume extraction North | BF4 casthouse fume extraction North Uncertainty Applied | BF4 casthouse fume extraction South | BF4 casthouse fume extraction South Uncertainty Applied | BF5 casthouse fume extraction | BF5 casthouse fume extraction | Iron desulphurisation/hot metal pouring fume extraction plant stack | Iron desulphurisation/hot metal pouring fume extraction plant stack Uncertainty Applied | Hot metal fume extraction no. 2 | Hot metal fume extraction no. 2 Uncetainty Applied | Secondary fume extraction stack North | Secondary fume extraction stack North Uncertainty Applied | Secondary fume extraction stack Centre | Secondary fume extraction stack Centre Uncertainty Applied | Secondary fume extraction stack South | Secondary fume extraction stack South Uncertainty Applied | CASOB/ desulph fume extraction plant | CASOB/ desulph fume extraction plant Uncertainty Applied | Sinter plant main stack | Sinter plant deduster stack |  | Sinter Plant Main Stack SO2 & NOX | Description | Morfa main stack
Date / Uncertainty |  | 30% |  | 20% |  | 20% |  | 30% |  | 30% |  | 30% |  | 30% |  | 30% |  | 30% |  | 30% |  | 30% |  | 30% |  | 30% |  |  |  |  | Week commencing | Measured | Uncertainty Applied 30% | Limit | Schedule 5 Notification
2022-10-01 | 35.49 |  | 522.0437 | 417.635 | 191.832 |  | 0.80709 |  | 1.3048 |  | 0.6974 |  | 1.9822 |  | 7.5727 |  | 12.0185 |  | 6.0965 |  | 7.1947 |  | 2.4924 |  | 0.00071716 |  | 40 | 10 | 15 | 500 | 2022-10-01 | 22.6738 |  | 25
2022-10-02 | 33.44 |  | 480.689 |  | 181.8915 |  | 0.74945 |  | 1.1616 |  | 0.66382 |  | 1.5963 |  | 7.3619 |  | 10.3936 |  | 5.6953 |  | 7.1563 |  | 2.3921 |  | 0.00043271 |  | 40 | 10 | 15 | 500 | 2022-10-08 | 21.8499 |  | 25
2022-10-03 | 36.91 |  | 522.3253 | 417.8603 | 178.6881 |  | 0.84879 |  | 1.4121 |  | 0.88246 |  | 1.0824 |  | 5.7818 |  | 9.2459 |  | 5.781 |  | 5.9299 |  | 2.366 |  | 0.00047866 |  | 40 | 10 | 15 | 500 | 2022-10-15 | 28.8334 | 20.1833 | 25
2022-10-04 | 26.4 |  | 250.0217 |  | 95.2049 |  | 0.4697 |  | 1.127 |  | 0.6168 |  | 1.3639 |  | 4.8357 |  | 10.0111 |  | 3.0832 |  | 4.0887 |  | 2.1448 |  | 0.0002561 |  | 40 | 10 | 15 | 500 | 2022-10-22 | 36.449 | 25.5143 | 25 | S5N_22_72A
2022-10-05 | 32.82 |  | 483.7111 |  | 185.0296 |  | 0.8534 |  | 1.1524 |  | 0.62885 |  | 1.315 |  | 3.5593 |  | 7.6693 |  | 3.9337 |  | 4.6689 |  | 2.028 |  | 0.001196 |  | 40 | 10 | 15 | 500 | 2022-10-29 | 21.2021 |  | 25
2022-10-06 | 38.42 |  | 474.1796 |  | 188.5563 |  | 0.88031 |  | 1.5031 |  | 0.77215 |  | 1.9261 |  | 4.5009 |  | 9.8769 |  | 4.828 |  | 4.1191 |  | 2.4474 |  | 0.0011935 |  | 40 | 10 | 15 | 500 | 2022-11-05 | 22.4764 |  | 25
2022-10-07 | 40.28 | 28.196 | 421.6074 |  | 190.8491 |  | 0.86477 |  | 1.3738 |  | 0.69124 |  | 1.4835 |  | 3.7286 |  | 11.5409 |  | 4.967 |  | 3.9516 |  | 2.388 |  | 0.0015924 |  | 40 | 10 | 15 | 500 | 2022-11-12 | 21.8418 |  | 25
2022-10-08 | 39.65 |  | 368.8884 |  | 175.6606 |  | 0.87323 |  | 1.0248 |  | 0.53622 |  | 2.1764 |  | 3.0297 |  | 7.5043 |  | 6.9928 |  | 4.5982 |  | 2.5652 |  | 0.000799 |  | 40 | 10 | 15 | 500 | 2022-11-19 | 23.1149 |  | 25
2022-10-09 | 43.71 | 30.597 | 391.2713 |  | 203.1876 |  | 0.90706 |  | 1.3984 |  | 0.73365 |  | 1.5543 |  | 2.9705 |  | 7.8507 |  | 6.9774 |  | 4.8166 |  | 2.5882 |  | 0.0017113 |  | 40 | 10 | 15 | 500 | 2022-11-26 | 23.1619 |  | 25
2022-10-10 | 53.78 | 37.646 | 360.6836 |  | 169.8138 |  | 0.93707 |  | 1.1554 |  | 0.63306 |  | 1.3665 |  | 2.8552 |  | 8.2689 |  | 9.5761 |  | 4.4376 |  | 2.7801 |  | 0.0013156 |  | 40 | 10 | 15 | 500 | 2022-12-03 | 33.1278 | 23.1894 | 25
2022-10-11 | 39.43 |  | 451.0078 |  | 169.195 |  | 0.99995 |  | 0.89494 |  | 0.54691 |  | 2.064 |  | 4.5091 |  | 9.9418 |  | 4.3017 |  | 4.5983 |  | 2.6068 |  | 0.001705 |  | 40 | 10 | 15 | 500 | 2022-12-10 | 24.1557 |  | 25
2022-10-12 | 47.18 | 33.026 | 437.984 |  | 147.0962 |  | 1.0211 |  | 1.8495 |  | 0.932 |  | 1.5515 |  | 3.7738 |  | 10.3585 |  | 6.6947 |  | 4.9808 |  | 2.5265 |  | 0.00066854 |  | 40 | 10 | 15 | 500 | 2022-12-17 | 31.0782 | 21.7548 | 25
2022-10-13 | 38.92 |  | 494.4915 |  | 163.9838 |  | 0.97581 |  | 1.468 |  | 0.43315 |  | 1.7271 |  | 5.2083 |  | 11.8403 |  | 6.0758 |  | 4.5989 |  | 2.5475 |  | 0.00071595 |  | 40 | 10 | 15 | 500 | 2022-12-24 | 29.5985 | 20.719 | 25
2022-10-14 | 35.35 |  | 459.2207 |  | 174.2584 |  | 0.85137 |  | 1.6716 |  | 0.44877 |  | 1.269 |  | 3.2118 |  | 9.2771 |  | 5.5488 |  | 4.4705 |  | 3.0615 |  | 0.00077505 |  | 40 | 10 | 15 | 500 | 2022-12-31 | 26.2955 | 18.4069 | 25
2022-10-15 | 40.37 | 28.259 | 421.5591 |  | 158.2827 |  | 0.87907 |  | 1.4461 |  | 0.42376 |  | 1.753 |  | 3.6075 |  | 9.9504 |  | 4.2938 |  | 3.5123 |  | 2.6825 |  | 0.00085159 |  | 40 | 10 | 15 | 500
2022-10-16 | 40.31 | 28.217 | 445.924 |  | 149.9963 |  | 1.0324 |  | 2.326 |  | 0.52417 |  | 1.8188 |  | 2.943 |  | 12.1719 |  | 4.9064 |  | 4.4596 |  | 3.243 |  | 0.0011607 |  | 40 | 10 | 15 | 500
2022-10-17 | 21.16 |  | 237.9488 |  | 77.4215 |  | 0.7074 |  | 2.5145 |  | 0.60068 |  | 1.6205 |  | 4.1596 |  | 11.7097 |  | 4.2555 |  | 4.1314 |  | 3.0068 |  | 0.0010028 |  | 40 | 10 | 15 | 500
2022-10-18 | 15.47 |  | 178.3805 |  | 68.5527 |  | 0.80582 |  | 1.1471 |  | 0.62773 |  | 1.7779 |  | 2.5274 |  | 6.6775 |  | 6.8495 |  | 3.8291 |  | 3.0968 |  | 0.0014576 |  | 40 | 10 | 15 | 500
2022-10-19 | 11.68 |  | 349.701 |  | 125.0635 |  | 1.1906 |  | 0.69591 |  | 0.36156 |  | 1.1017 |  | 1.3318 |  | 1.9275 |  | 4.5349 |  | 3.6342 |  | 2.3848 |  | 0.001908 |  | 40 | 10 | 15 | 500
2022-10-20 | 15.5 |  | 440.1113 |  | 168.2871 |  | 1.1596 |  | 1.5667 |  | 0.4412 |  | 1.5705 |  | 1.1514 |  | 1.5202 |  | 5.9409 |  | 3.9571 |  | 2.7999 |  | 0.0013551 |  | 40 | 10 | 15 | 500
2022-10-21 | 23.61 |  | 428.0911 |  | 178.3551 |  | 0.99192 |  | 2.1912 |  | 0.5972 |  | 1.4035 |  | 2.5192 |  | 2.1389 |  | 5.6708 |  | 4.2382 |  | 3.0492 |  | 0.0031196 |  | 40 | 10 | 15 | 500
2022-10-22 | 37.99 |  | 409.8948 |  | 137.0604 |  | 0.98939 |  | 2.0826 |  | 0.58757 |  | 1.7423 |  | 3.1655 |  | 2.3408 |  | 7.753 |  | 3.6719 |  | 2.8417 |  | 0.0018385 |  | 40 | 10 | 15 | 500
2022-10-23 | 20.92 |  | 421.8901 |  | 156.7208 |  | 0.98392 |  | 1.8974 |  | 0.46833 |  | 1.3714 |  | 3.7732 |  | 3.2451 |  | 6.344 |  | 5.0707 |  | 3.3324 |  | 0.0016464 |  | 40 | 10 | 15 | 500
2022-10-24 | 25.1 |  | 308.5595 |  | 152.8787 |  | 1.2697 |  | 2.5419 |  | 0.59578 |  | 1.2324 |  | 5.1458 |  | 3.6514 |  | 4.9548 |  | 4.9879 |  | 3.2152 |  | 0.0011062 |  | 40 | 10 | 15 | 500
2022-10-25 | 34.21 |  | 348.3069 |  | 147.9864 |  | 1.1453 |  | 2.9338 |  | 0.63141 |  | 1.2116 |  | 2.271 |  | 1.9272 |  | 5.9159 |  | 3.4214 |  | 2.5473 |  | 0.0025123 |  | 40 | 10 | 15 | 500
2022-10-26 | 39.09 |  | 407.7447 |  | 146.3074 |  | 1.1725 |  | 2.2514 |  | 0.5125 |  | 0.29188 |  | 1.305 |  | 1.7371 |  | 4.4173 |  | 3.1383 |  | 2.415 |  | 0.0045334 |  | 40 | 10 | 15 | 500
2022-10-27 | 43.25 | 30.275 | 426.2919 |  | 148.0118 |  | 1.0204 |  | 2.1956 |  | 0.57892 |  | 0.99936 |  | 1.0581 |  | 2.8531 |  | 6.2758 |  | 3.9058 |  | 2.4767 |  | 0.015634 |  | 40 | 10 | 15 | 500
2022-10-28 | 36.36 |  | 302.2839 |  | 135.8177 |  | 1.019 |  | 2.88 |  | 0.73382 |  | 1.329 |  | 3.4133 |  | 5.4156 |  | 3.8258 |  | 4.6904 |  | 2.5796 |  | 0.020068 |  | 40 | 10 | 15 | 500
2022-10-29 | 42.54 | 29.778 | 375.9595 |  | 159.8368 |  | 1.0851 |  | 2.3802 |  | 0.61349 |  | 1.595 |  | 3.108 |  | 5.1919 |  | No Data |  | No Data |  | No Data |  | 0.015607 |  | 40 | 10 | 15 | 500
2022-10-30 | 52.54 | 36.778 | 340.3806 |  | 142.664 |  | 0.96087 |  | 2.4152 |  | 0.71431 |  | 1.5166 |  | 3.7563 |  | 5.0898 |  | No Data |  | No Data |  | No Data |  | 0.013853 |  | 40 | 10 | 15 | 500
2022-10-31 | 43.22 | 30.254 | 298.302 |  | 159.8831 |  | 1.4085 |  | 2.2745 |  | 0.67702 |  | 1.6502 |  | 1.8804 |  | 6.2479 |  | 6.0884 |  | 7.5507 |  | 2.3662 |  | 0.031906 |  | 40 | 10 | 15 | 500
2022-11-01 | 9.07 |  | 90.3358 |  | 27.7546 |  | 0.53252 |  | 2.9021 |  | 0.78494 |  | 1.478 |  | 0.85066 |  | 7.8903 |  | 6.8437 |  | 6.7395 |  | 2.1542 |  | 0.042816 |  | 40 | 10 | 15 | 500
2022-11-02 | 0 |  | 27.4506 |  | 2.953 |  | 0.20885 |  | 2.6527 |  | 0.83127 |  | 0.99559 |  | 0.39762 |  | 6.1201 |  | 8.7501 |  | 5.7161 |  | 2.8746 |  | 0.057184 |  | 40 | 10 | 15 | 500
2022-11-03 | 0 |  | 29.2316 |  | 3.1708 |  | 0.60057 |  | 1.7431 |  | 0.56272 |  | 1.7523 |  | 0.62953 |  | 10.0619 |  | 6.2227 |  | 5.9515 |  | 2.9714 |  | 0.048476 |  | 40 | 10 | 15 | 500
2022-11-04 | 21.43 |  | 65.7386 |  | 33.5468 |  | 0.46179 |  | 1.7008 |  | 0.48704 |  | 1.7946 |  | 0.49114 |  | 13.9729 |  | 7.0014 |  | 6.4238 |  | 2.9547 |  | 0.055872 |  | 40 | 10 | 15 | 500
2022-11-05 | 38.83 |  | 331.7245 |  | 177.0813 |  | 1.1654 |  | 1.8273 |  | 0.51397 |  | 2.3734 |  | 0.32232 |  | 14.3024 |  | 8.2697 |  | 7.8923 |  | 2.911 |  | 0.037971 |  | 40 | 10 | 15 | 500
2022-11-06 | 38.79 |  | 367.6467 |  | 156.1333 |  | 1.1628 |  | 2.1178 |  | 0.53569 |  | 1.8826 |  | 0.45398 |  | 3.1606 |  | 6.8554 |  | 6.262 |  | 2.7482 |  | 0.055234 |  | 40 | 10 | 15 | 500
2022-11-07 | 27.98 |  | 362.4367 |  | 165.0761 |  | 1.5428 |  | 2.3561 |  | 0.53711 |  | 1.5206 |  | 0.35927 |  | 3.0111 |  | 6.3148 |  | 6.069 |  | 2.84 |  | 0.070809 |  | 40 | 10 | 15 | 500
2022-11-08 | 24.3 |  | 341.4357 |  | 155.8458 |  | 1.1542 |  | 1.1719 |  | 0.39872 |  | 1.6566 |  | 0.43619 |  | 2.4466 |  | 6.6491 |  | 6.1638 |  | 2.9454 |  | 0.086756 |  | 40 | 10 | 15 | 500
2022-11-09 | 16.44 |  | 302.8451 |  | 167.184 |  | 1.1128 |  | 1.924 |  | 0.50707 |  | 1.5307 |  | 0.46144 |  | 2.9021 |  | 6.7198 |  | 5.9708 |  | 2.9762 |  | 0.10814 |  | 40 | 10 | 15 | 500
2022-11-10 | 15.13 |  | 299.2338 |  | 163.1359 |  | 1.092 |  | 1.0586 |  | 0.37302 |  | 1.824 |  | 0.2988 |  | 4.4718 |  | 5.6332 |  | 6.1474 |  | 2.7571 |  | 0.085619 |  | 40 | 10 | 15 | 500
2022-11-11 | 21.18 |  | 296.8136 |  | 157.785 |  | 1.1254 |  | 0.93651 |  | 0.59048 |  | 1.788 |  | 0.18103 |  | 2.8538 |  | 7.7249 |  | 7.2944 |  | 2.4502 |  | 0.081899 |  | 40 | 10 | 15 | 500
2022-11-12 | 24.11 |  | 373.7024 |  | 182.3434 |  | 1.2099 |  | 0.54584 |  | 0.41613 |  | 2.2365 |  | 1.5933 |  | 2.109 |  | 4.0765 |  | 4.3081 |  | 2.4619 |  | 0.055718 |  | 40 | 10 | 15 | 500
2022-11-13 | 39.37 |  | 457.7305 |  | 155.3984 |  | 1.4983 |  | 0.79342 |  | 0.34922 |  | 2.0951 |  | 1.7378 |  | 3.0437 |  | 6.592 |  | 8.8243 |  | 3.1041 |  | 0.03863 |  | 40 | 10 | 15 | 500
2022-11-14 | 50.23 | 35.161 | 442.6337 |  | 177.5185 |  | 1.2482 |  | 1.3543 |  | 0.39925 |  | 1.4604 |  | 2.6751 |  | 5.7552 |  | 2.8838 |  | 6.6656 |  | 3.217 |  | 0.031516 |  | 40 | 10 | 15 | 500
2022-11-15 | 48.28 |  | 329.9209 |  | 171.5791 |  | 1.362 |  | 1.4601 |  | 0.37779 |  | 2.3309 |  | 3.5236 |  | 5.2348 |  | 0.74112 |  | 5.9903 |  | 3.1569 |  | 0.038908 |  | 40 | 10 | 15 | 500
2022-11-16 | 30.43 | 33.796 | 174.0804 |  | 87.5288 |  | 0.73361 |  | 1.3793 |  | 0.41063 |  | 1.6103 |  | 4.5241 |  | 8.8211 |  | 0.65728 |  | 4.7419 |  | 3.0955 |  | 0.044881 |  | 40 | 10 | 15 | 500
2022-11-17 | 28.18 |  | 323.7898 |  | 143.489 |  | 0.96972 |  | 1.3224 |  | 0.41441 |  | 1.6662 |  | 4.6137 |  | 9.0007 |  | 0.67515 |  | 5.6888 |  | 3.2414 |  | 0.034015 |  | 40 | 10 | 15 | 500
2022-11-18 | 42.01 | 29.407 | 345.1359 |  | 125.5501 |  | 0.89264 |  | 1.6084 |  | 0.43012 |  | 1.6151 |  | 3.2265 |  | 10.1429 |  | 0.98531 |  | 6.4994 |  | 3.0652 |  | 0.010102 |  | 40 | 10 | 15 | 500
2022-11-19 | 51.3 | 35.91 | 332.6005 |  | 128.5571 |  | 0.91288 |  | 1.7838 |  | 0.42433 |  | 2.6058 |  | 2.7668 |  | 12.4558 |  | 2.3702 |  | 6.3623 |  | 2.839 |  | 0.0094351 |  | 40 | 10 | 15 | 500
2022-11-20 | 80.2 | 56.14 | 375.8409 |  | 161.4511 |  | 0.99576 |  | 1.8677 |  | 0.44124 |  | 1.9112 |  | 3.779 |  | 13.4141 |  | 2.3837 |  | 5.7847 |  | 2.721 |  | 0.0083197 |  | 40 | 10 | 15 | 500
2022-11-21 | 68.24 | 47.768 | 345.4243 |  | 122.0558 |  | 1.1508 |  | 1.5132 |  | 0.38086 |  | 1.87 |  | 3.258 |  | 11.3686 |  | 2.1704 |  | 6.1709 |  | 2.5308 |  | 0.013439 |  | 40 | 10 | 15 | 500
2022-11-22 | 71.22 | 49.854 | 443.2322 |  | 165.7151 |  | 1.0286 |  | 1.5816 |  | 0.39808 |  | 1.9996 |  | 2.5833 |  | 9.2987 |  | 3.2131 |  | 6.2324 |  | 2.3157 |  | 0.0016671 |  | 40 | 10 | 15 | 500
2022-11-23 | 58.09 | 40.663 | 503.6503 | 402.9202 | 146.4382 |  | 1.3111 |  | 1.4041 |  | 0.39376 |  | 2.3505 |  | 2.6095 |  | 10.5836 |  | 5.0881 |  | 5.8301 |  | 2.2584 |  | 0.082772 |  | 40 | 10 | 15 | 500
2022-11-24 | 50.83 | 35.581 | 460.3239 |  | 124.1012 |  | 1.2044 |  | 1.1494 |  | 0.3839 |  | 2.4003 |  | 1.9562 |  | 8.6609 |  | 8.1976 |  | 6.1036 |  | 2.6466 |  | 0.0080777 |  | 40 | 10 | 15 | 500
2022-11-25 | 59.95 | 41.965 | 442.3568 |  | 123.8298 |  | 1.3918 |  | 1.5354 |  | 0.52056 |  | 2.3493 |  | 1.7639 |  | 9.0767 |  | 2.5851 |  | 5.6038 |  | 2.7884 |  | 0.0017293 |  | 40 | 10 | 15 | 500
2022-11-26 | 43.41 | 30.387 | 499.6921 |  | 136.1818 |  | 1.3357 |  | 1.3897 |  | 0.44264 |  | 2.7683 |  | 2.4642 |  | 11.3912 |  | 2.2021 |  | 6.2002 |  | 2.8394 |  | 0.00043346 |  | 40 | 10 | 15 | 500
2022-11-27 | 21.49 |  | 576.4615 | 461.1692 | 161.6025 |  | 1.2913 |  | 1.387 |  | 0.45726 |  | 2.6917 |  | 2.9779 |  | 15.0486 | 10.534 | 5.8591 |  | 12.5603 |  | 4.2543 |  | 0.0024442 |  | 40 | 10 | 15 | 500
2022-11-28 | 23.16 |  | 453.868 |  | 162.5585 |  | 1.3361 |  | 1.3029 |  | 0.46301 |  | 2.0543 |  | 2.1517 |  | 7.8238 |  | 9.0598 |  | 5.8147 |  | 4.373 |  | 0.017174 |  | 40 | 10 | 15 | 500
2022-11-29 | 35.84 |  | 351.5424 |  | 133.4796 |  | 1.2314 |  | 0.59486 |  | 0.38966 |  | 0.96255 |  | 1.3353 |  | 2.4601 |  | 7.9827 |  | 0.98823 |  | 2.6798 |  | 0.076416 |  | 40 | 10 | 15 | 500
2022-11-30 | 19.65 |  | 423.0605 |  | 137.5553 |  | 1.2967 |  | 1.6223 |  | 0.53648 |  | 0.21042 |  | 1.3903 |  | 2.4929 |  | 8.0122 |  | 0.9755 |  | 2.5622 |  | 0.079182 |  | 40 | 10 | 15 | 500
2022-12-01 | 15.31 |  | 429.488 |  | 113.9849 |  | 1.1624 |  | 3.7473 |  | 0.93277 |  | 0.23825 |  | 2.7259 |  | 6.118 |  | 4.0671 |  | 3.0216 |  | 3.9478 |  | 0.047101 |  | 40 | 10 | 15 | 500
2022-12-02 | 20.15 |  | 496.1878 |  | 144.5241 |  | 1.1783 |  | 2.2943 |  | 0.59115 |  | 0.91495 |  | 3.2946 |  | 8.3107 |  | 2.2637 |  | 7.3414 |  | 4.0101 |  | 0.055041 |  | 40 | 10 | 15 | 500
2022-12-03 | 16.01 |  | 413.5647 |  | 117.0893 |  | 1.1511 |  | 2.1916 |  | 0.72235 |  | 2.204 |  | 3.324 |  | 10.9045 |  | 5.5298 |  | 4.0194 |  | 4.2886 |  | 0.013909 |  | 40 | 10 | 15 | 500
2022-12-04 | 32.36 |  | 453.3939 |  | 140.136 |  | 1.1511 |  | 1.6245 |  | 0.71745 |  | 2.2367 |  | 3.3714 |  | 8.4091 |  | 4.4474 |  | 3.5325 |  | 4.3671 |  | 0.036549 |  | 40 | 10 | 15 | 500
2022-12-05 | 51.13 | 35.791 | 497.3711 |  | 153.5112 |  | 1.5241 |  | 1.9966 |  | 0.9084 |  | 2.2817 |  | 2.6129 |  | 11.3107 |  | 6.0486 |  | 4.4196 |  | 4.8672 |  | 0.013247 |  | 40 | 10 | 15 | 500
2022-12-06 | 54.69 | 38.283 | 459.9395 |  | 152.1318 |  | 0.92042 |  | 1.8461 |  | 0.73399 |  | 2.7567 |  | 2.8757 |  | 10.3453 |  | 7.6265 |  | 5.3815 |  | 4.8048 |  | 0.0028528 |  | 40 | 10 | 15 | 500
2022-12-07 | 19.62 |  | 100.6107 |  | 24.5351 |  | 0.35388 |  | 1.9517 |  | 0.70694 |  | 3.0091 |  | 3.0402 |  | 3.2749 |  | 9.4077 |  | 8.0518 |  | 4.9015 |  | 0.0038912 |  | 40 | 10 | 15 | 500
2022-12-08 | 38.44 |  | 268.7672 |  | 99.5355 |  | 0.49167 |  | 2.1789 |  | 0.87261 |  | 1.6875 |  | 3.0437 |  | 2.4126 |  | 7.5922 |  | 8.0973 |  | 3.5837 |  | 0.018729 |  | 40 | 10 | 15 | 500
2022-12-09 | 35.68 |  | 422.1885 |  | 127.7644 |  | 0.80506 |  | 2.6853 |  | 0.64249 |  | 1.7082 |  | 3.4438 |  | 2.87 |  | 4.8421 |  | 7.0708 |  | 2.6574 |  | 0.042041 |  | 40 | 10 | 15 | 500
2022-12-10 | 68.66 | 48.062 | 544.6743 | 435.7394 | 149.7062 |  | 0.90081 |  | 2.2796 |  | 0.87277 |  | 3.0075 |  | 3.6457 |  | 5.0345 |  | 7.5245 |  | 11.0306 |  | 2.9977 |  | 0.023662 |  | 40 | 10 | 15 | 500
2022-12-11 | 74.69 | 52.283 | 497.7783 |  | 130.8425 |  | 0.81663 |  | 4.2529 |  | 1.1152 |  | 2.7859 |  | 4.3602 |  | 6.2419 |  | 5.3641 |  | 10.1533 |  | 2.82 |  | 0.034828 |  | 40 | 10 | 15 | 500
2022-12-12 | 72.26 | 50.582 | 438.2553 |  | 127.8565 |  | 0.85248 |  | 2.9113 |  | 1.0882 |  | 2.1749 |  | 4.3382 |  | 6.4754 |  | 5.2983 |  | 12.614 |  | 3.062 |  | 0.085731 |  | 40 | 10 | 15 | 500
2022-12-13 | 71.69 | 50.183 | 475.2549 |  | 127.3617 |  | 1.0026 |  | 2.6966 |  | 0.9725 |  | 2.0112 |  | 3.321 |  | 5.1251 |  | 4.2451 |  | 6.6837 |  | 2.8626 |  | 0.064589 |  | 40 | 10 | 15 | 500
2022-12-14 | 43.43 | 30.401 | 144.2718 |  | 39.8106 |  | 0.3786 |  | 3.694 |  | 0.6629 |  | 1.8333 |  | 3.5149 |  | 6.8242 |  | 4.2801 |  | 6.9232 |  | 3.23 |  | 0.051778 |  | 40 | 10 | 15 | 500
2022-12-15 | 47.86 | 33.502 | 326.23 |  | 91.7703 |  | 0.61209 |  | 3.4185 |  | 0.568 |  | 2.8557 |  | 3.2977 |  | 6.3868 |  | 4.1429 |  | 6.4062 |  | 2.8959 |  | 0.061748 |  | 40 | 10 | 15 | 500
2022-12-16 | 70.88 | 49.616 | 209.3547 |  | 63.839 |  | 1.032 |  | 3.2687 |  | 0.42186 |  | 1.9687 |  | 3.4295 |  | 7.7599 |  | 5.0455 |  | 7.6123 |  | 3.0066 |  | 0.054828 |  | 40 | 10 | 15 | 500
2022-12-17 | 67.41 | 47.187 | 196.4834 |  | 61.4258 |  | 1.1823 |  | 2.5127 |  | 0.46424 |  | 2.4056 |  | 2.989 |  | 5.8547 |  | 4.1645 |  | 5.7729 |  | 2.5709 |  | 0.013623 |  | 40 | 10 | 15 | 500
2022-12-18 | 64.41 | 45.087 | 189.5197 |  | 60.2028 |  | 0.83094 |  | 3.4983 |  | 0.82716 |  | 2.091 |  | 3.293 |  | 7.8493 |  | 6.4915 |  | 7.928 |  | 3.1345 |  | 0.02916 |  | 40 | 10 | 15 | 500
2022-12-19 | 40.31 | 28.217 | 131.999 |  | 51.77 |  | 0.80001 |  | 1.8851 |  | 0.57441 |  | 1.7821 |  | 1.9852 |  | 5.4538 |  | 4.3447 |  | 6.7638 |  | 2.8753 |  | 0.00088666 |  | 40 | 10 | 15 | 500
2022-12-20 | 0 |  | 41.8595 |  | 5.552 |  | 0.30085 |  | 1.9852 |  | 0.36014 |  | 1.3644 |  | 2.239 |  | 6.0079 |  | 3.5949 |  | 4.6226 |  | 2.3799 |  | 0.02051 |  | 40 | 10 | 15 | 500
2022-12-21 | 3.54 |  | 43.8537 |  | 5.4013 |  | 0.27782 |  | 2.5641 |  | 0.4526 |  | 1.2989 |  | 2.6308 |  | 2.7271 |  | 3.4484 |  | 4.7769 |  | 1.664 |  | 0.0034188 |  | 40 | 10 | 15 | 500
2022-12-22 | 57.98 | 40.586 | 41.3251 |  | 21.8109 |  | 0.56952 |  | 2.6373 |  | 0.62143 |  | 1.2879 |  | 1.6523 |  | 3.0801 |  | 4.8442 |  | 10.1937 |  | 1.7013 |  | 0.0023321 |  | 40 | 10 | 15 | 500
2022-12-23 | 57.41 | 40.187 | 62.0901 |  | 93.9847 |  | 0.97148 |  | 2.6826 |  | 0.59033 |  | 2.2216 |  | 1.8896 |  | 2.6034 |  | 5.4176 |  | 11.7468 |  | 1.8672 |  | 0.017665 |  | 40 | 10 | 15 | 500
2022-12-24 | 73.41 | 51.387 | 171.5594 |  | 97.9973 |  | 0.81531 |  | 2.7413 |  | 0.76207 |  | 2.8171 |  | 1.9457 |  | 2.842 |  | 7.6163 |  | 11.9575 |  | 1.8642 |  | 0.017689 |  | 40 | 10 | 15 | 500
2022-12-25 | 47.06 | 32.942 | 150.4451 |  | 91.546 |  | 0.79151 |  | 2.0736 |  | 1.1774 |  | 2.237 |  | 2.2062 |  | 2.2792 |  | 8.3042 |  | 8.592 |  | 1.8622 |  | 0.0033681 |  | 40 | 10 | 15 | 500
2022-12-26 | 60.42 | 42.294 | 127.1558 |  | 83.5134 |  | 0.9424 |  | 1.753 |  | 1.1023 |  | 3.1469 |  | 2.8754 |  | 3.0873 |  | 12.6259 |  | 12.8129 |  | 1.9892 |  | 0.0036447 |  | 40 | 10 | 15 | 500
2022-12-27 | 64.88 | 45.416 | 63.2067 |  | 44.1358 |  | 0.88961 |  | 1.6127 |  | 1.1025 |  | 2.2379 |  | 2.5885 |  | 2.9773 |  | 16.0801 | 11.2561 | 15.579 | 10.9053 | 2.0045 |  | 0.053404 |  | 40 | 10 | 15 | 500
2022-12-28 | 44.56 | 31.192 | 173.157 |  | 68.483 |  | 1.0105 |  | 1.6866 |  | 0.99359 |  | 2.0656 |  | 2.235 |  | 2.7061 |  | 13.1408 |  | 12.9928 |  | 1.8663 |  | 0.18927 |  | 40 | 10 | 15 | 500
2022-12-29 | 44.15 | 30.905 | 480.3781 |  | 167.5484 |  | 0.96314 |  | 1.4325 |  | 0.90202 |  | 2.7363 |  | 3.2503 |  | 2.826 |  | 5.0829 |  | 5.7583 |  | 1.6735 |  | 0.25196 |  | 40 | 10 | 15 | 500
2022-12-30 | 52.37 | 36.659 | 506.3506 | 405.0805 | 165.6001 |  | 1.2839 |  | 1.2064 |  | 0.81714 |  | 1.7989 |  | 1.3454 |  | 1.9384 |  | 4.9989 |  | 5.6387 |  | 1.2519 |  | 0.232 |  | 40 | 10 | 15 | 500
2022-12-31 | 56.97 | 39.879 | 454.9729 |  | 171.1282 |  | 1.058 |  | 1.6933 |  | 0.90237 |  | 2.937 |  | 1.2893 |  | 2.3984 |  | 6.4005 |  | 6.3463 |  | 1.7304 |  | 0.23461 |  | 40 | 10 | 15 | 500
Formulas:
Source = [Source, row above]+7
Note on U34: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Part A reference - S5N_22_75A (Fan 4, 5 and 6 loss of data)
Note on W34: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Part A reference - S5N_22_75A (Fan 4, 5 and 6 loss of data)
Note on Y34: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Part A reference - S5N_22_75A (Fan 4, 5 and 6 loss of data)
Note on C37: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Plant offline until 04/11/22
Note on D56: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Part A reference - S5N_22_80A (Main stack particulate breach November)
Note on D76: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Part A reference - S5N_23_02A (Main stack particulate breach December)
Note on C86: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Plant offline until 22/12/22