## Notes
Reference conditions
All concentrations in this spreadsheet are reported in dry air at a temperature of 273K, at a pressure of 101.3 kPa and with an oxygen content of 3% dry
Uncertainty
Concentrations in this spreadsheet are reported after having subtracted the value of the 95% confidence interval (see Section 3.6.7 of the permit):
95% confidence interval for nitrogen oxides is taken to be 20%
95% confidence interval for sulphur dioxide is taken to be 20%
95% confidence interval for dust is taken to be 30%
95% confidence interval for carbon monoxide is taken to be 10%
Normal operating conditions
The document "Power Plant Boiler Abnormal Conditions" sets out the criteria for excluding emissions monitoring data from permitting or other reporting obligations:
| Parameter | Plant | Level representing abnormal conditions
| Boiler oxygen | All boilers | >17% oxygen
| Fuel input | A51, A52A, A52B, A53 and A62 | <50% BFG by thermal input
|  | A50 (Service Boilers) | <35% BFG by thermal input

## Summary
Dust concentrations in mg/m³ (except A55 as % obscuration), reported as measured (uncertainty not taken into account)
| Source | A1 | A2 | A8A | A8B | A9 | A10 | A10A | A14 | A15 | A16 | A55 | A63 | A1 | A1
| Description | Sinter plant main stack (particulate) | Sinter plant deduster stack | BF4 casthouse fume extraction North | BF4 casthouse fume extraction South | BF5 casthouse fume extraction | Iron desulphurisation/hot metal pouring fume extraction plant stack | Hot metal fume extraction no. 2 | Secondary fume extraction stack North | Secondary fume extraction stack Centre | Secondary fume extraction stack South | Morfa main stack | CASOB/ desulph fume extraction plant | Sinter plant main stack (SO2) | Sinter plant main stack (NOX)
Daily means | Minimum | 0.15 | 0.11 | 0.54 | 0.32 | 0.14 | 0 | 0.34 | 0.54 | 2.26 | 0.81 |  | 8.9857e-06 | 16.87 | 20.63
| Maximum | 72.32 | 1.64 | 2.97 | 1.4 | 2.59 | 20.19 | 16.79 | 16.76 | 12.63 | 3.73 |  | 0.041124 | 623.72 | 188.31
| Limit | 40 | 10 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 500 | 500
| No. > Limit | 39 | 0 | 0 | 0 | 0 | 1 | 2 | 1 | 0 | 0 |  | 0 | 5 | 0
| No. > Limit w Uncert | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
Weekly mean | Minimum | [10 empty] | 20.029
| Maximum | [10 empty] | 43.3194
| Limit | [10 empty] | 25
| No. > Limit | [10 empty] | 7
| No. > Limit w Uncert | [10 empty] | 2

## Plots
NOTES

## Data
| Measured concentrations - daily means (mg/m³) | [25 empty] | Limits |  |  |  |  | Obscuration %
Source | A1 | A1 | A1 | A1 | A1 | A1 | A2 | A2 | A8A | A8A | A8B | A8B | A9 | A9 | A10 | A10 | A10A | A10A | A14 | A14 | A15 | A15 | A16 | A16 | A63 | A63 | A1 | A2 | BF and BOS plant sources | A1 | Source | A55
Description | Sinter plant main stack (Particulate) | Sinter plant main stack (Particulate) Uncertainty Applied | Sinter plant main stack (SO2) | Sinter plant main stack (SO2) Uncertainty Applied | Sinter plant main stack (NOX) | Sinter plant main stack (NOx) Uncertainty Applied | Sinter plant deduster stack | Sinter plant deduster stack Uncertainty Applied | BF4 casthouse fume extraction North | BF4 casthouse fume extraction North Uncertainty Applied | BF4 casthouse fume extraction South | BF4 casthouse fume extraction South Uncertainty Applied | BF5 casthouse fume extraction | BF5 casthouse fume extraction | Iron desulphurisation/hot metal pouring fume extraction plant stack | Iron desulphurisation/hot metal pouring fume extraction plant stack Uncertainty Applied | Hot metal fume extraction no. 2 | Hot metal fume extraction no. 2 Uncetainty Applied | Secondary fume extraction stack North | Secondary fume extraction stack North Uncertainty Applied | Secondary fume extraction stack Centre | Secondary fume extraction stack Centre Uncertainty Applied | Secondary fume extraction stack South | Secondary fume extraction stack South Uncertainty Applied | CASOB/ desulph fume extraction plant | CASOB/ desulph fume extraction plant Uncertainty Applied | Sinter plant main stack | Sinter plant deduster stack |  | Sinter Plant Main Stack SO2 & NOX | Description | Morfa main stack
Date / Uncertainty |  | 30% |  | 20% |  | 20% |  | 30% |  | 30% |  | 30% |  | 30% |  | 30% |  | 30% |  | 30% |  | 30% |  | 30% |  | 30% |  |  |  |  | Week commencing | Measured | Uncertainty Applied 30% | Limit | Schedule 5 Notification
2022-07-01 | 17.54 |  | 159.26 |  | 118.16 |  | 0.56 |  | 1.26 |  | 0.32 |  | 2.21 |  | 4.19 |  | 7.09 |  | 2.73 |  | 2.63 |  | 2.09 |  | 0.00051401 |  | 40 | 10 | 15 | 500 | 2022-07-02 | 20.1521 |  | 25
2022-07-02 | 35.04 |  | 274.73 |  | 150.3 |  | 0.6 |  | 0.93 |  | 0.46 |  | 2.05 |  | 3.32 |  | 7.13 |  | 2.81 |  | 2.83 |  | 2.01 |  | 0.00080147 |  | 40 | 10 | 15 | 500 | 2022-07-09 | 20.029 |  | 25
2022-07-03 | 21.59 |  | 136.22 |  | 93.74 |  | 0.55 |  | 1 |  | 0.51 |  | 2.05 |  | 3.83 |  | 7.05 |  | 3.17 |  | 2.83 |  | 2.13 |  | 0.0003068 |  | 40 | 10 | 15 | 500 | 2022-07-16 | 21.2681 |  | 25
2022-07-04 | 36.94 |  | 256.63 |  | 129.06 |  | 0.55 |  | 1.45 |  | 0.57 |  | 1.84 |  | 4.44 |  | 7.08 |  | 1.34 |  | 2.98 |  | 2.15 |  | 0.00012874 |  | 40 | 10 | 15 | 500 | 2022-07-23 | 23.7407 |  | 25
2022-07-05 | 42.07 | 29.449 | 251.52 |  | 141.68 |  | 0.59 |  | 1.58 |  | 0.69 |  | 1.79 |  | 6.43 |  | 4.71 |  | 1.42 |  | 2.67 |  | 2.08 |  | 5.73e-05 |  | 40 | 10 | 15 | 500 | 2022-07-30 | 27.6244 | 19.3371 | 25
2022-07-06 | 43.99 | 30.793 | 304.62 |  | 129.2 |  | 0.58 |  | 1.51 |  | 0.69 |  | 1.63 |  | 5.57 |  | 2 |  | 0.79 |  | 3.13 |  | 2.04 |  | 7.2514e-05 |  | 40 | 10 | 15 | 500 | 2022-08-06 | 32.6612 | 22.8628 | 25
2022-07-07 | 36.59 |  | 274.73 |  | 150.18 |  | 0.63 |  | 1.45 |  | 0.86 |  | 2.1 |  | 2.25 |  | 12.13 |  | 0.54 |  | 5.24 |  | 2.16 |  | 0.0001174 |  | 40 | 10 | 15 | 500 | 2022-08-13 | 32.4443 | 22.711 | 25
2022-07-08 | 36.56 |  | 301.84 |  | 156.08 |  | 0.75 |  | 1.66 |  | 0.81 |  | 1.62 |  | 1.26 |  | 13.43 |  | 4.76 |  | 4.25 |  | 2.39 |  | 4.2471e-05 |  | 40 | 10 | 15 | 500 | 2022-08-20 | 37.2187 | 26.0531 | 25 | S5N_22_61A
2022-07-09 | 38.01 |  | 248.93 |  | 131.19 |  | 0.7 |  | 1.68 |  | 0.87 |  | 2.04 |  | 3.78 |  | 7.78 |  | 6.51 |  | 4.9 |  | 2.44 |  | 9.78e-05 |  | 40 | 10 | 15 | 500 | 2022-08-27 | 43.3194 | 30.3236 | 25 | S5N_22_62A
2022-07-10 | 26.78 |  | 235.24 |  | 136.33 |  | 0.87 |  | 2.25 |  | 0.99 |  | 1.74 |  | 5.07 |  | 3.1 |  | 7.82 |  | 5.31 |  | 2.52 |  | 0.00014867 |  | 40 | 10 | 15 | 500 | 2022-09-03 | 32.6064 | 22.8245 | 25
2022-07-11 | 31.61 |  | 170.03 |  | 138.22 |  | 0.92 |  | 1.72 |  | 0.74 |  | 1.72 |  | 6.35 |  | 3.03 |  | 4.74 |  | 4.82 |  | 2.39 |  | 6.02e-05 |  | 40 | 10 | 15 | 500 | 2022-09-10 | 21.8174 |  | 25
2022-07-12 | 52.4 | 36.68 | 244.17 |  | 139.41 |  | 0.97 |  | 1.17 |  | 0.81 |  | 2.29 |  | 4.32 |  | 4.09 |  | 3.73 |  | 4.41 |  | 2.36 |  | 3.3657e-05 |  | 40 | 10 | 15 | 500 | 2022-09-17 | 26.5288 | 18.5701 | 25
2022-07-13 | 37.58 |  | 113.92 |  | 76.8 |  | 0.59 |  | 1.22 |  | 0.72 |  | 1.69 |  | 3.33 |  | 4.23 |  | 5.97 |  | 4.09 |  | 2.35 |  | 4.3957e-05 |  | 40 | 10 | 15 | 500 | 2022-09-24 | 24.7387 |  | 25
2022-07-14 | 50.93 | 35.651 | 247.3 |  | 127.58 |  | 0.9 |  | 1.32 |  | 0.84 |  | 2.03 |  | 3.26 |  | 5.09 |  | 6.3 |  | 4.37 |  | 2.41 |  | 6.5886e-05 |  | 40 | 10 | 15 | 500
2022-07-15 | 65.43 | 45.801 | 224.59 |  | 147.09 |  | 0.98 |  | 1.16 |  | 0.78 |  | 2.43 |  | 5.67 |  | 9.18 |  | 7.04 |  | 5.35 |  | 2.64 |  | 4.4514e-05 |  | 40 | 10 | 15 | 500
2022-07-16 | 59.22 | 41.454 | 246.59 |  | 153.23 |  | 1.43 |  | 1.17 |  | 0.76 |  | 1.97 |  | 6.62 |  | 6.79 |  | 8.4 |  | 5.53 |  | 2.57 |  | 6.4671e-05 |  | 40 | 10 | 15 | 500
2022-07-17 | 62.82 | 43.974 | 228.34 |  | 146.34 |  | 1.64 |  | 1.55 |  | 0.96 |  | 2.21 |  | 6.02 |  | 8.05 |  | 10.24 |  | 6.26 |  | 2.8 |  | 2.37e-05 |  | 40 | 10 | 15 | 500
2022-07-18 | 52.12 | 36.484 | 166.42 |  | 121.99 |  | 1.33 |  | 1.38 |  | 0.88 |  | 1.95 |  | 5.73 |  | 4.63 |  | 8.43 |  | 4.75 |  | 2.55 |  | 2.42e-05 |  | 40 | 10 | 15 | 500
2022-07-19 | 48.93 | 34.251 | 228.68 |  | 142.62 |  | 1.51 |  | 0.91 |  | 0.7 |  | 1.87 |  | 7 |  | 1.49 |  | 9.24 |  | 5.95 |  | 2.63 |  | 0.00019091 |  | 40 | 10 | 15 | 500
2022-07-20 | 1.17 |  | 16.87 |  | 32.71 |  | 0.33 |  | 1.28 |  | 0.79 |  | 0.94 |  | 6.25 |  | 1.41 |  | 5.22 |  | 4.39 |  | 2.41 |  | 4.0314e-05 |  | 40 | 10 | 15 | 500
2022-07-21 | 25.13 |  | 90.2 |  | 79.5 |  | 0.67 |  | 1.36 |  | 0.9 |  | 1.33 |  | 7.34 |  | 2.66 |  | 5.09 |  | 4.37 |  | 2.27 |  | 4.7029e-05 |  | 40 | 10 | 15 | 500
2022-07-22 | 57.92 | 40.544 | 259.03 |  | 99.1 |  | 0.9 |  | 1.21 |  | 0.68 |  | 1.84 |  | 8.3 |  | 3.69 |  | 6.28 |  | 4.94 |  | 2.48 |  | 5.2814e-05 |  | 40 | 10 | 15 | 500
2022-07-23 | 64.76 | 45.332 | 373.46 |  | 125.88 |  | 0.92 |  | 1.1 |  | 0.74 |  | 1.94 |  | 6.33 |  | 2.43 |  | 5.25 |  | 4.2 |  | 2.5 |  | 0.00019817 |  | 40 | 10 | 15 | 500
2022-07-24 | 57.26 | 40.082 | 243.12 |  | 80.96 |  | 0.85 |  | 1.07 |  | 0.64 |  | 1.29 |  | 2.76 |  | 1.34 |  | 2.55 |  | 2.53 |  | 1.93 |  | 0.0013391 |  | 40 | 10 | 15 | 500
2022-07-25 | 53.02 | 37.114 | 252.88 |  | 93.73 |  | 0.92 |  | 1.08 |  | 0.53 |  | 0.44 |  | 6.16 |  | 0.68 |  | 1.79 |  | 2.36 |  | 1.74 |  | 0.001024 |  | 40 | 10 | 15 | 500
2022-07-26 | 66.54 | 46.578 | 371.87 |  | 141.3 |  | 0.96 |  | 0.83 |  | 0.57 |  | 0.5 |  | 2.14 |  | 0.34 |  | 2.26 |  | 2.74 |  | 2.16 |  | 0.00029721 |  | 40 | 10 | 15 | 500
2022-07-27 | 72.32 | 50.624 | 432.22 |  | 128.81 |  | 0.72 |  | 1.12 |  | 0.66 |  | 1.41 |  | 5 |  | 0.43 |  | 4.06 |  | 4.12 |  | 2.31 |  | 0.00036346 |  | 40 | 10 | 15 | 500
2022-07-28 | 27.13 |  | 235.95 |  | 85.03 |  | 0.33 |  | 1.09 |  | 0.7 |  | 1.58 |  | 6.64 |  | 3.08 |  | 5.31 |  | 4.75 |  | 2.47 |  | 3.84e-05 |  | 40 | 10 | 15 | 500
2022-07-29 | 0.15 |  | 98.94 |  | 39.1 |  | 0.11 |  | 1.48 |  | 0.86 |  | 1.53 |  | 9.18 |  | 0.85 |  | 8.61 |  | 6.76 |  | 2.67 |  | 8.8943e-05 |  | 40 | 10 | 15 | 500
2022-07-30 | 32.84 |  | 322.77 |  | 112.71 |  | 0.37 |  | 1.41 |  | 0.85 |  | 1.31 |  | 8.18 |  | 1.81 |  | 7.28 |  | 5.63 |  | 2.61 |  | 0.0002746 |  | 40 | 10 | 15 | 500
2022-07-31 | 42.71 | 29.897 | 408.46 |  | 158.47 |  | 0.35 |  | 1.26 |  | 0.8 |  | 1.4 |  | 7.67 |  | 1.3 |  | 5.91 |  | 4.87 |  | 2.47 |  | 0.00026119 |  | 40 | 10 | 15 | 500
2022-08-01 | 47.62 | 33.334 | 379.84 |  | 175.74 |  | 0.35 |  | 1.13 |  | 0.67 |  | 1.3 |  | 8.51 |  | 1.2 |  | 6.38 |  | 4.85 |  | 2.49 |  | 0.0011469 |  | 40 | 10 | 15 | 500
2022-08-02 | 49.43 | 34.601 | 416.06 |  | 165.53 |  | 0.38 |  | 0.98 |  | 0.64 |  | 1.43 |  | 8.24 |  | 1.48 |  | 5.4 |  | 4.59 |  | 2.45 |  | 0.00068584 |  | 40 | 10 | 15 | 500
2022-08-03 | 29.97 |  | 243.92 |  | 87.74 |  | 0.38 |  | 0.89 |  | 0.43 |  | 1.46 |  | 4.18 |  | 1.76 |  | 7.1 |  | 5.35 |  | 2.51 |  | 0.00040184 |  | 40 | 10 | 15 | 500
2022-08-04 | 28.25 |  | 252.86 |  | 100.97 |  | 0.33 |  | 2.97 |  | 1.4 |  | 1.69 |  | 1.85 |  | 1.23 |  | 6.4 |  | 3.85 |  | 2.69 |  | 0.00028406 |  | 40 | 10 | 15 | 500
2022-08-05 | 35.36 |  | 302.85 |  | 127.62 |  | 0.28 |  | 0.7 |  | 0.4 |  | 1.4 |  | 1.98 |  | 1.04 |  | 4.26 |  | 2.78 |  | 2.39 |  | 0.0023302 |  | 40 | 10 | 15 | 500
2022-08-06 | 37.93 |  | 370.49 |  | 132.25 |  | 0.43 |  | 0.55 |  | 0.55 |  | 1.69 |  | 4.66 |  | 2.12 |  | 6.75 |  | 5.1 |  | 2.59 |  | 0.00019616 |  | 40 | 10 | 15 | 500
2022-08-07 | 10.87 |  | 117.95 |  | 38.83 |  | 0.25 |  | 0.54 |  | 0.74 |  | 1.36 |  | 5.78 |  | 2.21 |  | 6.65 |  | 4.9 |  | 2.54 |  | 0.00028567 |  | 40 | 10 | 15 | 500
2022-08-08 | 37.3 |  | 405.26 |  | 138.52 |  | 0.81 |  | 0.65 |  | 0.78 |  | 1.2 |  | 7.97 |  | 2.66 |  | 7.01 |  | 5.49 |  | 2.5 |  | 6.7443e-05 |  | 40 | 10 | 15 | 500
2022-08-09 | 40.37 | 28.259 | 352.65 |  | 135.48 |  | 0.48 |  | 0.6 |  | 0.85 |  | 1.76 |  | 5.69 |  | 1.34 |  | 5.29 |  | 4.26 |  | 2.24 |  | 5.9657e-05 |  | 40 | 10 | 15 | 500
2022-08-10 | 3.06 |  | 79.29 |  | 25.39 |  | 0.15 |  | 0.69 |  | 0.65 |  | 1.01 |  | 4.68 |  | 1.54 |  | 5.38 |  | 3.99 |  | 2.3 |  | 8.9857e-06 |  | 40 | 10 | 15 | 500
2022-08-11 | 19.47 |  | 103.09 |  | 29.15 |  | 0.18 |  | 0.83 |  | 0.57 |  | 1.24 |  | 5.4 |  | 1.02 |  | 4.94 |  | 2.93 |  | 2.18 |  | 0.027947 |  | 40 | 10 | 15 | 500
2022-08-12 | 22.57 |  | 355.48 |  | 119.3 |  | 0.49 |  | 0.77 |  | 0.67 |  | 1.89 |  | 5.32 |  | 1.43 |  | 4.55 |  | 3.8 |  | 2.23 |  | 0.0027054 |  | 40 | 10 | 15 | 500
2022-08-13 | 31.4 |  | 398.78 |  | 156.8 |  | 0.62 |  | 0.98 |  | 0.61 |  | 1.81 |  | 5.74 |  | 2.18 |  | 6 |  | 4.64 |  | 2.41 |  | 0.0001423 |  | 40 | 10 | 15 | 500
2022-08-14 | 44.72 | 31.304 | 418.06 |  | 179.8 |  | 0.62 |  | 0.64 |  | 0.45 |  | 1.21 |  | 6.24 |  | 0.85 |  | 2.43 |  | 2.26 |  | 2.09 |  | 0.00032039 |  | 40 | 10 | 15 | 500
2022-08-15 | 45.2 | 31.64 | 432.1 |  | 184.7 |  | 0.5 |  | 1.1 |  | 0.71 |  | 0.96 |  | 4.53 |  | 1.95 |  | 4.35 |  | 3.36 |  | 1.98 |  | 7.4129e-05 |  | 40 | 10 | 15 | 500
2022-08-16 | 36.26 |  | 426.54 |  | 173.99 |  | 0.54 |  | 0.74 |  | 0.81 |  | 0.67 |  | 5.93 |  | 1.46 |  | 4.13 |  | 3.37 |  | 1.69 |  | 0.000257 |  | 40 | 10 | 15 | 500
2022-08-17 | 29.86 |  | 377.44 |  | 160.15 |  | 0.52 |  | 1.58 |  | 0.95 |  | 1.04 |  | 5.47 |  | 4.71 |  | 9.17 |  | 5.44 |  | 2.54 |  | 8.3257e-05 |  | 40 | 10 | 15 | 500
2022-08-18 | 25.72 |  | 413.34 |  | 158.04 |  | 0.5 |  | 1.33 |  | 0.81 |  | 1.47 |  | 2.5 |  | 6.96 |  | 9.5 |  | 5.37 |  | 2.63 |  | 8.0871e-05 |  | 40 | 10 | 15 | 500
2022-08-19 | 32.94 |  | 420.53 |  | 178.13 |  | 0.48 |  | 1.06 |  | 0.71 |  | 1.4 |  | 1.09 |  | 6.17 |  | 10.09 |  | 5.83 |  | 2.6 |  | 0.00012001 |  | 40 | 10 | 15 | 500
2022-08-20 | 30.76 |  | 471 |  | 166.83 |  | 0.52 |  | 1.34 |  | 0.78 |  | 2.59 |  | 2.86 |  | 6.37 |  | 8.65 |  | 5.36 |  | 2.58 |  | 6.5786e-05 |  | 40 | 10 | 15 | 500
2022-08-21 | 35.01 |  | 529.89 | 423.912 | 184.18 |  | 0.62 |  | 1.64 |  | 0.63 |  | 2.06 |  | 1.86 |  | 5.68 |  | 5.56 |  | 3.61 |  | 2.35 |  | 0.00017396 |  | 40 | 10 | 15 | 500
2022-08-22 | 33.12 |  | 414.86 |  | 168.85 |  | 0.55 |  | 1.12 |  | 0.63 |  | 1.97 |  | 2.03 |  | 5.99 |  | 5.94 |  | 4.23 |  | 2.4 |  | 0.00032807 |  | 40 | 10 | 15 | 500
2022-08-23 | 42.86 | 30.002 | 420.77 |  | 182.77 |  | 0.61 |  | 1.46 |  | 0.65 |  | 1.9 |  | 1.81 |  | 4.55 |  | 4.97 |  | 3.63 |  | 2.23 |  | 0.0013121 |  | 40 | 10 | 15 | 500
2022-08-24 | 41.38 | 28.966 | 220.19 |  | 91.81 |  | 0.41 |  | 1.05 |  | 0.75 |  | 1.08 |  | 4.03 |  | 5.47 |  | 9.36 |  | 5.74 |  | 2.62 |  | 0.0010602 |  | 40 | 10 | 15 | 500
2022-08-25 | 23.85 |  | 233.58 |  | 112.6 |  | 0.45 |  | 0.9 |  | 0.71 |  | 0.91 |  | 3.18 |  | 5.51 |  | 8.6 |  | 5.98 |  | 2.71 |  | 0.001601 |  | 40 | 10 | 15 | 500
2022-08-26 | 42.89 | 30.023 | 274.47 |  | 165.69 |  | 0.63 |  | 0.89 |  | 0.59 |  | 1.08 |  | 2.96 |  | 7.68 |  | 8.8 |  | 5.83 |  | 2.53 |  | 0.00046599 |  | 40 | 10 | 15 | 500
2022-08-27 | 37.52 |  | 211.92 |  | 130.74 |  | 0.49 |  | 0.77 |  | 0.73 |  | 0.9 |  | 0.05 |  | 6.75 |  | 13.58 |  | 8.85 |  | 3.04 |  | 0.00042366 |  | 40 | 10 | 15 | 500
2022-08-28 | 43.55 | 30.485 | 290.4 |  | 171.67 |  | 0.51 |  | 1.22 |  | 0.94 |  | 0.94 |  | 0 |  | 11.33 |  | 16.76 | 11.732 | 12.63 |  | 3.73 |  | 7.2757e-05 |  | 40 | 10 | 15 | 500
2022-08-29 | 45.63 | 31.941 | 265.66 |  | 162.78 |  | 0.61 |  | 1.08 |  | 0.77 |  | 0.89 |  | 0.01 |  | 12.46 |  | 6.7 |  | 10.81 |  | 2.86 |  | 7.1643e-05 |  | 40 | 10 | 15 | 500
2022-08-30 | 54.42 | 38.094 | 374.03 |  | 162.34 |  | 0.63 |  | 1.18 |  | 0.83 |  | 0.93 |  | 0 |  | 16.79 | 11.753 | 14.47 |  | 10.94 |  | 2.9 |  | 7.3171e-05 |  | 40 | 10 | 15 | 500
2022-08-31 | 39.96 |  | 357.32 |  | 137.09 |  | 0.72 |  | 0.84 |  | 0.52 |  | 0.97 |  | 0 |  | 8.04 |  | 8.3 |  | 6.16 |  | 2.55 |  | 2.7129e-05 |  | 40 | 10 | 15 | 500
2022-09-01 | 29.29 |  | 354.05 |  | 142.64 |  | 0.82 |  | 1.12 |  | 0.59 |  | 1.09 |  | 0 |  | 9.68 |  | 6.49 |  | 8.16 |  | 3.06 |  | 4.7329e-05 |  | 40 | 10 | 15 | 500
2022-09-02 | 36.83 |  | 361.61 |  | 176.77 |  | 0.7 |  | 1.09 |  | 0.65 |  | 1.18 |  | 0 |  | 7.41 |  | 5.18 |  | 5.62 |  | 2.58 |  | 6.7086e-05 |  | 40 | 10 | 15 | 500
2022-09-03 | 13.08 |  | 173.33 |  | 67.37 |  | 0.36 |  | 1.09 |  | 0.52 |  | 1.07 |  | 2.72 |  | 7.54 |  | 7.15 |  | 6.62 |  | 2.85 |  | 0.00050566 |  | 40 | 10 | 15 | 500
2022-09-04 | 45.11 | 31.577 | 427.93 |  | 174.49 |  | 0.72 |  | 1.16 |  | 0.62 |  | 1.19 |  | 6.56 |  | 10.4 |  | 7.77 |  | 7.15 |  | 2.94 |  | 0.041124 |  | 40 | 10 | 15 | 500
2022-09-05 | 47.87 | 33.509 | 393.85 |  | 170 |  | 0.74 |  | 1.22 |  | 0.7 |  | 1.2 |  | 9.04 |  | 13.59 |  | 8.53 |  | 7.84 |  | 1.69 |  | 0.0022526 |  | 40 | 10 | 15 | 500
2022-09-06 | 53.4 | 37.38 | 454.17 |  | 169.92 |  | 0.62 |  | 1 |  | 0.54 |  | 1.35 |  | 12.55 |  | 10.57 |  | 8.68 |  | 8.48 |  | 0.81 |  | 0.0018829 |  | 40 | 10 | 15 | 500
2022-09-07 | 19.51 |  | 129.52 |  | 31.5 |  | 0.32 |  | 1.11 |  | 0.7 |  | 1.77 |  | 11.46 |  | 11.13 |  | 9.72 |  | 3.98 |  | 2.04 |  | 0.0041328 |  | 40 | 10 | 15 | 500
2022-09-08 | 20.77 |  | 120.29 |  | 29.18 |  | 0.2 |  | 0.78 |  | 0.46 |  | 1.6 |  | 12.4 |  | 8.89 |  | 9.4 |  | 3.99 |  | 2.82 |  | 0.0006483 |  | 40 | 10 | 15 | 500
2022-09-09 | 10.12 |  | 232.91 |  | 84.1 |  | 0.44 |  | 1.33 |  | 0.92 |  | 1.01 |  | 8.51 |  | 10.45 |  | 6.69 |  | 6.58 |  | 2.64 |  | 0.00030174 |  | 40 | 10 | 15 | 500
2022-09-10 | 9.47 |  | 265.07 |  | 97.74 |  | 0.45 |  | 1.46 |  | 0.85 |  | 1.07 |  | 13.79 |  | 15.55 | 10.885 | 8.08 |  | 6.92 |  | 2.61 |  | 0.00098939 |  | 40 | 10 | 15 | 500
2022-09-11 | 5.36 |  | 181.18 |  | 62.41 |  | 0.35 |  | 1.86 |  | 1.06 |  | 1.86 |  | 13.03 |  | 14.32 |  | 7.26 |  | 5.99 |  | 2.54 |  | 0.00021011 |  | 40 | 10 | 15 | 500
2022-09-12 | 18.63 |  | 323.03 |  | 118.11 |  | 0.47 |  | 1.67 |  | 0.95 |  | 0.73 |  | 7.21 |  | 9.73 |  | 5.42 |  | 5.11 |  | 2.34 |  | 0.00039779 |  | 40 | 10 | 15 | 500
2022-09-13 | 22.78 |  | 321.67 |  | 106.86 |  | 0.46 |  | 1.64 |  | 0.87 |  | 0.52 |  | 7.2 |  | 9.17 |  | 3.57 |  | 4.15 |  | 1.99 |  | 4.9314e-05 |  | 40 | 10 | 15 | 500
2022-09-14 | 23 |  | 352.34 |  | 133.32 |  | 0.48 |  | 1.94 |  | 1.14 |  | 0.15 |  | 5.17 |  | 6.78 |  | 3.17 |  | 3.71 |  | 1.75 |  | 0.00025866 |  | 40 | 10 | 15 | 500
2022-09-15 | 15.56 |  | 179.27 |  | 58.93 |  | 0.32 |  | 1.8 |  | 1.13 |  | 0.14 |  | 2.31 |  | 8.87 |  | 3.38 |  | 3.56 |  | 2.14 |  | 0.0002546 |  | 40 | 10 | 15 | 500
2022-09-16 | 15.59 |  | 316.88 |  | 120.41 |  | 0.5 |  | 2.35 |  | 1.23 |  | 0.61 |  | 3.97 |  | 10.7 |  | 4.12 |  | 4.44 |  | 2.27 |  | 0.00036719 |  | 40 | 10 | 15 | 500
2022-09-17 | 15.45 |  | 100.42 |  | 20.63 |  | 0.25 |  | 1.85 |  | 1.1 |  | 1.09 |  | 3.09 |  | 2.87 |  | 4.16 |  | 4.63 |  | 2.4 |  | 0.00032713 |  | 40 | 10 | 15 | 500
2022-09-18 | 25.29 |  | 421.71 |  | 136.49 |  | 0.52 |  | 1.82 |  | 1.03 |  | 1.11 |  | 5.75 |  | 3.9 |  | 4.01 |  | 4.48 |  | 2.33 |  | 0.00035109 |  | 40 | 10 | 15 | 500
2022-09-19 | 48.75 | 34.125 | 623.72 | 498.976 | 183.52 |  | 0.66 |  | 1.55 |  | 0.86 |  | 1.36 |  | 10.7 |  | 5.55 |  | 5.06 |  | 5.67 |  | 2.29 |  | 0.00045384 |  | 40 | 10 | 15 | 500
2022-09-20 | 52.27 | 36.589 | 566.73 | 453.384 | 179.54 |  | 0.65 |  | 1.86 |  | 0.76 |  | 2.05 |  | 11.65 |  | 6.06 |  | 6.28 |  | 6.89 |  | 2.36 |  | 0.0002115 |  | 40 | 10 | 15 | 500
2022-09-21 | 40.86 | 28.602 | 407.79 |  | 145.04 |  | 0.65 |  | 1.41 |  | 0.8 |  | 1.52 |  | 14.19 |  | 5.98 |  | 5.35 |  | 5.89 |  | 2.34 |  | 0.0003352 |  | 40 | 10 | 15 | 500
2022-09-22 | 53.69 | 37.583 | 509.41 | 407.528 | 177.87 |  | 0.7 |  | 1.29 |  | 0.76 |  | 1.43 |  | 8.99 |  | 6.9 |  | 5.7 |  | 6.33 |  | 2.14 |  | 0.00047686 |  | 40 | 10 | 15 | 500
2022-09-23 | 54.54 | 38.178 | 434.53 |  | 143.79 |  | 0.71 |  | 1.4 |  | 0.78 |  | 1.15 |  | 9.69 |  | 4.88 |  | 8.19 |  | 6.92 |  | 2.72 |  | 0.00051006 |  | 40 | 10 | 15 | 500
2022-09-24 | 50.56 | 35.392 | 465.18 |  | 168.85 |  | 0.7 |  | 1.74 |  | 1.08 |  | 1.8 |  | 10.37 |  | 4.67 |  | 13.43 |  | 6.49 |  | 3.49 |  | 0.00025663 |  | 40 | 10 | 15 | 500
2022-09-25 | 55.27 | 38.689 | 479.47 |  | 178.84 |  | 0.75 |  | 1.78 |  | 1.08 |  | 1.2 |  | 10.53 |  | 7.14 |  | 11.87 |  | 6.1 |  | 2.64 |  | 0.00046511 |  | 40 | 10 | 15 | 500
2022-09-26 | 56.96 | 39.872 | 459.39 |  | 178.86 |  | 0.85 |  | 1.32 |  | 0.84 |  | 1.5 |  | 20.19 | 14.133 | 9.43 |  | 8.62 |  | 8.44 |  | 2.65 |  | 0.00012386 |  | 40 | 10 | 15 | 500
2022-09-27 | 32.46 |  | 101.29 |  | 49.75 |  | 0.48 |  | 2.07 |  | 1.04 |  | 1.28 |  | 14.47 |  | 8.58 |  | 4.67 |  | 4.87 |  | 2.4 |  | 0.00017293 |  | 40 | 10 | 15 | 500
2022-09-28 | 33.69 |  | 433.13 |  | 140.5 |  | 0.59 |  | 1.78 |  | 0.9 |  | 1.7 |  | 9.06 |  | 10.95 |  | 4.38 |  | 4.69 |  | 2.33 |  | 0.00027951 |  | 40 | 10 | 15 | 500
2022-09-29 | 36.77 |  | 527.95 | 422.36 | 188.31 |  | 0.63 |  | 1.45 |  | 0.83 |  | 2.01 |  | 3.81 |  | 8.82 |  | 4.04 |  | 4.71 |  | 2.13 |  | 0.00029584 |  | 40 | 10 | 15 | 500
2022-09-30 | 41.16 | 28.812 | 492.74 |  | 187.68 |  | 0.66 |  | 1.02 |  | 0.57 |  | 1.62 |  | 3.32 |  | 6.74 |  | 4.04 |  | 4.37 |  | 2.15 |  | 0.00128
Formulas:
Source = [Source, row above]+7
Note on Q12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Fan 3 offline for planned maintenance betwenn 10:00am 07/07/22 ann 16:00pm 08/07/2022 - A10 BOS 021_07
Note on D20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Part A Reference - S5N_22_58A (July Particulate Breaches)
Note on C25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Planned stop
Note on S30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Fan 3A planned maintenance between 11:00am 25/07/2022 and 08:15am 30/07/2022 - A10A BOS 026_250722
Note on U30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Fan 4 Planned maintenance between 8:15 and 16:15 25/07/2022 - A14 BOS 025_250722
Note on C34: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Plant temporarily offline
Note on C43: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Plant offline temporarily
Note on C46: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Plant offline temporarily
Note on Q54: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Planned maintenance between 08:15 18/08/2022 and 13:00 19/08/2022 - A10 BOS 027_180822
Note on Q62: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Unplanned maintenance between 20:00 26/08/2022 and 10:00 03/09/2022 - A10 BOS 30_260822
Note on Y72: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Planned maintenance between 09:00 05/09/2022 and 13:00 07/09/2022 - A16 BOS 033_050922
Note on C74: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sinter Plant Main Stack on single fan operations until the end of the quarter: Ref - A1 Sinter Plant 035_070922
Note on W74: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Planned maintenance between 12:30 07/09/2022 and 20:00 08/09/2022 - A15 BOS 037_070922
Note on C76: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Planned stop
Note on C79: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Planned stoppage temporarily
Note on C80: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Planned stoppage temporarily
Note on C81: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Planned stoppage temporarily
Note on C82: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Planned stoppage temporarily
Note on C83: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Plant offline for cooler derailment
Note on C84: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Temporary stoppages throughout day
Note on C94: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Planned stop