## Notes
Reference conditions
All concentrations in this spreadsheet are reported in dry air at a temperature of 273K, at a pressure of 101.3 kPa and with an oxygen content of 3% dry
Uncertainty
Concentrations in this spreadsheet are reported after having subtracted the value of the 95% confidence interval (see Section 3.6.7 of the permit):
95% confidence interval for nitrogen oxides is taken to be 20%
95% confidence interval for sulphur dioxide is taken to be 20%
95% confidence interval for dust is taken to be 30%
95% confidence interval for carbon monoxide is taken to be 10%
Normal operating conditions
The document "Power Plant Boiler Abnormal Conditions" sets out the criteria for excluding emissions monitoring data from permitting or other reporting obligations:
| Parameter | Plant | Level representing abnormal conditions
| Boiler oxygen | All boilers | >17% oxygen
| Fuel input | A51, A52A, A52B, A53 and A62 | <50% BFG by thermal input
|  | A50 (Service Boilers) | <35% BFG by thermal input

## A50 Service Boilers
|  | Concentrations in mg/m³ at reference conditions after subtracting uncertainty | [9 empty] | Daily means, excluding hours outside normal operating conditions
|  | 2022-04-01 |  |  | 2022-05-01 |  |  | 2022-06-01 |  |  | Date | Fuel mix |  |  |  |  | Particulate Matter concentration (mg/m³) after subtracting uncertainty |  |  |  |  | Sulphur dioxide concentration (mg/m³) after subtracting uncertainty |  |  |  |  | Oxides of nitrogen concentration (mg/m³) after subtracting uncertainty
|  | PM | SO2 | NOx | PM | SO2 | NOx | PM | SO2 | NOx |  | % BFG | % COG | % BOSg | % NG | % HFO | No.valid hours | No.hours OTNOC | Measured | Limit | Breach? | No.valid hours | No.hours OTNOC | Measured | Limit | Breach? | No.valid hours | No.hours OTNOC | Measured | Limit | Breach?
Daily means | Minimum | 0.5 | 52.2 | 49.4 | 0.3 | 17.8 | 23.9 | 0 | 15.4 | 38.1 | 2022-04-01 | 69.1% | 16.95% |  | 13.95% |  | 24 | 0 | 5.1 | 14 | NO | 24 | 0 | 330.1 | 232 | YES | 24 | 0 | 128.7 | 299.3 | NO
| Maximum | 6.5 | 376.5 | 165 | 2.6 | 396.4 | 129.3 | 8 | 89 | 65 | 2022-04-02 | 71.06% | 12.55% |  | 16.39% |  | 24 | 0 | 3 | 12.9 | NO | 24 | 0 | 214.7 | 217.9 | NO | 24 | 0 | 92.2 | 293.9 | NO
| No. > Limit | 0 | 4 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 2022-04-03 | 69.78% | 14.69% |  | 15.53% |  | 24 | 0 | 2.5 | 13.4 | NO | 24 | 0 | 167.8 | 224.2 | NO | 24 | 0 | 111.9 | 295.9 | NO
Monthly mean |  | 2.3 | 149.9 | 99.2 | 1.1 | 128.3 | 78.9 | 4.3 | 52.4 | 51.7 | 2022-04-04 | 56.32% | 26.52% |  | 17.16% |  | 24 | 3 | 1.9 | 15.9 | NO | 24 | 3 | 147.1 | 247.2 | NO | 24 | 3 | 113.6 | 292.3 | NO
Monthly mean limit |  | 13.5 | 213.2 | 261.8 | 14.6 | 237.8 | 286.4 | 13.8 | 232 | 290.2 | 2022-04-05 | 48.67% | 19.74% |  | 31.59% |  | 24 | 2 | 3.4 | 13.6 | NO | 24 | 2 | 132 | 206.1 | NO | 24 | 2 | 76.4 | 260.5 | NO
[11 empty] | 2022-04-06 | 36.48% | 13.21% |  | 50.31% |  | 24 | 6 | 6 | 11.1 | NO | 24 | 6 | 114 | 157.8 | NO | 24 | 6 | 87.4 | 219.3 | NO
[11 empty] | 2022-04-07 | 37.59% | 18.12% |  | 44.29% |  | 24 | 5 | 6.5 | 12.6 | NO | 24 | 5 | 149.7 | 179.5 | NO | 24 | 5 | 165 | 232.6 | NO
[11 empty] | 2022-04-08 | 25.94% | 48.75% |  | 25.31% |  | 24 | 15 | 4 | 20.3 | NO | 24 | 15 | 376.5 | 281.3 | YES | 24 | 15 | 125.3 | 274.3 | NO
[11 empty] | 2022-04-09 | 53.67% | 22.99% |  | 23.34% |  | 24 | 0 | 2.8 | 14.8 | NO | 24 | 0 | 190.7 | 228.2 | NO | 24 | 0 | 107 | 278.7 | NO
[11 empty] | 2022-04-10 | 69.45% | 17.05% |  | 13.5% |  | 24 | 0 | 1.5 | 14 | NO | 24 | 0 | 89 | 233 | NO | 24 | 0 | 94.7 | 300.3 | NO
[11 empty] | 2022-04-11 | 66.5% | 19.74% |  | 13.76% |  | 24 | 2 | 1.3 | 14.6 | NO | 24 | 2 | 71.5 | 238.4 | NO | 24 | 2 | 94 | 299.7 | NO
[11 empty] | 2022-04-12 | 47.29% | 36.75% |  | 15.96% |  | 24 | 11 | 3.8 | 18.2 | NO | 24 | 11 | 202 | 271.9 | NO | 24 | 11 | 81.6 | 294.9 | NO
[11 empty] | 2022-04-13 | 48.51% | 21.08% |  | 30.41% |  | 24 | 7 | 2.4 | 14 | NO | 24 | 7 | 259 | 211.2 | YES | 24 | 7 | 93.7 | 263.1 | NO
[11 empty] | 2022-04-14 | 39.88% | 30.46% |  | 29.66% |  | 24 | 12 | 2.3 | 16.1 | NO | 24 | 12 | 100.3 | 233.2 | NO | 24 | 12 | 102.8 | 264.8 | NO
[11 empty] | 2022-04-15 | 50.4% | 20.38% |  | 29.22% |  | 24 | 5 | 2.4 | 13.9 | NO | 24 | 5 | 188.9 | 211.8 | NO | 24 | 5 | 102.9 | 265.7 | NO
[11 empty] | 2022-04-16 | 41.42% | 31.93% |  | 26.65% |  | 24 | 13 | 1.4 | 16.6 | NO | 24 | 13 | 195.1 | 241.9 | NO | 24 | 13 | 99.6 | 271.4 | NO
[11 empty] | 2022-04-17 | 44.99% | 32.47% |  | 22.54% |  | 24 | 0 | 1.6 | 16.9 | NO | 24 | 0 | 209 | 250.5 | NO | 24 | 0 | 97.9 | 280.4 | NO
[11 empty] | 2022-04-18 | 57.68% | 15.05% |  | 27.27% |  | 24 | 0 | 1.4 | 12.8 | NO | 24 | 0 | 130.7 | 203.6 | NO | 24 | 0 | 78.1 | 270 | NO
[11 empty] | 2022-04-19 | 58.56% | 22.54% |  | 18.9% |  | 24 | 0 | 1.5 | 14.9 | NO | 24 | 0 | 71.4 | 235.3 | NO | 24 | 0 | 88.8 | 288.4 | NO
[11 empty] | 2022-04-20 | 55.6% | 31.29% |  | 13.11% |  | 24 | 0 | 3.4 | 17.2 | NO | 24 | 0 | 75.9 | 265 | NO | 24 | 0 | 92.8 | 301.2 | NO
[11 empty] | 2022-04-21 | 59.1% | 27.83% |  | 13.07% |  | 24 | 3 | 2.7 | 16.4 | NO | 24 | 3 | 133.3 | 257.5 | NO | 24 | 3 | 133.3 | 301.2 | NO
[11 empty] | 2022-04-22 | 64.16% | 19.52% |  | 16.32% |  | 24 | 0 | 2.5 | 14.4 | NO | 24 | 0 | 258.5 | 233.3 | YES | 24 | 0 | 120.4 | 294.1 | NO
[11 empty] | 2022-04-23 | 63.06% | 21.62% |  | 15.32% |  | 24 | 2 | 1.4 | 14.9 | NO | 24 | 2 | 182.4 | 239.8 | NO | 24 | 2 | 111.1 | 296.3 | NO
[11 empty] | 2022-04-24 | 63.58% | 21.17% |  | 15.25% |  | 24 | 2 | 1.6 | 14.8 | NO | 24 | 2 | 81 | 238.9 | NO | 24 | 2 | 102.9 | 296.5 | NO
[11 empty] | 2022-04-25 | 71.67% | 11.67% |  | 16.66% |  | 24 | 0 | 0.6 | 12.7 | NO | 24 | 0 | 107.1 | 215.4 | NO | 24 | 0 | 116.3 | 293.4 | NO
[11 empty] | 2022-04-26 | 59.41% | 29.15% |  | 11.44% |  | 24 | 6 | 1.3 | 16.8 | NO | 24 | 6 | 130 | 263.4 | NO | 24 | 6 | 121.6 | 304.8 | NO
[11 empty] | 2022-04-27 | 75.2% | 20.42% |  | 4.38% |  | 24 | 1 | 1.7 | 15.3 | NO | 24 | 1 | 91.6 | 257 | NO | 24 | 1 | 105.4 | 320.4 | NO
[11 empty] | 2022-04-28 | 79.27% | 18.27% |  | 2.46% |  | 24 | 0 | 1.1 | 14.9 | NO | 24 | 0 | 145.2 | 255.7 | NO | 24 | 0 | 84.2 | 324.6 | NO
[11 empty] | 2022-04-29 | 67.93% | 18.27% |  | 13.8% |  | 24 | 1 | 1.5 | 14.3 | NO | 24 | 1 | 52.2 | 235.1 | NO | 24 | 1 | 49.4 | 299.6 | NO
[11 empty] | 2022-04-30 | 78.95% | 18.56% |  | 2.49% |  | 24 | 0 | 0.5 | 14.9 | NO | 24 | 0 | 103.6 | 256.3 | NO | 24 | 0 | 56.1 | 324.5 | NO
[11 empty] | 2022-05-01 | 83.11% | 14.58% |  | 2.31% |  | 24 | 0 | 0.6 | 14.1 | NO | 24 | 0 | 117.3 | 247.9 | NO | 24 | 0 | 68.8 | 324.9 | NO
[11 empty] | 2022-05-02 | 60.59% | 37.06% |  | 2.35% |  | 24 | 2 | 1.1 | 19 | NO | 24 | 2 | 173.4 | 297.3 | NO | 24 | 2 | 96 | 324.8 | NO
[11 empty] | 2022-05-03 | 61.63% | 35.37% |  | 3% |  | 24 | 0 | 1.4 | 18.6 | NO | 24 | 0 | 144.7 | 292.4 | NO | 24 | 0 | 54.8 | 323.4 | NO
[11 empty] | 2022-05-04 | 46.75% | 51.12% |  | 2.13% |  | 24 | 8 | 0.9 | 22.1 | NO | 24 | 8 | 319.6 | 328.6 | NO | 24 | 8 | 103.4 | 325.3 | NO
[11 empty] | 2022-05-05 | 33.12% | 64.31% |  | 2.57% |  | 24 | 24 |  | 25 | NO | 24 | 24 |  | 356.5 | NO | 24 | 24 |  | 323.5 | NO
[11 empty] | 2022-05-06 | 35.8% | 57.27% |  | 6.93% |  | 24 | 20 | 0.6 | 23.2 | NO | 24 | 20 | 206.5 | 333.1 | NO | 24 | 20 | 113.7 | 313.9 | NO
[11 empty] | 2022-05-07 | 75.56% | 21.93% |  | 2.51% |  | 24 | 0 | 0.8 | 15.7 | NO | 24 | 0 | 130.7 | 263.7 | NO | 24 | 0 | 102.6 | 324.5 | NO
[11 empty] | 2022-05-08 | 78.52% | 18.62% |  | 2.86% |  | 24 | 0 | 1.2 | 14.9 | NO | 24 | 0 | 66.3 | 255.8 | NO | 24 | 0 | 87.8 | 323.7 | NO
[11 empty] | 2022-05-09 | 71.37% | 17.82% |  | 10.81% |  | 24 | 0 | 1.1 | 14.3 | NO | 24 | 0 | 91 | 239.6 | NO | 24 | 0 | 73.4 | 306.2 | NO
[11 empty] | 2022-05-10 | 45.54% | 29.41% |  | 25.05% |  | 24 | 0 | 1.1 | 16.1 | NO | 24 | 0 | 143.9 | 239.2 | NO | 24 | 0 | 102.3 | 274.9 | NO
[11 empty] | 2022-05-11 | 67.07% | 24.06% |  | 8.87% |  | 24 | 0 | 1.2 | 15.8 | NO | 24 | 0 | 307.9 | 256.8 | YES | 24 | 0 | 113.5 | 310.5 | NO
[11 empty] | 2022-05-12 | 81.99% | 15.43% |  | 2.58% |  | 24 | 0 | 1.8 | 14.3 | NO | 24 | 0 | 159.1 | 249.3 | NO | 24 | 0 | 80.6 | 324.3 | NO
[11 empty] | 2022-05-13 | 90.71% | 6.35% |  | 2.94% |  | 24 | 0 | 0.3 | 12.2 | NO | 24 | 0 | 49.1 | 228.6 | NO | 24 | 0 | 69.2 | 323.5 | NO
[11 empty] | 2022-05-14 | 83.78% | 13.48% |  | 2.74% |  | 24 | 0 | 1 | 13.8 | NO | 24 | 0 | 87.5 | 244.7 | NO | 24 | 0 | 81.4 | 324 | NO
[11 empty] | 2022-05-15 | 77.02% | 16.9% |  | 6.08% |  | 24 | 0 | 1.1 | 14.4 | NO | 24 | 0 | 57.3 | 246.2 | NO | 24 | 0 | 99.3 | 316.6 | NO
[11 empty] | 2022-05-16 | 69.82% | 27.18% |  | 3% |  | 24 | 0 | 1.8 | 16.8 | NO | 24 | 0 | 117.9 | 274.3 | NO | 24 | 0 | 97.8 | 323.4 | NO
[11 empty] | 2022-05-17 | 72.76% | 23.99% |  | 3.25% |  | 24 | 0 | 1.2 | 16.1 | NO | 24 | 0 | 180 | 266.9 | NO | 24 | 0 | 102.1 | 322.9 | NO
[11 empty] | 2022-05-18 | 61.63% | 35.26% |  | 3.11% |  | 24 | 0 | 0.6 | 18.6 | NO | 24 | 0 | 293.5 | 291.9 | YES | 24 | 0 | 123.1 | 323.2 | NO
[11 empty] | 2022-05-19 | 84.62% | 12.61% |  | 2.77% |  | 24 | 0 | 1 | 13.6 | NO | 24 | 0 | 165.5 | 242.7 | NO | 24 | 0 | 81.5 | 323.9 | NO
[11 empty] | 2022-05-20 | 75.52% | 20.98% |  | 3.5% |  | 24 | 2 | 1 | 15.4 | NO | 24 | 2 | 114.9 | 259.8 | NO | 24 | 2 | 78.7 | 322.3 | NO
[11 empty] | 2022-05-21 | 73.27% | 24.15% |  | 2.58% |  | 24 | 0 | 1.2 | 16.2 | NO | 24 | 0 | 173.5 | 268.5 | NO | 24 | 0 | 82.4 | 324.3 | NO
[11 empty] | 2022-05-22 | 52.93% | 44.47% |  | 2.6% |  | 24 | 2 | 1.6 | 20.6 | NO | 24 | 2 | 220.7 | 313.1 | NO | 24 | 2 | 94 | 324.3 | NO
[11 empty] | 2022-05-23 | 0.48% | 59.5% |  | 40.02% |  | 24 | 24 |  | 21.9 | NO | 24 | 24 |  | 278.3 | NO | 24 | 24 |  | 242 | NO
[11 empty] | 2022-05-24 | 13.56% | 48.52% |  | 37.92% |  | 24 | 19 | 2.6 | 19.6 | NO | 24 | 19 | 396.4 | 257.9 | YES | 24 | 19 | 129.3 | 246.6 | NO
[11 empty] | 2022-05-25 | 55.11% | 35.56% |  | 9.33% |  | 24 | 10 | 0.6 | 18.3 | NO | 24 | 10 | 68 | 281.3 | NO | 24 | 10 | 56.1 | 309.5 | NO
[11 empty] | 2022-05-26 | 97.32% | 0.7% |  | 1.98% |  | 24 | 0 | 1.8 | 11 | NO | 24 | 0 | 60.3 | 217.9 | NO | 24 | 0 | 49.1 | 325.6 | NO
[11 empty] | 2022-05-27 | 97.48% | 0.49% |  | 2.03% |  | 24 | 0 | 1.2 | 11 | NO | 24 | 0 | 44.2 | 217.4 | NO | 24 | 0 | 52.7 | 325.5 | NO
[11 empty] | 2022-05-28 | 97.03% | 0.41% |  | 2.56% |  | 24 | 0 | 0.8 | 10.9 | NO | 24 | 0 | 83.6 | 216.2 | NO | 24 | 0 | 56.7 | 324.4 | NO
[11 empty] | 2022-05-29 | 96.74% | 0.26% |  | 3% |  | 24 | 0 | 0.9 | 10.9 | NO | 24 | 0 | 17.8 | 215.1 | NO | 24 | 0 | 23.9 | 323.4 | NO
[11 empty] | 2022-05-30 | 94.66% | 1.27% |  | 4.07% |  | 24 | 0 | 0.7 | 11.1 | NO | 24 | 0 | 30.7 | 215.4 | NO | 24 | 0 | 38.6 | 321.1 | NO
[11 empty] | 2022-05-31 | 94.96% | 0.74% |  | 4.3% |  | 24 | 0 | 2.3 | 10.9 | NO | 24 | 0 | 26.7 | 213.8 | NO | 24 | 0 | 45.1 | 320.5 | NO
[11 empty] | 2022-06-01 | 96.78% | 0.36% |  | 2.86% |  | 24 | 0 | 0.1 | 10.9 | NO | 24 | 0 | 39 | 215.6 | NO | 24 | 0 | 41.4 | 323.7 | NO
[11 empty] | 2022-06-02 | 96.24% | 0.72% |  | 3.04% |  | 24 | 0 | 0 | 11 | NO | 24 | 0 | 18.8 | 216 | NO | 24 | 0 | 48.8 | 323.3 | NO
[11 empty] | 2022-06-03 | 96.33% | 0.43% |  | 3.24% |  | 24 | 0 | 0 | 10.9 | NO | 24 | 0 | 40.6 | 215.1 | NO | 24 | 0 | 54.5 | 322.9 | NO
[11 empty] | 2022-06-04 | 96.09% | 0.64% |  | 3.27% |  | 24 | 0 | 0 | 11 | NO | 24 | 0 | 32.7 | 215.5 | NO | 24 | 0 | 47 | 322.8 | NO
[11 empty] | 2022-06-05 | 95.71% | 0.35% |  | 3.94% |  | 24 | 0 | 0 | 10.8 | NO | 24 | 0 | 36.3 | 213.4 | NO | 24 | 0 | 42.3 | 320.5 | NO
[11 empty] | 2022-06-06 | 88.29% | 7.87% |  | 3.84% |  | 24 | 0 | 0 | 12.5 | NO | 24 | 0 | 68.5 | 230.1 | NO | 24 | 0 | 38.1 | 320.7 | NO
[11 empty] | 2022-06-07 | 85.84% | 11.1% |  | 3.06% |  | 24 | 0 | 0 | 13.3 | NO | 24 | 0 | 74.9 | 238.8 | NO | 24 | 0 | 53.4 | 323.3 | NO
[11 empty] | 2022-06-08 | 82.86% | 14.17% |  | 2.97% |  | 24 | 0 | 0 | 14 | NO | 24 | 0 | 68.7 | 245.8 | NO | 24 | 0 | 55.4 | 323.5 | NO
[11 empty] | 2022-06-09 | 83.93% | 13.05% |  | 3.02% |  | 24 | 0 | 2.5 | 13.7 | NO | 24 | 0 | 61.8 | 243.2 | NO | 24 | 0 | 53.3 | 323.4 | NO
[11 empty] | 2022-06-10 | 84.53% | 12.34% |  | 3.13% |  | 24 | 0 | 6 | 13.5 | NO | 24 | 0 | 51.7 | 241.5 | NO | 24 | 0 | 52.7 | 323.1 | NO
[11 empty] | 2022-06-11 | 84.87% | 11.94% |  | 3.19% |  | 24 | 0 | 5.9 | 13.5 | NO | 24 | 0 | 46.7 | 240.5 | NO | 24 | 0 | 52.8 | 323 | NO
[11 empty] | 2022-06-12 | 83.48% | 13.43% |  | 3.09% |  | 24 | 0 | 6.7 | 13.8 | NO | 24 | 0 | 41.7 | 243.9 | NO | 24 | 0 | 53.4 | 323.2 | NO
[11 empty] | 2022-06-13 | 82.63% | 14.41% |  | 2.96% |  | 24 | 0 | 6.5 | 14 | NO | 24 | 0 | 38.8 | 246.3 | NO | 24 | 0 | 44.2 | 323.5 | NO
[11 empty] | 2022-06-14 | 82.8% | 14.53% |  | 2.67% |  | 24 | 0 | 6.5 | 14 | NO | 24 | 0 | 89 | 247.1 | NO | 24 | 0 | 55 | 324.1 | NO
[11 empty] | 2022-06-15 | 85.77% | 11.57% |  | 2.66% |  | 24 | 0 | 6.1 | 13.4 | NO | 24 | 0 | 43.7 | 240.6 | NO | 24 | 0 | 42.4 | 324.1 | NO
[11 empty] | 2022-06-16 | 66.35% | 26.19% |  | 7.46% |  | 24 | 4 | 8 | 16.4 | NO | 24 | 4 | 61.6 | 264.1 | NO | 24 | 4 | 56.4 | 313.6 | NO
[11 empty] | 2022-06-17 | 84.74% | 12.03% |  | 3.23% |  | 24 | 0 | 5.1 | 13.5 | NO | 24 | 0 | 61.2 | 240.6 | NO | 24 | 0 | 59.2 | 322.9 | NO
[11 empty] | 2022-06-18 | 85.21% | 11.82% |  | 2.97% |  | 24 | 0 | 4.9 | 13.4 | NO | 24 | 0 | 15.4 | 240.6 | NO | 24 | 0 | 53.4 | 323.5 | NO
[11 empty] | 2022-06-19 | 83.82% | 13.23% |  | 2.95% |  | 24 | 0 | 5.4 | 13.7 | NO | 24 | 0 | 71.7 | 243.7 | NO | 24 | 0 | 52.4 | 323.5 | NO
[11 empty] | 2022-06-20 | 86.64% | 10.1% |  | 3.26% |  | 24 | 0 | 5.6 | 13 | NO | 24 | 0 | 52.5 | 236.3 | NO | 24 | 0 | 47.5 | 322.8 | NO
[11 empty] | 2022-06-21 | 83.8% | 12.59% |  | 3.61% |  | 24 | 0 | 5 | 13.6 | NO | 24 | 0 | 23.8 | 241.1 | NO | 24 | 0 | 54.4 | 322.1 | NO
[11 empty] | 2022-06-22 | 83.08% | 13.52% |  | 3.4% |  | 24 | 0 | 5.5 | 13.8 | NO | 24 | 0 | 62.6 | 243.6 | NO | 24 | 0 | 55 | 322.5 | NO
[11 empty] | 2022-06-23 | 83.58% | 12.95% |  | 3.47% |  | 24 | 0 | 5.4 | 13.7 | NO | 24 | 0 | 44.3 | 242.2 | NO | 24 | 0 | 59.2 | 322.4 | NO
[11 empty] | 2022-06-24 | 67.47% | 27.57% |  | 4.96% |  | 24 | 6 | 5.3 | 16.8 | NO | 24 | 6 | 42.5 | 271.7 | NO | 24 | 6 | 65 | 319.1 | NO
[11 empty] | 2022-06-25 | 84.62% | 12.27% |  | 3.11% |  | 24 | 0 | 5.5 | 13.5 | NO | 24 | 0 | 86.9 | 241.3 | NO | 24 | 0 | 60.4 | 323.1 | NO
[11 empty] | 2022-06-26 | 88.31% | 8.32% |  | 3.37% |  | 24 | 0 | 6.5 | 12.6 | NO | 24 | 0 | 45.8 | 232.2 | NO | 24 | 0 | 42.2 | 322.6 | NO
[11 empty] | 2022-06-27 | 54.01% | 37.05% |  | 8.94% |  | 24 | 9 | 7.9 | 18.7 | NO | 24 | 9 | 76 | 285.3 | NO | 24 | 9 | 53.8 | 310.3 | NO
[11 empty] | 2022-06-28 | 11.5% | 79.81% |  | 8.69% |  | 24 | 21 | 7.3 | 28.1 | NO | 24 | 21 | 48.4 | 379.8 | NO | 24 | 21 | 53.9 | 310.9 | NO
[11 empty] | 2022-06-29 | 4.1% | 83.99% |  | 11.91% |  | 24 | 24 |  | 28.8 | NO | 24 | 24 |  | 383.2 | NO | 24 | 24 |  | 303.8 | NO
[11 empty] | 2022-06-30 | 7.99% | 77.5% |  | 14.51% |  | 24 | 24 |  | 27.3 | NO | 24 | 24 |  | 364.2 | NO | 24 | 24 |  | 298.1 | NO
[11 empty] | 0 | 0% | 0% |  | 0% |  | 0 | 0 | 0 | 0 | NO | 0 | 0 | 0 | 0 | NO | 24 | 0 | 99.554 | 278.3265 | NO
[11 empty] | 0 | 0% | 0% |  | 0% |  | 0 | 0 | 0 | 0 | NO | 0 | 0 | 0 | 0 | NO | 24 | 0 | 99.7316 | 281.2178 | NO
Note on E7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Part A Reference: S5N_22_37A
Note on H7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Part A Reference: S5N_22_52A

## A51 Boiler 5
|  | Concentrations in mg/m³ at reference conditions after subtracting uncertainty | [9 empty] | Daily means, excluding hours outside normal operating conditions
|  | 2022-04-01 |  |  | 2022-05-01 |  |  | 2022-06-01 |  |  | Date | Fuel mix |  |  |  |  | Particulate Matter concentration (mg/m³) after subtracting uncertainty
|  | PM | SO2 | NOx | PM | SO2 | NOx | PM | SO2 | NOx |  | % BFG | % COG | % BOSg | % NG | % HFO | No.valid hours | No.hours OTNOC | Measured | Limit | Breach?
Daily means | Minimum | 0.4 | Discontinuous monitoring only |  | 0.3 | Discontinuous monitoring only |  | 0.4 | Discontinuous monitoring only |  | 2022-04-01 | 86.63% | 12.14% |  | 1.24% | 0% | 24 | 0 | 1 | 13.6 | NO
| Maximum | 6.5 |  |  | 1.9 |  |  | 1.4 |  |  | 2022-04-02 | 81.21% | 17.44% |  | 1.35% | 0% | 24 | 0 | 2.2 | 14.9 | NO
| No. > Limit | 0 |  |  | 0 |  |  | 0 |  |  | 2022-04-03 | 77.76% | 21.08% |  | 1.16% | 0% | 24 | 0 | 1.1 | 15.6 | NO
Monthly mean |  | 1.2 |  |  | 0.6 |  |  | 0.6 |  |  | 2022-04-04 | 70.71% | 14.25% |  | 15.04% | 0% | 24 | 0 | 3.6 | 13.5 | NO
Monthly mean limit |  | 12.5 |  |  | 12.3 |  |  | 12.5 |  |  | 2022-04-05 | 67.83% | 9.37% |  | 22.81% | 0% | 24 | 0 | 1.5 | 12.2 | NO
[11 empty] | 2022-04-06 | 70.8% | 0% |  | 29.2% | 0% | 24 | 0 | 6.5 | 9.4 | NO
[11 empty] | 2022-04-07 | 81.19% | 0% |  | 18.81% | 0% | 24 | 0 | 1.8 | 10 | NO
[11 empty] | 2022-04-08 | 83.85% | 14.19% |  | 1.96% | 0% | 24 | 0 | 1.7 | 14.1 | NO
[11 empty] | 2022-04-09 | 83.26% | 15.49% |  | 1.25% | 0% | 24 | 0 | 1.5 | 14.4 | NO
[11 empty] | 2022-04-10 | 85.75% | 13.09% |  | 1.15% | 0% | 24 | 0 | 1 | 13.8 | NO
[11 empty] | 2022-04-11 | 86.39% | 12.5% |  | 1.12% | 0% | 24 | 0 | 0.8 | 13.7 | NO
[11 empty] | 2022-04-12 | 86.74% | 12.08% |  | 1.17% | 0% | 24 | 0 | 0.6 | 13.6 | NO
[11 empty] | 2022-04-13 | 79.59% | 8.65% |  | 11.77% | 0% | 24 | 0 | 3 | 12.4 | NO
[11 empty] | 2022-04-14 | 76.79% | 16.94% |  | 6.27% | 0% | 24 | 0 | 0.6 | 14.3 | NO
[11 empty] | 2022-04-15 | 76.24% | 17.69% |  | 6.08% | 0% | 24 | 0 | 0.5 | 14.6 | NO
[11 empty] | 2022-04-16 | 77.1% | 16.62% |  | 6.27% | 0% | 24 | 0 | 0.5 | 14.3 | NO
[11 empty] | 2022-04-17 | 74.71% | 18.95% |  | 6.34% | 0% | 24 | 0 | 0.5 | 14.8 | NO
[11 empty] | 2022-04-18 | 75.02% | 18.41% |  | 6.57% | 0% | 24 | 0 | 0.6 | 14.7 | NO
[11 empty] | 2022-04-19 | 76.89% | 16.82% |  | 6.3% | 0% | 24 | 0 | 0.7 | 14.4 | NO
[11 empty] | 2022-04-20 | 78.07% | 15.61% |  | 6.32% | 0% | 24 | 0 | 0.6 | 14.1 | NO
[11 empty] | 2022-04-21 | 76.2% | 16.88% |  | 6.92% | 0% | 24 | 0 | 0.5 | 14.4 | NO
[11 empty] | 2022-04-22 | 75.65% | 18.31% |  | 6.05% | 0% | 24 | 0 | 0.5 | 14.7 | NO
[11 empty] | 2022-04-23 | 76.1% | 18.11% |  | 5.79% | 0% | 24 | 0 | 0.5 | 14.7 | NO
[11 empty] | 2022-04-24 | 76.58% | 17.62% |  | 5.79% | 0% | 24 | 0 | 0.4 | 14.6 | NO
[11 empty] | 2022-04-25 | 80.56% | 13.62% |  | 5.83% | 0% | 24 | 0 | 0.5 | 13.6 | NO
[11 empty] | 2022-04-26 | 83.64% | 10.11% |  | 6.25% | 0% | 24 | 0 | 0.4 | 12.9 | NO
[11 empty] | 2022-04-27 | 86.26% | 9.62% |  | 4.13% | 0% | 24 | 0 | 0.5 | 12.9 | NO
[11 empty] | 2022-04-28 | 89.12% | 9.76% |  | 1.12% | 0% | 24 | 0 | 0.6 | 13.1 | NO
[11 empty] | 2022-04-29 | 81.46% | 13.23% |  | 5.31% | 0% | 24 | 0 | 1.1 | 13.5 | NO
[11 empty] | 2022-04-30 | 76.09% | 20.47% |  | 3.45% | 0% | 24 | 0 | 0.7 | 15.3 | NO
[11 empty] | 2022-05-01 | 85.04% | 14.33% |  | 0.62% | 0% | 24 | 0 | 0.6 | 14 | NO
[11 empty] | 2022-05-02 | 84.47% | 15.03% |  | 0.51% | 0% | 24 | 0 | 0.6 | 14.1 | NO
[11 empty] | 2022-05-03 | 88.78% | 10.31% |  | 0.9% | 0% | 24 | 0 | 0.5 | 13.2 | NO
[11 empty] | 2022-05-04 | 87.96% | 10.95% |  | 1.09% | 0% | 24 | 0 | 0.5 | 13.4 | NO
[11 empty] | 2022-05-05 | 87.24% | 11.62% |  | 1.14% | 0% | 24 | 0 | 0.6 | 13.5 | NO
[11 empty] | 2022-05-06 | 87.57% | 11.16% |  | 1.27% | 0% | 24 | 0 | 0.6 | 13.9 | NO
[11 empty] | 2022-05-07 | 83.54% | 15.59% |  | 0.86% | 0% | 24 | 0 | 1.1 | 15.5 | NO
[11 empty] | 2022-05-08 | 87.69% | 11.28% |  | 1.02% | 0% | 24 | 0 | 1 | 13.4 | NO
[11 empty] | 2022-05-09 | 87.27% | 11.73% |  | 1% | 0% | 24 | 0 | 0.4 | 13.5 | NO
[11 empty] | 2022-05-10 | 90.73% | 8.13% |  | 1.14% | 0% | 24 | 0 | 0.5 | 13.1 | NO
[11 empty] | 2022-05-11 | 89.8% | 8.84% |  | 1.36% | 0% | 24 | 0 | 1.1 | 12.9 | NO
[11 empty] | 2022-05-12 | 85.65% | 13.08% |  | 1.26% | 0% | 24 | 0 | 1.4 | 13.8 | NO
[11 empty] | 2022-05-13 | 87.32% | 11.48% |  | 1.2% | 0% | 24 | 0 | 0.7 | 13.5 | NO
[11 empty] | 2022-05-14 | 88.58% | 10.29% |  | 1.13% | 0% | 24 | 0 | 0.5 | 13.2 | NO
[11 empty] | 2022-05-15 | 88.01% | 10.89% |  | 1.1% | 0% | 24 | 0 | 0.4 | 13.3 | NO
[11 empty] | 2022-05-16 | 87.97% | 10.87% |  | 1.17% | 0% | 24 | 0 | 0.5 | 13.3 | NO
[11 empty] | 2022-05-17 | 87.9% | 10.91% |  | 1.19% | 0% | 24 | 0 | 0.3 | 13.3 | NO
[11 empty] | 2022-05-18 | 87.23% | 11.58% |  | 1.2% | 0% | 24 | 0 | 0.4 | 13.5 | NO
[11 empty] | 2022-05-19 | 87.8% | 11.01% |  | 1.2% | 0% | 24 | 0 | 0.5 | 13.4 | NO
[11 empty] | 2022-05-20 | 89.66% | 9.14% |  | 1.2% | 0% | 24 | 0 | 0.5 | 12.9 | NO
[11 empty] | 2022-05-21 | 89.01% | 9.83% |  | 1.16% | 0% | 24 | 0 | 0.5 | 13.1 | NO
[11 empty] | 2022-05-22 | 85.66% | 12.96% |  | 1.38% | 0% | 24 | 0 | 0.4 | 13.8 | NO
[11 empty] | 2022-05-23 | 83.15% | 13.78% |  | 3.07% | 0% | 24 | 0 | 1.9 | 13.9 | NO
[11 empty] | 2022-05-24 | 83.6% | 15.05% |  | 1.35% | 0% | 24 | 0 | 0.7 | 14.2 | NO
[11 empty] | 2022-05-25 | 87.92% | 10.54% |  | 1.55% | 0% | 24 | 0 | 0.6 | 13.2 | NO
[11 empty] | 2022-05-26 | 89.17% | 9.26% |  | 1.57% | 0% | 24 | 0 | 0.6 | 13 | NO
[11 empty] | 2022-05-27 | 89.72% | 8.73% |  | 1.55% | 0% | 24 | 0 | 0.5 | 12.8 | NO
[11 empty] | 2022-05-28 | 87.41% | 11.1% |  | 1.49% | 0% | 24 | 0 | 0.4 | 13.4 | NO
[11 empty] | 2022-05-29 | 86.71% | 11.78% |  | 1.51% | 0% | 24 | 0 | 0.4 | 13.5 | NO
[11 empty] | 2022-05-30 | 86.77% | 11.73% |  | 1.51% | 0% | 24 | 0 | 0.6 | 13.5 | NO
[11 empty] | 2022-05-31 | 88.59% | 9.98% |  | 1.43% | 0% | 24 | 0 | 0.5 | 13.1 | NO
[11 empty] | 2022-06-01 | 88.73% | 9.85% |  | 1.42% | 0% | 24 | 0 | 1.3 | 13.1 | NO
[11 empty] | 2022-06-02 | 88.3% | 10.44% |  | 1.26% | 0% | 24 | 0 | 1.1 | 13.2 | NO
[11 empty] | 2022-06-03 | 87.24% | 11.55% |  | 1.21% | 0% | 24 | 0 | 0.5 | 13.5 | NO
[11 empty] | 2022-06-04 | 86.66% | 11.88% |  | 1.47% | 0% | 24 | 0 | 0.5 | 13.6 | NO
[11 empty] | 2022-06-05 | 87.05% | 11.4% |  | 1.56% | 0% | 24 | 0 | 0.5 | 13.4 | NO
[11 empty] | 2022-06-06 | 87.5% | 10.24% |  | 2.26% | 0% | 24 | 0 | 1.4 | 13.2 | NO
[11 empty] | 2022-06-07 | 89.12% | 9.6% |  | 1.28% | 0% | 24 | 0 | 0.5 | 13.1 | NO
[11 empty] | 2022-06-08 | 89.66% | 9.13% |  | 1.2% | 0% | 24 | 0 | 1 | 12.9 | NO
[11 empty] | 2022-06-09 | 89.8% | 8.96% |  | 1.24% | 0% | 24 | 0 | 0.6 | 12.9 | NO
[11 empty] | 2022-06-10 | 90.04% | 8.72% |  | 1.25% | 0% | 24 | 0 | 0.5 | 12.9 | NO
[11 empty] | 2022-06-11 | 89.56% | 9.18% |  | 1.26% | 0% | 24 | 0 | 0.5 | 13 | NO
[11 empty] | 2022-06-12 | 89.82% | 8.89% |  | 1.29% | 0% | 24 | 0 | 0.5 | 12.9 | NO
[11 empty] | 2022-06-13 | 90.4% | 8.32% |  | 1.27% | 0% | 24 | 0 | 0.5 | 12.8 | NO
[11 empty] | 2022-06-14 | 90.28% | 8.48% |  | 1.24% | 0% | 24 | 0 | 0.5 | 12.8 | NO
[11 empty] | 2022-06-15 | 89.54% | 9.13% |  | 1.32% | 0% | 24 | 0 | 0.5 | 13 | NO
[11 empty] | 2022-06-16 | 87.77% | 10.75% |  | 1.49% | 0% | 24 | 0 | 0.6 | 13.4 | NO
[11 empty] | 2022-06-17 | 87.06% | 11.56% |  | 1.38% | 0% | 24 | 0 | 0.4 | 13.5 | NO
[11 empty] | 2022-06-18 | 88.06% | 10.65% |  | 1.29% | 0% | 24 | 0 | 0.4 | 13.4 | NO
[11 empty] | 2022-06-19 | 89.55% | 9.17% |  | 1.28% | 0% | 24 | 0 | 0.5 | 13.1 | NO
[11 empty] | 2022-06-20 | 89.54% | 9.19% |  | 1.27% | 0% | 24 | 0 | 0.6 | 13.1 | NO
[11 empty] | 2022-06-21 | 88.91% | 9.81% |  | 1.28% | 0% | 24 | 0 | 0.5 | 13.2 | NO
[11 empty] | 2022-06-22 | 87.49% | 11.26% |  | 1.24% | 0% | 24 | 0 | 0.5 | 13.5 | NO
[11 empty] | 2022-06-23 | 80.05% | 19.13% |  | 0.82% | 0% | 24 | 0 | 0.4 | 15.3 | NO
[11 empty] | 2022-06-24 | 78.03% | 20.94% |  | 1.03% | 0% | 24 | 0 | 0.5 | 15.7 | NO
[11 empty] | 2022-06-25 | 80.23% | 18.68% |  | 1.09% | 0% | 24 | 0 | 0.5 | 15.1 | NO
[11 empty] | 2022-06-26 | 81.66% | 17.24% |  | 1.1% | 0% | 24 | 0 | 0.6 | 14.8 | NO
[11 empty] | 2022-06-27 | 81.05% | 17.73% |  | 1.22% | 0% | 24 | 0 | 0.6 | 14.9 | NO
[11 empty] | 2022-06-28 | 78.55% | 19.95% |  | 1.5% | 0% | 24 | 0 | 1.1 | 15.5 | NO
[11 empty] | 2022-06-29 | 79.69% | 18.94% |  | 1.37% | 0% | 23 | 0 | 0.5 | 15.2 | NO
[11 empty] | 2022-06-30 | 78.21% | 20.59% |  | 1.19% | 0% | 24 | 0 | 0.5 | 15.5 | NO
[11 empty] | 0 | 84.28% | 11.73% | 0% | 3.991% | 0% | 24 | 0 | 1.0459 | 14.124 | NO
[11 empty] | 0 | 84.56% | 11.42% | 0% | 4.022% | 0% | 24 | 0 | 1.0763 | 13.9727 | NO

## A53 Mitchell Boiler
|  | Concentrations in mg/m³ at reference conditions after subtracting uncertainty | [9 empty] | Daily means, excluding hours outside normal operating conditions
|  | 2022-04-01 |  |  | 2022-05-01 |  |  | 2022-06-01 |  |  | Date | Fuel mix |  |  |  |  | Particulate Matter concentration (mg/m³) after subtracting uncertainty
|  | PM | SO2 | NOx | PM | SO2 | NOx | PM | SO2 | NOx |  | % BFG | % COG | % BOSg | % NG | % HFO | No.valid hours | No.hours OTNOC | Measured | Limit | Breach?
Daily means | Minimum | 0 | Discontinuous monitoring only |  | 0 | Discontinuous monitoring only |  | 1.8 | Discontinuous monitoring only |  | 2022-04-01 | 97.78% | 1.63% |  | 0.59% | 0% | 24 | 0 | 2.2 | 10.3 | NO
| Maximum | 2.4 |  |  | 3 |  |  | 1.8 |  |  | 2022-04-02 | 97.31% | 2.2% |  | 0.48% | 0% | 24 | 0 | 2.4 | 10.4 | NO
| No. > Limit | 0 |  |  | 0 |  |  | 0 |  |  | 2022-04-03 | 97.45% | 2.11% |  | 0.44% | 0% | 24 | 0 | 2.4 | 10.4 | NO
Monthly mean |  | 2.1 |  |  | 2.2 |  |  | 3 |  |  | 2022-04-04 | 96.24% | 2.16% |  | 1.6% | 0.01% | 24 | 0 | 2.1 | 10.4 | NO
Monthly mean limit |  | 10.4 |  |  | 9.1 |  |  | 11.3 |  |  | 2022-04-05 | 97.05% | 1% |  | 1.94% | 0% | 24 | 0 | 2.2 | 10.1 | NO
[11 empty] | 2022-04-06 | 95.02% | 0.52% |  | 4.46% | 0% | 24 | 0 | 2.4 | 9.9 | NO
[11 empty] | 2022-04-07 | 94.48% | 1.08% |  | 4.43% | 0.01% | 24 | 0 | 2.3 | 10 | NO
[11 empty] | 2022-04-08 | 94.09% | 4.79% |  | 1.11% | 0.01% | 24 | 0 | 0 | 11 | NO
[11 empty] | 2022-04-09 | 97.46% | 2.03% |  | 0.51% | 0% | 24 | 0 | 2.3 | 10.4 | NO
[11 empty] | 2022-04-10 | 98.22% | 1.3% |  | 0.47% | 0% | 24 | 0 | 2.1 | 10.2 | NO
[11 empty] | 2022-04-11 | 97.43% | 2.06% |  | 0.5% | 0.01% | 24 | 0 | 2.1 | 10.4 | NO
[11 empty] | 2022-04-12 | 96.99% | 2.56% |  | 0.45% | 0.01% | 24 | 0 | 1.8 | 10.5 | NO
[11 empty] | 2022-04-13 | 93.13% | 3.51% |  | 3.36% | 0.01% | 24 | 0 | 2.3 | 10.6 | NO
[11 empty] | 2022-04-14 | 95.92% | 3.36% |  | 0.71% | 0% | 24 | 0 | 2.3 | 10.7 | NO
[11 empty] | 2022-04-15 | 96.48% | 2.94% |  | 0.57% | 0.01% | 24 | 0 | 2 | 10.6 | NO
[11 empty] | 2022-04-16 | 96.44% | 2.81% |  | 0.74% | 0.01% | 24 | 0 | 1.6 | 10.6 | NO
[11 empty] | 2022-04-17 | 97.37% | 2.14% |  | 0.48% | 0.01% | 24 | 0 | 1.8 | 10.4 | NO
[11 empty] | 2022-04-18 | 96.88% | 2.62% |  | 0.49% | 0% | 24 | 0 | 2 | 10.5 | NO
[11 empty] | 2022-04-19 | 97.76% | 1.76% |  | 0.47% | 0.01% | 24 | 0 | 2 | 10.3 | NO
[11 empty] | 2022-04-20 | 97.19% | 2.38% |  | 0.44% | 0% | 24 | 0 | 1.8 | 10.4 | NO
[11 empty] | 2022-04-21 | 95.08% | 2.65% |  | 2.26% | 0.01% | 24 | 0 | 1.9 | 10.5 | NO
[11 empty] | 2022-04-22 | 97.46% | 2.06% |  | 0.47% | 0% | 24 | 0 | 2 | 10.4 | NO
[11 empty] | 2022-04-23 | 97.14% | 2.35% |  | 0.5% | 0% | 24 | 0 | 2.1 | 10.4 | NO
[11 empty] | 2022-04-24 | 97.38% | 2.15% |  | 0.46% | 0% | 24 | 0 | 1.8 | 10.4 | NO
[11 empty] | 2022-04-25 | 96.21% | 3.36% |  | 0.43% | 0% | 24 | 0 | 1.9 | 10.7 | NO
[11 empty] | 2022-04-26 | 96.32% | 3.15% |  | 0.53% | 0.01% | 24 | 0 | 1.8 | 10.6 | NO
[11 empty] | 2022-04-27 | 97.19% | 2.36% |  | 0.44% | 0.01% | 24 | 0 | 1.9 | 10.5 | NO
[11 empty] | 2022-04-28 | 97.68% | 1.85% |  | 0.46% | 0.01% | 24 | 0 | 2 | 10.4 | NO
[11 empty] | 2022-04-29 | 96% | 2.65% |  | 1.34% | 0.01% | 24 | 0 | 1.9 | 10.5 | NO
[11 empty] | 2022-04-30 | 95.89% | 3.69% |  | 0.41% | 0.01% | 24 | 0 | 1.9 | 10.7 | NO
[11 empty] | 2022-05-01 | 95.8% | 3.67% |  | 0.52% | 0.01% | 24 | 0 | 2.2 | 10.7 | NO
[11 empty] | 2022-05-02 | 96.69% | 2.6% |  | 0.71% | 0% | 24 | 0 | 2.2 | 10.5 | NO
[11 empty] | 2022-05-03 | 97.17% | 2.28% |  | 0.55% | 0.01% | 24 | 0 | 2 | 10.4 | NO
[11 empty] | 2022-05-04 | 94.44% | 4.61% |  | 0.95% | 0% | 24 | 0 | 2.2 | 10.9 | NO
[11 empty] | 2022-05-05 | 93.86% | 5.52% |  | 0.62% | 0.01% | 24 | 0 | 2.6 | 11.1 | NO
[11 empty] | 2022-05-06 | 95.62% | 3.65% |  | 0.72% | 0.01% | 24 | 0 | 2.5 | 10.8 | NO
[11 empty] | 2022-05-07 | 96.26% | 3.3% |  | 0.43% | 0.01% | 24 | 0 | 1.9 | 10.6 | NO
[11 empty] | 2022-05-08 | 96.28% | 3.24% |  | 0.48% | 0.01% | 24 | 0 | 0 | 10.6 | NO
[11 empty] | 2022-05-09 | 95.76% | 3.5% |  | 0.73% | 0% | 24 | 0 | 2.1 | 10.7 | NO
[11 empty] | 2022-05-10 | 94.37% | 4.92% |  | 0.71% | 0.01% | 24 | 0 | 3 | 11 | NO
[11 empty] | 2022-05-11 | 96.57% | 2.68% |  | 0.75% | 0.01% | 24 | 0 | 2.8 | 10.6 | NO
[11 empty] | 2022-05-12 | 97.94% | 1.63% |  | 0.43% | 0% | 24 | 0 | 2.1 | 10.3 | NO
[11 empty] | 2022-05-13 | 97.89% | 1.64% |  | 0.47% | 0% | 24 | 0 | 2.4 | 10.3 | NO
[11 empty] | 2022-05-14 | 97.63% | 1.91% |  | 0.45% | 0.01% | 24 | 0 | 2 | 10.4 | NO
[11 empty] | 2022-05-15 | 97.45% | 1.97% |  | 0.58% | 0.01% | 24 | 0 | 1.9 | 10.4 | NO
[11 empty] | 2022-05-16 | 98.11% | 1.44% |  | 0.45% | 0.01% | 24 | 0 | 1.7 | 10.3 | NO
[11 empty] | 2022-05-17 | 97.19% | 2.15% |  | 0.65% | 0.01% | 24 | 0 | 2.1 | 10.4 | NO
[11 empty] | 2022-05-18 | 97.55% | 1.9% |  | 0.54% | 0% | 24 | 0 | 1.9 | 10.4 | NO
[11 empty] | 2022-05-19 | 97.27% | 2.14% |  | 0.58% | 0.01% | 24 | 0 | 2.2 | 10.4 | NO
[11 empty] | 2022-05-20 | 94.79% | 3.14% |  | 2.06% | 0.02% | 24 | 0 | 2.4 | 10.6 | NO
[11 empty] | 2022-05-21 | 94.09% | 5.11% |  | 0.79% | 0.01% | 24 | 0 | 2.5 | 11 | NO
[11 empty] | 2022-05-22 | 96% | 3.42% |  | 0.58% | 0% | 24 | 0 | 2.6 | 10.7 | NO
[11 empty] | 2022-05-23 | 94.59% | 3.92% |  | 1.48% | 0.01% | 24 | 0 | 2.6 | 10.7 | NO
[11 empty] | 2022-05-24 | 96.08% | 3.31% |  | 0.61% | 0.01% | 24 | 0 | 2.3 | 10.6 | NO
[11 empty] | 2022-05-25 | 96.17% | 3.16% |  | 0.67% | 0% | 24 | 0 | 2.4 | 10.6 | NO
[11 empty] | 2022-05-26 | 97.8% | 1.77% |  | 0.43% | 0% | 24 | 0 | 2.1 | 10.3 | NO
[11 empty] | 2022-05-27 | 97.44% | 1.87% |  | 0.68% | 0.01% | 24 | 0 | 2.1 | 4.9 | NO
[11 empty] | 2022-05-28 | OFF
[11 empty] | 2022-05-29 | OFF
[11 empty] | 2022-05-30 | OFF
[11 empty] | 2022-05-31 | OFF
[11 empty] | 2022-06-01 | OFF
[11 empty] | 2022-06-02 | OFF
[11 empty] | 2022-06-03 | OFF
[11 empty] | 2022-06-04 | OFF
[11 empty] | 2022-06-05 | OFF
[11 empty] | 2022-06-06 | OFF
[11 empty] | 2022-06-07 | OFF
[11 empty] | 2022-06-08 | OFF
[11 empty] | 2022-06-09 | OFF
[11 empty] | 2022-06-10 | OFF
[11 empty] | 2022-06-11 | OFF
[11 empty] | 2022-06-12 | OFF
[11 empty] | 2022-06-13 | OFF
[11 empty] | 2022-06-14 | OFF
[11 empty] | 2022-06-15 | OFF
[11 empty] | 2022-06-16 | OFF
[11 empty] | 2022-06-17 | OFF
[11 empty] | 2022-06-18 | OFF
[11 empty] | 2022-06-19 | OFF
[11 empty] | 2022-06-20 | OFF
[11 empty] | 2022-06-21 | OFF
[11 empty] | 2022-06-22 | OFF
[11 empty] | 2022-06-23 | OFF
[11 empty] | 2022-06-24 | OFF
[11 empty] | 2022-06-25 | OFF
[11 empty] | 2022-06-26 | OFF
[11 empty] | 2022-06-27 | OFF
[11 empty] | 2022-06-28 | OFF
[11 empty] | 2022-06-29 | OFF
[11 empty] | 2022-06-30 | 92.19% | 4.39% |  | 1.79% | 1.63% | 24 | 0 | 1.8 | 10.4 | NO
[11 empty] | 0 | 93.73% | 5.191% |  | 1.078% | 0.006667% | 24 | 0 | 1.948 | 10.9871 | NO
[11 empty] | 0 | 92.76% | 5.789% |  | 1.444% | 0.004511% | 24 | 0 | 2.1552 | 11.1145 | NO

## A62 Boiler 3
|  | Concentrations in mg/m³ at reference conditions after subtracting uncertainty | [9 empty] | Daily means, excluding hours outside normal operating conditions
|  | 2022-04-01 |  |  | 2022-05-01 |  |  | 2022-06-01 |  |  | Date | Fuel mix |  |  |  |  | Particulate Matter concentration (mg/m³) after subtracting uncertainty |  |  |  |  | Sulphur dioxide concentration (mg/m³) after subtracting uncertainty |  |  |  |  | Oxides of nitrogen concentration (mg/m³) after subtracting uncertainty
|  | PM | SO2 | NOx | PM | SO2 | NOx | PM | SO2 | NOx |  | % BFG | % COG | % BOSg | % NG | % HFO | No.valid hours | No.hours OTNOC | Measured | Limit | Breach? | No.valid hours | No.hours OTNOC | Measured | Limit | Breach? | No.valid hours | No.hours OTNOC | Measured | Limit | Breach?
Daily means | Minimum | 0.8 | 27.4 | Monitor out of calibration (Part A - S5N_21_76A) | 0.4 | 34.6 | Monitor out of calibration (Part A - S5N_21_76A) | 0.1 | 36.6 | Monitor out of calibration (Part A - S5N_21_76A) | 2022-04-01 | 96.06% | 0.76% |  | 3.18% |  | 24 | 1 | 1.6 | 11 | NO | 24 | 1 | 47.3 | 215.9 | NO | 24 | 1 |  | 216.5 | NO
| Maximum | 3.4 | 59 |  | 2.5 | 103.2 |  | 3.5 | 67.7 |  | 2022-04-02 | 98.98% | 0.99% |  | 0.04% |  | 24 | 0 | 2 | 11.2 | NO | 24 | 0 | 39.1 | 222.1 | NO | 24 | 0 |  | 220 | NO
| No. > Limit | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 2022-04-03 | 99.92% | 0.03% |  | 0.06% |  | 24 | 0 | 1.3 | 11 | NO | 24 | 0 | 45.5 | 220 | NO | 24 | 0 |  | 219.9 | NO
Monthly mean |  | 1.5 | 59 |  | 1.1 | 50.3 |  | 0.7 | 55.9 |  | 2022-04-04 | 99.81% | 0.16% |  | 0.04% |  | 24 | 0 | 1.1 | 11 | NO | 24 | 0 | 45.9 | 220.3 | NO | 24 | 0 |  | 220 | NO
Monthly mean limit |  | 9.5 | 184.9 | 189.4 | 9 | 175.4 | 180.6 | 8.5 | 163 | 171 | 2022-04-05 | 99.77% | 0.21% |  | 0.02% |  | 24 | 0 | 1.1 | 11 | NO | 24 | 0 | 43.9 | 220.4 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-04-06 | 99.73% | 0.26% |  | 0.01% |  | 24 | 0 | 1.1 | 11.1 | NO | 24 | 0 | 44.5 | 220.5 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-04-07 | 99.46% | 0.51% |  | 0.03% |  | 24 | 0 | 1.2 | 11.1 | NO | 24 | 0 | 44.8 | 221.1 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-04-08 | 27.19% | 4.85% |  | 67.96% |  | 24 | 18 | 1.8 | 8.3 | NO | 24 | 18 | 40.8 | 107.3 | NO | 24 | 18 |  | 145.2 | NO
[11 empty] | 2022-04-09 | 83.73% | 3.69% |  | 12.57% |  | 24 | 3 | 3.3 | 11.1 | NO | 24 | 3 | 51.6 | 205.3 | NO | 24 | 3 |  | 206.2 | NO
[11 empty] | 2022-04-10 | 99.84% | 0.11% |  | 0.05% |  | 24 | 0 | 1.6 | 11 | NO | 24 | 0 | 36.5 | 220.1 | NO | 24 | 0 |  | 219.9 | NO
[11 empty] | 2022-04-11 | 99.71% | 0.28% |  | 0.01% |  | 24 | 0 | 1.2 | 11.1 | NO | 24 | 0 | 38.5 | 220.6 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-04-12 | 99.64% | 0.36% |  | 0% |  | 24 | 0 | 0.8 | 11.1 | NO | 24 | 0 | 53.7 | 220.8 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-04-13 | 79.29% | 0.76% |  | 19.95% |  | 24 | 2 | 2.5 | 10.1 | NO | 24 | 2 | 27.4 | 185.5 | NO | 24 | 2 |  | 198.1 | NO
[11 empty] | 2022-04-14 | 65.98% | 17.91% |  | 16.11% |  | 24 | 7 | 2.5 | 14.1 | NO | 24 | 7 | 43.9 | 230.2 | NO | 24 | 7 |  | 202.3 | NO
[11 empty] | 2022-04-15 | 77.48% | 11.12% |  | 11.41% |  | 24 | 4 | 2.8 | 12.8 | NO | 24 | 4 | 46.8 | 223.7 | NO | 24 | 4 |  | 207.5 | NO
[11 empty] | 2022-04-16 | 61.11% | 4.02% |  | 34.86% |  | 24 | 9 | 3.4 | 10 | NO | 24 | 9 | 45.3 | 165.6 | NO | 24 | 9 |  | 181.6 | NO
[11 empty] | 2022-04-17 | 99.9% | 0.08% |  | 0.01% |  | 24 | 0 | 1 | 11 | NO | 24 | 0 | 45.7 | 220.2 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-04-18 | 98.08% | 0.07% |  | 1.85% |  | 24 | 0 | 1.2 | 10.9 | NO | 24 | 0 | 33.9 | 216.8 | NO | 24 | 0 |  | 218 | NO
[11 empty] | 2022-04-19 | 99.07% | 0.39% |  | 0.53% |  | 24 | 0 | 1.4 | 11.1 | NO | 24 | 0 | 53.9 | 219.9 | NO | 24 | 0 |  | 219.4 | NO
[11 empty] | 2022-04-20 | 99.66% | 0.33% |  | 0.01% |  | 24 | 0 | 0.8 | 11.1 | NO | 24 | 0 | 51.3 | 220.7 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-04-21 | 73.93% | 0.53% |  | 25.54% |  | 24 | 7 | 3.2 | 9.7 | NO | 24 | 7 | 33 | 174.8 | NO | 24 | 7 |  | 191.9 | NO
[11 empty] | 2022-04-22 | 99.95% | 0.04% |  | 0.01% |  | 24 | 0 | 1.3 | 11 | NO | 24 | 0 | 41.4 | 220.1 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-04-23 | 98.18% | 1.81% |  | 0.01% |  | 24 | 0 | 1.3 | 11.4 | NO | 24 | 0 | 30.5 | 224 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-04-24 | 99.93% | 0.07% |  | 0% |  | 24 | 0 | 1.3 | 11 | NO | 24 | 0 | 35.6 | 220.1 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-04-25 | 99.82% | 0.17% |  | 0.01% |  | 24 | 0 | 0.9 | 11 | NO | 24 | 0 | 48.2 | 220.4 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-04-26 | 76.92% | 6.15% |  | 16.93% |  | 24 | 6 | 0.8 | 11.4 | NO | 24 | 6 | 44.2 | 202.8 | NO | 24 | 6 |  | 201.4 | NO
[11 empty] | 2022-04-27 | 97.23% | 1.05% |  | 1.71% |  | 24 | 1 | 1.3 | 11.1 | NO | 24 | 1 | 52.2 | 219.2 | NO | 24 | 1 |  | 218.1 | NO
[11 empty] | 2022-04-28 | 99.83% | 0.16% |  | 0.01% |  | 24 | 0 | 1.2 | 11 | NO | 24 | 0 | 44.5 | 220.3 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-04-29 | 99.71% | 0.29% |  | 0.01% |  | 24 | 0 | 1.1 | 11.1 | NO | 24 | 0 | 45.3 | 220.6 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-04-30 | 99.55% | 0.44% |  | 0.01% |  | 24 | 0 | 0.9 | 11.1 | NO | 24 | 0 | 59 | 220.9 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-05-01 | 99.35% | 0.64% |  | 0.01% |  | 24 | 0 | 1 | 11.1 | NO | 24 | 0 | 43.5 | 221.4 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-05-02 | 58.71% | 1.63% |  | 39.65% |  | 24 | 10 | 1.6 | 9.2 | NO | 24 | 10 | 54 | 151.6 | NO | 24 | 10 |  | 176.4 | NO
[11 empty] | 2022-05-03 | 34.65% | 26.21% |  | 39.14% |  | 24 | 16 | 2.3 | 14.6 | NO | 24 | 16 | 61.1 | 206.6 | NO | 24 | 16 |  | 176.9 | NO
[11 empty] | 2022-05-04 | 40.89% | 25.76% |  | 33.35% |  | 24 | 13 | 1.4 | 14.8 | NO | 24 | 13 | 85.2 | 216.1 | NO | 24 | 13 |  | 183.3 | NO
[11 empty] | 2022-05-05 | 39.61% | 33.03% |  | 27.36% |  | 24 | 12 | 2.2 | 16.8 | NO | 24 | 12 | 103.2 | 243 | NO | 24 | 12 |  | 189.9 | NO
[11 empty] | 2022-05-06 | 54.47% | 15.86% |  | 29.67% |  | 24 | 12 | 2.3 | 12.9 | NO | 24 | 12 | 47.9 | 201 | NO | 24 | 12 |  | 187.4 | NO
[11 empty] | 2022-05-07 | 99.95% | 0.04% |  | 0.01% |  | 24 | 0 | 0.9 | 11 | NO | 24 | 0 | 50 | 220.1 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-05-08 | 99.92% | 0.07% |  | 0.01% |  | 24 | 0 | 0.8 | 11 | NO | 24 | 0 | 42.6 | 220.1 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-05-09 | 91.08% | 0.21% |  | 8.72% |  | 24 | 3 | 1 | 10.6 | NO | 24 | 3 | 39.3 | 204.6 | NO | 24 | 3 |  | 210.4 | NO
[11 empty] | 2022-05-10 | 81.58% | 9.92% |  | 8.5% |  | 24 | 4 | 1.5 | 12.7 | NO | 24 | 4 | 35.8 | 226.4 | NO | 24 | 4 |  | 210.7 | NO
[11 empty] | 2022-05-11 | 51.78% | 24.57% |  | 23.65% |  | 24 | 12 | 2.1 | 15.1 | NO | 24 | 12 | 63.9 | 231.1 | NO | 24 | 12 |  | 194 | NO
[11 empty] | 2022-05-12 | 99.95% | 0.04% |  | 0.01% |  | 24 | 0 | 1.7 | 11 | NO | 24 | 0 | 40.1 | 220.1 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-05-13 | 99.91% | 0.09% |  | 0% |  | 24 | 0 | 1 | 11 | NO | 24 | 0 | 48.3 | 220.2 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-05-14 | 99.85% | 0.15% |  | 0% |  | 24 | 0 | 0.6 | 11 | NO | 24 | 0 | 50.6 | 220.3 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-05-15 | 99.9% | 0.09% |  | 0% |  | 24 | 0 | 0.7 | 11 | NO | 24 | 0 | 48.4 | 220.2 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-05-16 | 97.9% | 2.09% |  | 0.01% |  | 24 | 0 | 0.7 | 11.5 | NO | 24 | 0 | 37.2 | 224.6 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-05-17 | 99.9% | 0.09% |  | 0.01% |  | 24 | 0 | 0.9 | 11 | NO | 24 | 0 | 40 | 220.2 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-05-18 | 99.96% | 0.04% |  | 0.01% |  | 24 | 0 | 1 | 11 | NO | 24 | 0 | 52.1 | 220.1 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-05-19 | 99.86% | 0.12% |  | 0.02% |  | 24 | 0 | 1 | 11 | NO | 24 | 0 | 40.4 | 220.2 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-05-20 | 85.24% | 0.41% |  | 14.36% |  | 24 | 3 | 1.1 | 10.3 | NO | 24 | 3 | 55.2 | 194.8 | NO | 24 | 3 |  | 204.2 | NO
[11 empty] | 2022-05-21 | 90.45% | 7.69% |  | 1.87% |  | 24 | 1 | 1.2 | 12.6 | NO | 24 | 1 | 56.6 | 233.5 | NO | 24 | 1 |  | 217.9 | NO
[11 empty] | 2022-05-22 | 94.45% | 5.54% |  | 0.01% |  | 24 | 0 | 1.1 | 12.2 | NO | 24 | 0 | 60.6 | 232.2 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-05-23 | 92.02% | 3.52% |  | 4.46% |  | 24 | 1 | 2.5 | 11.5 | NO | 24 | 1 | 44.9 | 219.6 | NO | 24 | 1 |  | 215.1 | NO
[11 empty] | 2022-05-24 | 99.9% | 0.09% |  | 0.02% |  | 24 | 0 | 0.9 | 11 | NO | 24 | 0 | 34.6 | 220.2 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-05-25 | 99.73% | 0.19% |  | 0.08% |  | 24 | 0 | 1.1 | 11 | NO | 24 | 0 | 35.4 | 220.3 | NO | 24 | 0 |  | 219.9 | NO
[11 empty] | 2022-05-26 | 99.84% | 0.11% |  | 0.04% |  | 24 | 0 | 0.6 | 11 | NO | 24 | 0 | 52.5 | 220.2 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-05-27 | 79.91% | 3.29% |  | 16.8% |  | 24 | 5 | 0.4 | 10.8 | NO | 24 | 5 | 54 | 196.8 | NO | 24 | 5 |  | 201.5 | NO
[11 empty] | 2022-05-28 | 92.53% | 7.46% |  | 0.01% |  | 24 | 0 | 0.4 | 12.6 | NO | 24 | 0 | 66.4 | 236.4 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-05-29 | 92.08% | 7.9% |  | 0.02% |  | 24 | 0 | 0.6 | 12.7 | NO | 24 | 0 | 63.6 | 237.3 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-05-30 | 99.53% | 0.05% |  | 0.42% |  | 24 | 0 | 0.6 | 11 | NO | 24 | 0 | 46.5 | 219.3 | NO | 24 | 0 |  | 219.5 | NO
[11 empty] | 2022-05-31 | 99.9% | 0.09% |  | 0.01% |  | 24 | 0 | 0.4 | 11 | NO | 24 | 0 | 62.8 | 220.2 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-06-01 | 68.51% | 7.34% |  | 24.15% |  | 24 | 7 | 0.6 | 11.3 | NO | 24 | 7 | 54 | 192.3 | NO | 24 | 7 |  | 193.4 | NO
[11 empty] | 2022-06-02 | 99.96% | 0.03% |  | 0.01% |  | 24 | 0 | 0.3 | 11 | NO | 24 | 0 | 55.4 | 220.1 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-06-03 | 99.95% | 0.04% |  | 0.01% |  | 24 | 0 | 0.2 | 11 | NO | 24 | 0 | 55.1 | 220.1 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-06-04 | 99.54% | 0.05% |  | 0.41% |  | 24 | 0 | 0.3 | 11 | NO | 24 | 0 | 52.8 | 219.4 | NO | 24 | 0 |  | 219.6 | NO
[11 empty] | 2022-06-05 | 87.49% | 12.5% |  | 0.01% |  | 24 | 0 | 0.8 | 13.7 | NO | 24 | 0 | 54.8 | 247.5 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-06-06 | 94.31% | 3.81% |  | 1.88% |  | 24 | 0 | 0.3 | 11.7 | NO | 24 | 0 | 58.9 | 225 | NO | 24 | 0 |  | 217.9 | NO
[11 empty] | 2022-06-07 | 97.97% | 2.02% |  | 0.01% |  | 24 | 0 | 0.3 | 11.4 | NO | 24 | 0 | 61.3 | 224.4 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-06-08 | 99.96% | 0.03% |  | 0.01% |  | 24 | 0 | 0.4 | 11 | NO | 24 | 0 | 59.1 | 220 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-06-09 | 99.65% | 0.34% |  | 0.01% |  | 24 | 0 | 0.8 | 11.1 | NO | 24 | 0 | 60.4 | 220.7 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-06-10 | 98.8% | 1.19% |  | 0.01% |  | 24 | 0 | 0.6 | 11.3 | NO | 24 | 0 | 59.4 | 222.6 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-06-11 | 99.93% | 0.06% |  | 0.01% |  | 24 | 0 | 0.7 | 11 | NO | 24 | 0 | 59.1 | 220.1 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-06-12 | 99.86% | 0.12% |  | 0.02% |  | 24 | 0 | 0.8 | 11 | NO | 24 | 0 | 62 | 220.2 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-06-13 | 99.97% | 0.02% |  | 0.01% |  | 24 | 0 | 0.7 | 11 | NO | 24 | 0 | 67.7 | 220 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-06-14 | 99.95% | 0.03% |  | 0.01% |  | 24 | 0 | 0.6 | 11 | NO | 24 | 0 | 59.8 | 220.1 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-06-15 | 99.96% | 0.03% |  | 0.02% |  | 24 | 0 | 0.6 | 11 | NO | 24 | 0 | 58.5 | 220 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-06-16 | 35.66% | 22.67% |  | 41.67% |  | 24 | 16 | 1.3 | 13.7 | NO | 24 | 16 | 65.1 | 194.3 | NO | 24 | 16 |  | 174.2 | NO
[11 empty] | 2022-06-17 | 93.97% | 5.99% |  | 0.04% |  | 24 | 0 | 0.5 | 12.3 | NO | 24 | 0 | 59.1 | 233.1 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-06-18 | 99.91% | 0.06% |  | 0.03% |  | 24 | 0 | 1 | 11 | NO | 24 | 0 | 42.9 | 220.1 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-06-19 | 99.86% | 0.11% |  | 0.03% |  | 24 | 0 | 1 | 11 | NO | 24 | 0 | 54.9 | 220.2 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-06-20 | 99.94% | 0.04% |  | 0.02% |  | 24 | 0 | 0.7 | 11 | NO | 24 | 0 | 50.7 | 220 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-06-21 | 95.84% | 3.43% |  | 0.73% |  | 24 | 1 | 0.5 | 11.7 | NO | 24 | 1 | 45.2 | 226.2 | NO | 24 | 1 |  | 219.2 | NO
[11 empty] | 2022-06-22 | 99.95% | 0.03% |  | 0.02% |  | 24 | 0 | 0.2 | 11 | NO | 24 | 0 | 44.9 | 220 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-06-23 | 99.92% | 0.03% |  | 0.04% |  | 24 | 0 | 0.1 | 11 | NO | 24 | 0 | 49.9 | 220 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-06-24 | 76.79% | 0.1% |  | 23.11% |  | 24 | 6 | 1.2 | 9.8 | NO | 24 | 6 | 54.5 | 178.3 | NO | 24 | 6 |  | 194.6 | NO
[11 empty] | 2022-06-25 | 99.26% | 0.73% |  | 0% |  | 24 | 0 | 1.1 | 11.2 | NO | 24 | 0 | 56.9 | 221.6 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2022-06-26 | 60.26% | 12.25% |  | 27.49% |  | 24 | 9 | 1 | 12.2 | NO | 24 | 9 | 63.5 | 197.1 | NO | 24 | 9 |  | 189.8 | NO
[11 empty] | 2022-06-27 | 14.13% | 18.18% |  | 67.69% |  | 24 | 21 | 2.6 | 11.3 | NO | 24 | 21 | 36.6 | 137.1 | NO | 24 | 21 |  | 145.5 | NO
[11 empty] | 2022-06-28 | 15.19% | 38.23% |  | 46.58% |  | 24 | 21 | 3.5 | 16.8 | NO | 24 | 21 | 49.6 | 219.6 | NO | 24 | 21 |  | 168.8 | NO
[11 empty] | 2022-06-29 | 1.4% | 47.66% |  | 50.94% |  | 24 | 24 |  | 18.7 | NO | 24 | 24 |  | 232.4 | NO | 24 | 24 |  | 164 | NO
[11 empty] | 2022-06-30 | 2.36% | 46.25% |  | 51.39% |  | 24 | 24 |  | 18.3 | NO | 24 | 24 |  | 228.5 | NO | 24 | 24 |  | 163.5 | NO
[11 empty] | 0 | 99.79% | 0.2056% | 0% | 0% |  | 24 | 0 | 1.3433 | 11.0452 | NO | 24 | 0 | 22.8636 | 220.4524 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 0 | 99.53% | 0.4709% | 0% | 0% |  | 24 | 0 | 2.2054 | 11.1036 | NO | 24 | 0 | 25.3225 | 221.036 | NO | 24 | 0 |  | 220 | NO

## A52A Boiler 6
|  | Concentrations in mg/m³ at reference conditions after subtracting uncertainty | [9 empty] | Daily means, excluding hours outside normal operating conditions
|  | 2022-04-01 |  |  | 2022-05-01 |  |  | 2022-06-01 |  |  | Date | Fuel mix |  |  |  |  | Particulate Matter concentration (mg/m³) after subtracting uncertainty |  |  |  |  | Sulphur dioxide concentration (mg/m³) after subtracting uncertainty |  |  |  |  | Oxides of nitrogen concentration (mg/m³) after subtracting uncertainty
|  | PM | SO2 | NOx | PM | SO2 | NOx | PM | SO2 | NOx |  | % BFG | % COG | % BOSg | % NG | % HFO | No.valid hours | No.hours OTNOC | Measured | Limit | Breach? | No.valid hours | No.hours OTNOC | Measured | Limit | Breach? | No.valid hours | No.hours OTNOC | Measured | Limit | Breach?
Daily means | Minimum | 1.2 | 38.6 | 33.4 | 1.1 | 32.2 | 33.5 | 0.9 | 61.9 | 36.6 | 2022-04-01 | 76.05% | 9.69% | 3.86% | 10.4% | 0% | 24 | 0 | 1.5 | 15.2 | NO | 24 | 0 | 59.7 | 234.3 | NO | 24 | 0 | 37.9 | 321.4 | NO
| Maximum | 1.6 | 85.2 | 63.4 | 1.5 | 92.3 | 91.8 | 1.7 | 90.5 | 95.2 | 2022-04-02 | 82.52% | 11.2% | 4.07% | 2.21% | 0% | 24 | 0 | 1.6 | 13.7 | NO | 24 | 0 | 57.5 | 237 | NO | 24 | 0 | 37.3 | 321 | NO
| No. > Limit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2022-04-03 | 75.69% | 8.51% | 4.58% | 11.22% | 0% | 24 | 0 | 1.5 | 15.1 | NO | 24 | 0 | 63.3 | 230.5 | NO | 24 | 0 | 39 | 319.9 | NO
Monthly mean |  | 1.5 | 63.6 | 39.6 | 1.3 | 62.4 | 46.8 | 1.3 | 75.5 | 59.7 | 2022-04-04 | 74.67% | 5.59% | 10.34% | 9.4% | 0% | 24 | 0 | 1.3 | 13.7 | NO | 24 | 0 | 52.3 | 213.4 | NO | 24 | 0 | 34.8 | 307.2 | NO
Monthly mean limit |  | 13.4 | 206.7 | 283.4 | 13.5 | 201.9 | 277.5 | 14.9 | 218.5 | 290.5 | 2022-04-05 | 78.33% | 3.68% | 10.49% | 7.5% | 0% | 24 | 0 | 1.3 | 12.9 | NO | 24 | 0 | 51.6 | 209.2 | NO | 24 | 0 | 35.4 | 307 | NO
[11 empty] | 2022-04-06 | 77.79% | 0.3% | 10.62% | 11.3% | 0% | 24 | 0 | 1.3 | 13 | NO | 24 | 0 | 38.6 | 201.4 | NO | 24 | 0 | 34.6 | 306.6 | NO
[11 empty] | 2022-04-07 | 77.84% | 0.64% | 12.05% | 9.47% | 0% | 24 | 0 | 1.4 | 12.6 | NO | 24 | 0 | 42.6 | 199.6 | NO | 24 | 0 | 34.3 | 303.5 | NO
[11 empty] | 2022-04-08 | 58.31% | 14.77% | 20.79% | 6.13% | 0% | 24 | 0 | 1.6 | 14.1 | NO | 24 | 0 | 53.6 | 214 | NO | 24 | 0 | 36.7 | 281.2 | NO
[11 empty] | 2022-04-09 | 79.14% | 9.56% | 5.58% | 5.72% | 0% | 24 | 0 | 1.4 | 14 | NO | 24 | 0 | 66.6 | 230.8 | NO | 24 | 0 | 33.5 | 317.6 | NO
[11 empty] | 2022-04-10 | 81.69% | 8.32% | 4.35% | 5.63% | 0% | 24 | 0 | 1.4 | 13.8 | NO | 24 | 0 | 69.4 | 230.4 | NO | 24 | 0 | 36.5 | 320.5 | NO
[11 empty] | 2022-04-11 | 77.89% | 6.2% | 2.64% | 13.27% | 0% | 24 | 0 | 1.3 | 15.1 | NO | 24 | 0 | 66.3 | 228.9 | NO | 24 | 0 | 33.8 | 324.2 | NO
[11 empty] | 2022-04-12 | 79.53% | 8.45% | 2.89% | 9.13% | 0% | 24 | 3 | 1.2 | 14.7 | NO | 24 | 3 | 85.2 | 233.2 | NO | 24 | 3 | 33.8 | 323.6 | NO
[11 empty] | 2022-04-13 | 53.31% | 7.52% | 18.13% | 7.51% | 13.52% | 24 | 2 | 1.5 | 15.3 | NO | 24 | 2 | 68.5 | 210 | NO | 24 | 2 | 40.7 | 272.6 | NO
[11 empty] | 2022-04-14 | 63.1% | 14.92% | 17.24% | 4.74% | 0% | 24 | 0 | 1.3 | 14.1 | NO | 24 | 0 | 77.4 | 221 | NO | 24 | 0 | 50.5 | 289.9 | NO
[11 empty] | 2022-04-15 | 75.26% | 12.36% | 5.65% | 6.73% | 0% | 24 | 0 | 1.2 | 14.9 | NO | 24 | 0 | 72.5 | 237.4 | NO | 24 | 0 | 37.8 | 317.7 | NO
[11 empty] | 2022-04-16 | 71.78% | 13.21% | 8.87% | 6.14% | 0% | 24 | 0 | 1.2 | 14.6 | NO | 24 | 0 | 67.1 | 233.2 | NO | 24 | 0 | 51.7 | 309.3 | NO
[11 empty] | 2022-04-17 | 77.28% | 10.46% | 5.98% | 6.28% | 0% | 24 | 0 | 1.2 | 14.4 | NO | 24 | 0 | 68.3 | 232.4 | NO | 24 | 0 | 34.1 | 317 | NO
[11 empty] | 2022-04-18 | 75.65% | 10.27% | 6.09% | 7.99% | 0% | 24 | 0 | 1.3 | 14.7 | NO | 24 | 0 | 54.7 | 231.7 | NO | 24 | 0 | 41.7 | 316.7 | NO
[11 empty] | 2022-04-19 | 72.44% | 10.64% | 5.47% | 11.45% | 0% | 24 | 0 | 1.4 | 15.6 | NO | 24 | 0 | 75.2 | 233.5 | NO | 24 | 0 | 38.6 | 318 | NO
[11 empty] | 2022-04-20 | 73.86% | 10.84% | 4.46% | 10.84% | 0% | 24 | 0 | 1.3 | 15.5 | NO | 24 | 0 | 76.1 | 235.7 | NO | 24 | 0 | 36.5 | 320.1 | NO
[11 empty] | 2022-04-21 | 66.17% | 12.18% | 7.46% | 14.18% | 0% | 24 | 0 | 1.2 | 16.3 | NO | 24 | 0 | 68.1 | 233.6 | NO | 24 | 0 | 63.4 | 312.5 | NO
[11 empty] | 2022-04-22 | 84.23% | 8.75% | 3.12% | 3.9% | 0% | 24 | 0 | 1.2 | 13.6 | NO | 24 | 0 | 74 | 233.5 | NO | 24 | 0 | 38.7 | 323.1 | NO
[11 empty] | 2022-04-23 | 79.53% | 7.62% | 4.74% | 8.11% | 0% | 24 | 3 | 1.2 | 14.1 | NO | 24 | 3 | 54.7 | 228 | NO | 24 | 3 | 57.1 | 319.1 | NO
[11 empty] | 2022-04-24 | 80.38% | 9.78% | 2.42% | 7.42% | 0% | 24 | 21 | 1.2 | 14.7 | NO | 24 | 21 | 69.1 | 237.1 | NO | 24 | 21 | 34.4 | 324.7 | NO
[11 empty] | 2022-04-25 | 77.78% | 7.35% | 3.43% | 11.44% | 0% | 24 | 1 | 1.2 | 15 | NO | 24 | 1 | 56.7 | 230 | NO | 24 | 1 | 47.8 | 322.5 | NO
[11 empty] | 2022-04-26 | 74.04% | 9.18% | 4.65% | 12.13% | 0% | 24 | 0 | 1.3 | 15.4 | NO | 24 | 0 | 57.9 | 232.3 | NO | 24 | 0 | 45 | 319.4 | NO
[11 empty] | 2022-04-27 | 23.56% | 25.81% | 34.99% | 6.77% | 8.87% | 24 | 0 | 1.6 | 17 | NO | 24 | 0 | 63.5 | 217.1 | NO | 24 | 0 | 39.4 | 236.9 | NO
[11 empty] | 2022-04-28 | 80.84% | 9.08% | 2.45% | 7.6% | 0.02% | 24 | 0 | 1.4 | 14.5 | NO | 24 | 0 | 62.2 | 235.5 | NO | 24 | 0 | 33.4 | 324.6 | NO
[11 empty] | 2022-04-29 | 72% | 7.8% | 4% | 16.18% | 0.02% | 24 | 0 | 1.3 | 16.1 | NO | 24 | 0 | 58.2 | 230.2 | NO | 24 | 0 | 39 | 321.3 | NO
[11 empty] | 2022-04-30 | 73.15% | 10.86% | 2.58% | 13.39% | 0.02% | 24 | 2 | 1.4 | 16.2 | NO | 24 | 2 | 73 | 239.3 | NO | 24 | 2 | 42.6 | 324.3 | NO
[11 empty] | 2022-05-01 | 74.89% | 9.38% | 1.15% | 14.59% | 0% | 24 | 0 | 1.5 | 16.2 | NO | 24 | 0 | 71.8 | 238.5 | NO | 24 | 0 | 35.7 | 327.5 | NO
[11 empty] | 2022-05-02 | 69.66% | 13.14% | 6.86% | 10.34% | 0% | 24 | 0 | 1.4 | 15.6 | NO | 24 | 0 | 67.2 | 235.8 | NO | 24 | 0 | 72.9 | 313.1 | NO
[11 empty] | 2022-05-03 | 60.76% | 9.88% | 17.51% | 11.85% | 0% | 24 | 8 | 1.4 | 14.9 | NO | 24 | 8 | 69.3 | 210.5 | NO | 24 | 8 | 34.3 | 291.9 | NO
[11 empty] | 2022-05-04 | 52.3% | 5.39% | 33.28% | 9.02% | 0% | 24 | 10 | 1.4 | 12.3 | NO | 24 | 10 | 37.8 | 170.4 | NO | 24 | 10 | 42.6 | 256.3 | NO
[11 empty] | 2022-05-05 | 64.46% | 0.66% | 26.08% | 8.8% | 0% | 24 | 0 | 1.4 | 11.8 | NO | 24 | 0 | 32.2 | 175 | NO | 24 | 0 | 34.7 | 273.6 | NO
[11 empty] | 2022-05-06 | 72.54% | 2.5% | 18.16% | 6.81% | 0% | 24 | 4 | 1.3 | 11.8 | NO | 24 | 4 | 63.7 | 190.7 | NO | 24 | 4 | 35.3 | 288.1 | NO
[11 empty] | 2022-05-07 | 77.41% | 1.48% | 9.84% | 11.27% | 0% | 24 | 0 | 1.2 | 13.3 | NO | 24 | 0 | 65.4 | 205.3 | NO | 24 | 0 | 33.5 | 308.3 | NO
[11 empty] | 2022-05-08 | 79.01% | 2.72% | 9.9% | 8.36% | 0% | 24 | 0 | 1.1 | 12.9 | NO | 24 | 0 | 62 | 207.9 | NO | 24 | 0 | 33.8 | 308.1 | NO
[11 empty] | 2022-05-09 | 75.37% | 1.4% | 16.82% | 6.42% | 0% | 24 | 0 | 1.1 | 11.7 | NO | 24 | 0 | 42.4 | 191.8 | NO | 24 | 0 | 46 | 292.2 | NO
[11 empty] | 2022-05-10 | 53.73% | 0.53% | 34.49% | 11.25% | 0% | 24 | 6 | 1.2 | 11.5 | NO | 24 | 6 | 34.6 | 157.6 | NO | 24 | 6 | 38.2 | 252.9 | NO
[11 empty] | 2022-05-11 | 61.94% | 2.68% | 28.04% | 7.34% | 0% | 24 | 2 | 1.4 | 11.5 | NO | 24 | 2 | 43.3 | 173.3 | NO | 24 | 2 | 40.4 | 266.7 | NO
[11 empty] | 2022-05-12 | 81.94% | 11.36% | 3.16% | 3.54% | 0% | 24 | 0 | 1.5 | 14.1 | NO | 24 | 0 | 62 | 239.5 | NO | 24 | 0 | 36.8 | 323.2 | NO
[11 empty] | 2022-05-13 | 77.45% | 11.17% | 3.36% | 8.02% | 0% | 24 | 0 | 1.2 | 15.1 | NO | 24 | 0 | 58.9 | 238.4 | NO | 24 | 0 | 33.7 | 322.8 | NO
[11 empty] | 2022-05-14 | 76.56% | 11.76% | 11.55% | 0.12% | 0% | 24 | 0 | 1.1 | 13 | NO | 24 | 0 | 66.3 | 225.1 | NO | 24 | 0 | 58.3 | 304.7 | NO
[11 empty] | 2022-05-15 | 68.51% | 8.15% | 21.87% | 1.48% | 0% | 24 | 0 | 1.1 | 11.9 | NO | 24 | 0 | 43.6 | 198.2 | NO | 24 | 0 | 91.8 | 281.9 | NO
[11 empty] | 2022-05-16 | 70.02% | 10.65% | 4.12% | 15.21% | 0% | 24 | 0 | 1.1 | 16.5 | NO | 24 | 0 | 57.8 | 236.1 | NO | 24 | 0 | 57.2 | 321.2 | NO
[11 empty] | 2022-05-17 | 72.83% | 16.51% | 0.82% | 9.84% | 0% | 24 | 0 | 1.3 | 16.8 | NO | 24 | 0 | 66.3 | 254.3 | NO | 24 | 0 | 41.7 | 328.2 | NO
[11 empty] | 2022-05-18 | 75.88% | 11.06% | 0.71% | 12.36% | 0% | 24 | 0 | 1.1 | 16.1 | NO | 24 | 0 | 67.8 | 242.9 | NO | 24 | 0 | 35.4 | 328.4 | NO
[11 empty] | 2022-05-19 | 73.97% | 9.58% | 3.81% | 12.65% | 0% | 24 | 0 | 1.2 | 15.8 | NO | 24 | 0 | 67.5 | 235.3 | NO | 24 | 0 | 41.7 | 322.6 | NO
[11 empty] | 2022-05-20 | 56.45% | 13.1% | 8.98% | 12.68% | 8.8% | 24 | 6 | 1.2 | 17.3 | NO | 24 | 6 | 78.1 | 237.5 | NO | 24 | 6 | 33.9 | 297.4 | NO
[11 empty] | 2022-05-21 | 61.6% | 18.36% | 3.25% | 14.57% | 2.22% | 24 | 2 | 1.5 | 18.2 | NO | 24 | 2 | 87.9 | 255.8 | NO | 24 | 2 | 35.5 | 318.5 | NO
[11 empty] | 2022-05-22 | 74.85% | 16.81% | 1.37% | 6.97% | 0% | 24 | 0 | 1.2 | 16.2 | NO | 24 | 0 | 92.3 | 254.5 | NO | 24 | 0 | 35.8 | 327 | NO
[11 empty] | 2022-05-23 | 68.07% | 5.25% | 12.84% | 11.4% | 2.43% | 24 | 1 | 1.3 | 14.2 | NO | 24 | 1 | 48.3 | 208.8 | NO | 24 | 1 | 56.5 | 298.1 | NO
[11 empty] | 2022-05-24 | 68.23% | 4.59% | 15.03% | 6.14% | 6% | 24 | 0 | 1.3 | 13.4 | NO | 24 | 0 | 55.8 | 205.6 | NO | 24 | 0 | 44.4 | 289.7 | NO
[11 empty] | 2022-05-25 | 60.69% | 12.79% | 7.51% | 12.8% | 6.2% | 24 | 4 | 1.2 | 17.2 | NO | 24 | 4 | 50.7 | 237.8 | NO | 24 | 4 | 59.8 | 306.6 | NO
[11 empty] | 2022-05-26 | 73.58% | 9.44% | 1.2% | 10.42% | 5.37% | 24 | 0 | 1.2 | 16.2 | NO | 24 | 0 | 71.7 | 241.5 | NO | 24 | 0 | 48.7 | 321.4 | NO
[11 empty] | 2022-05-27 | 65.88% | 14.69% | 3.29% | 10.93% | 5.22% | 24 | 3 | 1.3 | 17.3 | NO | 24 | 3 | 75.5 | 249.2 | NO | 24 | 3 | 59.6 | 316.9 | NO
[11 empty] | 2022-05-28 | 68.1% | 10.76% | 0.99% | 15.06% | 5.08% | 24 | 0 | 1.2 | 17.5 | NO | 24 | 0 | 71.8 | 244.7 | NO | 24 | 0 | 49 | 322.2 | NO
[11 empty] | 2022-05-29 | 69.26% | 9.66% | 0.97% | 15.04% | 5.08% | 24 | 0 | 1.2 | 17.2 | NO | 24 | 0 | 69.8 | 242.3 | NO | 24 | 0 | 52.8 | 322.3 | NO
[11 empty] | 2022-05-30 | 70.36% | 8.75% | 3.55% | 11.84% | 5.5% | 24 | 1 | 1.5 | 16.2 | NO | 24 | 1 | 64.7 | 236.1 | NO | 24 | 1 | 62.6 | 316.1 | NO
[11 empty] | 2022-05-31 | 68.6% | 12.93% | 3.82% | 9.15% | 5.5% | 24 | 1 | 1.5 | 16.5 | NO | 24 | 1 | 76.4 | 244.4 | NO | 24 | 1 | 57.9 | 315.1 | NO
[11 empty] | 2022-06-01 | 56.9% | 16.1% | 14.43% | 12.57% | 0% | 24 | 9 | 1.4 | 16.4 | NO | 24 | 9 | 74.2 | 229.9 | NO | 24 | 9 | 94.6 | 297.5 | NO
[11 empty] | 2022-06-02 | 68.74% | 11.48% | 4.23% | 15.56% | 0% | 24 | 0 | 1.2 | 16.7 | NO | 24 | 0 | 68.3 | 237.2 | NO | 24 | 0 | 49.9 | 320.4 | NO
[11 empty] | 2022-06-03 | 71.33% | 11.47% | 0.72% | 16.48% | 0% | 24 | 0 | 1.2 | 17.1 | NO | 24 | 0 | 65.4 | 243.8 | NO | 24 | 0 | 54.9 | 328.4 | NO
[11 empty] | 2022-06-04 | 72.57% | 17.23% | 2.25% | 7.95% | 0% | 24 | 0 | 1.2 | 16.4 | NO | 24 | 0 | 88.5 | 253.8 | NO | 24 | 0 | 67.2 | 325.1 | NO
[11 empty] | 2022-06-05 | 70.87% | 15.57% | 3.85% | 9.71% | 0% | 24 | 0 | 1.3 | 16.3 | NO | 24 | 0 | 90.5 | 248.4 | NO | 24 | 0 | 88.7 | 321.4 | NO
[11 empty] | 2022-06-06 | 78.07% | 12.96% | 1.57% | 7.4% | 0% | 24 | 0 | 1.2 | 15.4 | NO | 24 | 0 | 85.3 | 245.7 | NO | 24 | 0 | 51.3 | 326.6 | NO
[11 empty] | 2022-06-07 | 85.42% | 10.32% | 0.75% | 3.51% | 0% | 24 | 0 | 0.9 | 14 | NO | 24 | 0 | 75.6 | 241.3 | NO | 24 | 0 | 57.4 | 328.4 | NO
[11 empty] | 2022-06-08 | 81.81% | 9.17% | 0.29% | 8.73% | 0% | 24 | 0 | 1.1 | 14.9 | NO | 23 | 0 | 70.8 | 239.5 | NO | 24 | 0 | 59.1 | 329.4 | NO
[11 empty] | 2022-06-09 | 73.25% | 6.62% | 0.43% | 19.71% | 0% | 24 | 0 | 1.1 | 16.8 | NO | 23 | 0 | 68.7 | 233.8 | NO | 24 | 0 | 53.9 | 329.1 | NO
[11 empty] | 2022-06-10 | 74.14% | 7.99% | 0.36% | 17.5% | 0% | 24 | 0 | 1.1 | 16.6 | NO | 24 | 0 | 77.3 | 236.9 | NO | 24 | 0 | 47.6 | 329.2 | NO
[11 empty] | 2022-06-11 | 76.48% | 8.18% | 0.48% | 14.86% | 0% | 24 | 0 | 1.1 | 16 | NO | 24 | 0 | 70.1 | 237.1 | NO | 24 | 0 | 49.3 | 329 | NO
[11 empty] | 2022-06-12 | 73.88% | 7.49% | 0.4% | 18.23% | 0% | 24 | 0 | 1.2 | 16.6 | NO | 24 | 0 | 63.4 | 235.7 | NO | 24 | 0 | 48.9 | 329.1 | NO
[11 empty] | 2022-06-13 | 75.33% | 7.98% | 0.79% | 15.9% | 0% | 24 | 0 | 1.1 | 16.2 | NO | 24 | 0 | 67.8 | 236.1 | NO | 24 | 0 | 48.9 | 328.3 | NO
[11 empty] | 2022-06-14 | 69.07% | 7.11% | 0.86% | 22.96% | 0% | 24 | 0 | 1.3 | 17.6 | NO | 24 | 0 | 61.9 | 234.3 | NO | 24 | 0 | 52.7 | 328.1 | NO
[11 empty] | 2022-06-15 | 76% | 11.13% | 1.23% | 11.63% | 0% | 24 | 0 | 1.3 | 15.9 | NO | 24 | 0 | 79.1 | 242.3 | NO | 24 | 0 | 65.9 | 327.3 | NO
[11 empty] | 2022-06-16 | 49.31% | 18.41% | 17.25% | 15.02% | 0% | 24 | 15 | 1.4 | 17.1 | NO | 24 | 15 | 73.9 | 228.5 | NO | 24 | 15 | 91.7 | 289.8 | NO
[11 empty] | 2022-06-17 | 81.83% | 13.44% | 1.74% | 2.99% | 0% | 24 | 0 | 1.1 | 14.5 | NO | 24 | 0 | 88.7 | 246.3 | NO | 24 | 0 | 37.7 | 326.2 | NO
[11 empty] | 2022-06-18 | 77.85% | 11.74% | 0.81% | 9.6% | 0% | 24 | 0 | 1.3 | 15.7 | NO | 24 | 0 | 70.4 | 244.4 | NO | 24 | 0 | 49 | 328.2 | NO
[11 empty] | 2022-06-19 | 76.54% | 10.59% | 0.92% | 11.94% | 0% | 24 | 0 | 1.3 | 15.9 | NO | 24 | 0 | 77.9 | 241.7 | NO | 24 | 0 | 39.3 | 328 | NO
[11 empty] | 2022-06-20 | 77.2% | 13.47% | 0.62% | 8.66% | 0.04% | 24 | 0 | 1.3 | 15.8 | NO | 24 | 0 | 82.7 | 248.5 | NO | 24 | 0 | 36.6 | 328.6 | NO
[11 empty] | 2022-06-21 | 77.61% | 12.25% | 0.59% | 9.55% | 0% | 24 | 0 | 1.3 | 15.8 | NO | 24 | 0 | 73.2 | 245.8 | NO | 24 | 0 | 42.4 | 328.7 | NO
[11 empty] | 2022-06-22 | 70.56% | 8.32% | 1.33% | 19.78% | 0% | 24 | 0 | 1.2 | 17.1 | NO | 24 | 0 | 78.9 | 235.9 | NO | 24 | 0 | 37.6 | 327.1 | NO
[11 empty] | 2022-06-23 | 70.34% | 8.38% | 1.14% | 20.14% | 0% | 24 | 0 | 1.3 | 17.2 | NO | 24 | 0 | 78.2 | 236.4 | NO | 24 | 0 | 41.9 | 327.5 | NO
[11 empty] | 2022-06-24 | 65.41% | 10.43% | 1.29% | 22.86% | 0% | 24 | 3 | 1.7 | 18.3 | NO | 24 | 3 | 77.5 | 244.1 | NO | 24 | 3 | 46.5 | 327.1 | NO
[11 empty] | 2022-06-25 | 73.33% | 7.98% | 3.1% | 15.6% | 0% | 24 | 0 | 1.2 | 16 | NO | 24 | 0 | 75.5 | 232 | NO | 24 | 0 | 50.9 | 323.3 | NO
[11 empty] | 2022-06-26 | 63.98% | 13.52% | 1.35% | 21.15% | 0% | 24 | 6 | 1.4 | 18.5 | NO | 24 | 6 | 75 | 248.5 | NO | 24 | 6 | 55.9 | 327 | NO
[11 empty] | 2022-06-27 | 62.77% | 22.97% | 7.55% | 6.72% | 0% | 24 | 0 | 1.3 | 17.1 | NO | 24 | 0 | 75.8 | 257.2 | NO | 24 | 0 | 61.8 | 313.3 | NO
[11 empty] | 2022-06-28 | 60.75% | 28.18% | 7.14% | 3.93% | 0% | 24 | 8 | 1.7 | 17.9 | NO | 24 | 8 | 80 | 277.6 | NO | 24 | 8 | 72.5 | 316.1 | NO
[11 empty] | 2022-06-29 | 48.52% | 21.36% | 23.88% | 6.24% | 0% | 24 | 12 | 1.6 | 15.6 | NO | 24 | 12 | 68.5 | 222.9 | NO | 24 | 12 | 95.2 | 276.2 | NO
[11 empty] | 2022-06-30 | 46.54% | 20.37% | 24.16% | 8.92% | 0% | 24 | 14 | 1.3 | 16.1 | NO | 24 | 0 | 75.8 | 221.5 | NO | 24 | 0 | 92.6 | 277.1 | NO
[11 empty] | 0 | 75.93% | 8.223% | 14.04% | 1.808% | 0% | 24 | 0 | 1.2809 | 15.7975 | NO | 24 | 0 | 52.0813 | 234.7945 | NO | 24 | 0 | 64.742 | 326.0243 | NO
[11 empty] | 0 | 78.2% | 7.786% | 12.58% | 1.435% | 0% | 24 | 0 | 1.1695 | 15.3783 | NO | 24 | 0 | 37.1714 | 235.3297 | NO | 24 | 0 | 98.2477 | 326.6528 | NO

## A52B Boiler 7
|  | Concentrations in mg/m³ at reference conditions after subtracting uncertainty | [9 empty] | Daily means, excluding hours outside normal operating conditions
|  | 2022-04-01 |  |  | 2022-05-01 |  |  | 2022-06-01 |  |  | Date | Fuel mix |  |  |  |  | Particulate Matter concentration (mg/m³) after subtracting uncertainty |  |  |  |  | Sulphur dioxide concentration (mg/m³) after subtracting uncertainty |  |  |  |  | Oxides of nitrogen concentration (mg/m³) after subtracting uncertainty
|  | PM | SO2 | NOx | PM | SO2 | NOx | PM | SO2 | NOx |  | % BFG | % COG | % BOSg | % NG | % HFO | No.valid hours | No.hours OTNOC | Measured | Limit | Breach? | No.valid hours | No.hours OTNOC | Measured | Limit | Breach? | No.valid hours | No.hours OTNOC | Measured | Limit | Breach?
Daily means | Minimum | 1.3 | 14.9 | 104.1 | 1.2 | 6.2 | 23.1 | 1.2 | 11 | 20.5 | 2022-04-01 | 78.92% | 9.59% | 3% | 8.49% | 0% | 24 | 0 | 2 | 15.5 | NO | 24 | 0 | 24.8 | 240.5 | NO | 24 | 0 | 109.7 | 330.5 | NO
| Maximum | 2.6 | 30.8 | 157.5 | 1.9 | 39.7 | 184.1 | 2.4 | 23.3 | 57.6 | 2022-04-02 | 86.46% | 9.06% | 3.48% | 1% | 0% | 24 | 0 | 2.1 | 13.5 | NO | 24 | 0 | 21.1 | 236.7 | NO | 24 | 0 | 123.2 | 327 | NO
| No. > Limit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2022-04-03 | 79.8% | 8.43% | 2.32% | 9.45% | 0% | 24 | 0 | 2 | 15.5 | NO | 24 | 0 | 21.6 | 239.1 | NO | 24 | 0 | 118.1 | 332 | NO
Monthly mean |  | 1.6 | 22 | 126.3 | 1.5 | 16.5 | 117.9 | 1.6 | 15.8 | 33.6 | 2022-04-04 | 78.08% | 6.6% | 7.76% | 7.56% | 0% | 24 | 0 | 1.5 | 14.4 | NO | 24 | 0 | 21.6 | 225.1 | NO | 24 | 0 | 117.7 | 319.8 | NO
Monthly mean limit |  | 13.8 | 216.2 | 296.2 | 14.2 | 215.4 | 291.6 | 15.2 | 223.6 | 299 | 2022-04-05 | 80.64% | 3.46% | 10.06% | 5.84% | 0% | 24 | 0 | 1.5 | 13.1 | NO | 24 | 0 | 22.5 | 213.3 | NO | 24 | 0 | 120.8 | 313.8 | NO
[11 empty] | 2022-04-06 | 77.34% | 4.67% | 8.84% | 9.15% | 0% | 24 | 0 | 1.5 | 14.2 | NO | 24 | 0 | 17.9 | 218.4 | NO | 24 | 0 | 109.8 | 316.9 | NO
[11 empty] | 2022-04-07 | 74.9% | 8.75% | 9.3% | 7.05% | 0% | 24 | 0 | 1.8 | 14.6 | NO | 24 | 0 | 15.7 | 226.6 | NO | 24 | 0 | 108.2 | 315.8 | NO
[11 empty] | 2022-04-08 | 53.29% | 16.03% | 16.79% | 6.21% | 7.7% | 24 | 10 | 2.6 | 16.2 | NO | 24 | 10 | 29 | 231.4 | NO | 24 | 10 | 104.1 | 284.2 | NO
[11 empty] | 2022-04-09 | 82.4% | 9.49% | 4.02% | 4.09% | 0% | 24 | 0 | 2 | 14.4 | NO | 24 | 0 | 24.3 | 237.5 | NO | 24 | 0 | 118.1 | 327 | NO
[11 empty] | 2022-04-10 | 82.33% | 11.09% | 2.58% | 4% | 0% | 24 | 0 | 1.8 | 14.7 | NO | 24 | 0 | 26.2 | 243.5 | NO | 24 | 0 | 124.8 | 330 | NO
[11 empty] | 2022-04-11 | 79.98% | 8.42% | 0.59% | 11.01% | 0% | 24 | 0 | 1.6 | 16 | NO | 24 | 0 | 21.5 | 242.4 | NO | 24 | 0 | 121.8 | 336.2 | NO
[11 empty] | 2022-04-12 | 83.22% | 8.3% | 1.09% | 7.39% | 0% | 24 | 0 | 1.6 | 15.1 | NO | 24 | 0 | 23.6 | 240.9 | NO | 24 | 0 | 121.3 | 334.5 | NO
[11 empty] | 2022-04-13 | 66.41% | 10.58% | 9.14% | 5.37% | 8.49% | 24 | 6 | 2.2 | 15.9 | NO | 24 | 6 | 27 | 235.4 | NO | 24 | 6 | 131.9 | 305 | NO
[11 empty] | 2022-04-14 | 64.71% | 16% | 14.77% | 4.52% | 0% | 24 | 4 | 1.7 | 14.6 | NO | 24 | 4 | 30.2 | 229.6 | NO | 24 | 4 | 148.7 | 297.8 | NO
[11 empty] | 2022-04-15 | 79.53% | 12.99% | 2.33% | 5.15% | 0% | 24 | 0 | 1.5 | 15.6 | NO | 24 | 0 | 23.6 | 249.5 | NO | 24 | 0 | 138.9 | 331.7 | NO
[11 empty] | 2022-04-16 | 72.49% | 16.11% | 6.64% | 4.77% | 0% | 24 | 4 | 1.4 | 15.5 | NO | 24 | 4 | 24.8 | 247.4 | NO | 24 | 4 | 157.5 | 318.9 | NO
[11 empty] | 2022-04-17 | 81.03% | 10.02% | 4.25% | 4.7% | 0% | 24 | 0 | 1.4 | 14.6 | NO | 24 | 0 | 14.9 | 238.5 | NO | 24 | 0 | 135 | 326.8 | NO
[11 empty] | 2022-04-18 | 80.47% | 9.98% | 3.09% | 6.47% | 0% | 24 | 0 | 1.5 | 15.1 | NO | 24 | 0 | 21.7 | 240.9 | NO | 24 | 0 | 130.4 | 329.9 | NO
[11 empty] | 2022-04-19 | 75.52% | 10.38% | 4.43% | 9.67% | 0% | 24 | 0 | 1.6 | 15.8 | NO | 24 | 0 | 23.5 | 239.4 | NO | 24 | 0 | 127.3 | 327.1 | NO
[11 empty] | 2022-04-20 | 78.92% | 9.71% | 2.12% | 9.25% | 0% | 24 | 0 | 1.4 | 15.8 | NO | 24 | 0 | 22.6 | 242.3 | NO | 24 | 0 | 136 | 332.4 | NO
[11 empty] | 2022-04-21 | 67.07% | 14.65% | 6.62% | 11.66% | 0% | 24 | 3 | 1.3 | 17 | NO | 24 | 3 | 23.6 | 244.3 | NO | 24 | 3 | 145.5 | 321.3 | NO
[11 empty] | 2022-04-22 | 88.72% | 7.43% | 1.37% | 2.48% | 0% | 24 | 0 | 1.4 | 13.6 | NO | 24 | 0 | 19.4 | 237.4 | NO | 24 | 0 | 120.2 | 332.4 | NO
[11 empty] | 2022-04-23 | 82.08% | 9.09% | 2.42% | 6.4% | 0% | 24 | 0 | 1.4 | 14.9 | NO | 24 | 0 | 20.9 | 240 | NO | 24 | 0 | 115.6 | 330.7 | NO
[11 empty] | 2022-04-24 | 84.3% | 8.75% | 1.24% | 5.71% | 0% | 24 | 0 | 1.4 | 14.8 | NO | 24 | 0 | 15.9 | 241.3 | NO | 24 | 0 | 123 | 333.8 | NO
[11 empty] | 2022-04-25 | 82.3% | 7.33% | 0.69% | 9.68% | 0% | 24 | 0 | 1.5 | 15.5 | NO | 24 | 0 | 16.1 | 239.9 | NO | 24 | 0 | 134.2 | 336 | NO
[11 empty] | 2022-04-26 | 78.59% | 9.96% | 1.18% | 10.26% | 0% | 24 | 0 | 1.5 | 16.1 | NO | 24 | 0 | 21.2 | 245.5 | NO | 24 | 0 | 146.5 | 334.8 | NO
[11 empty] | 2022-04-27 | 87.41% | 9.27% | 2.11% | 1.21% | 0% | 24 | 0 | 1.5 | 14.6 | NO | 24 | 0 | 30.8 | 246.2 | NO | 24 | 0 | 133.9 | 339.7 | NO
[11 empty] | 2022-04-28 | 83.33% | 9.12% | 1.62% | 5.93% | 0% | 24 | 0 | 1.6 | 14.8 | NO | 24 | 0 | 26.9 | 241.1 | NO | 24 | 0 | 123.4 | 332.4 | NO
[11 empty] | 2022-04-29 | 75.81% | 6.42% | 3.67% | 14.09% | 0% | 24 | 0 | 1.7 | 16.2 | NO | 24 | 0 | 19.2 | 233.4 | NO | 24 | 0 | 119.6 | 330.5 | NO
[11 empty] | 2022-04-30 | 78.67% | 8.86% | 0.85% | 11.62% | 0% | 24 | 0 | 1.6 | 16.3 | NO | 24 | 0 | 20.9 | 243.6 | NO | 24 | 0 | 129.5 | 336.5 | NO
[11 empty] | 2022-05-01 | 78.34% | 8.37% | 1.23% | 12.06% | 0% | 24 | 0 | 1.7 | 16.4 | NO | 24 | 0 | 15.7 | 242.5 | NO | 24 | 0 | 122.7 | 336.7 | NO
[11 empty] | 2022-05-02 | 71.11% | 12.44% | 7.16% | 9.29% | 0% | 24 | 0 | 1.7 | 15.7 | NO | 24 | 0 | 12.4 | 237.8 | NO | 24 | 0 | 163.4 | 317.8 | NO
[11 empty] | 2022-05-03 | 65.26% | 11.49% | 12.86% | 10.39% | 0% | 24 | 1 | 1.5 | 15.9 | NO | 24 | 1 | 20.4 | 227.7 | NO | 24 | 1 | 157.1 | 309.7 | NO
[11 empty] | 2022-05-04 | 50.63% | 13.33% | 28.81% | 7.22% | 0% | 24 | 9 | 1.5 | 14.4 | NO | 24 | 9 | 19.7 | 200.2 | NO | 24 | 9 | 179.8 | 271.6 | NO
[11 empty] | 2022-05-05 | 60.19% | 24.46% | 8.67% | 6.68% | 0% | 24 | 5 | 1.6 | 18 | NO | 24 | 5 | 32.3 | 262.5 | NO | 24 | 5 | 176 | 316.9 | NO
[11 empty] | 2022-05-06 | 76.2% | 14.35% | 4.57% | 4.88% | 0% | 24 | 0 | 1.6 | 15.6 | NO | 24 | 0 | 25 | 248.6 | NO | 24 | 0 | 166.8 | 326.7 | NO
[11 empty] | 2022-05-07 | 79.16% | 8.83% | 3.29% | 8.72% | 0% | 24 | 0 | 1.4 | 15.5 | NO | 24 | 0 | 17.4 | 239.1 | NO | 24 | 0 | 151.3 | 331.2 | NO
[11 empty] | 2022-05-08 | 79.97% | 11.64% | 2.03% | 6.36% | 0% | 24 | 0 | 1.3 | 15.5 | NO | 24 | 0 | 17.1 | 246.2 | NO | 24 | 0 | 148.4 | 332.2 | NO
[11 empty] | 2022-05-09 | 77.96% | 10.09% | 7.7% | 4.26% | 0% | 24 | 0 | 1.4 | 14.3 | NO | 24 | 0 | 13 | 232.3 | NO | 24 | 0 | 148.3 | 319.1 | NO
[11 empty] | 2022-05-10 | 45.28% | 15.89% | 30.82% | 8.01% | 0% | 24 | 15 | 1.5 | 14.9 | NO | 24 | 15 | 21.7 | 201.4 | NO | 24 | 15 | 184.1 | 265.3 | NO
[11 empty] | 2022-05-11 | 66.37% | 13.55% | 14.53% | 5.55% | 0% | 24 | 4 | 1.9 | 15 | NO | 24 | 4 | 27.2 | 228.1 | NO | 24 | 4 | 164.4 | 304.2 | NO
[11 empty] | 2022-05-12 | 84.64% | 10.18% | 3.22% | 1.96% | 0% | 24 | 0 | 1.7 | 14.1 | NO | 24 | 0 | 15.7 | 240.3 | NO | 24 | 0 | 142 | 328.5 | NO
[11 empty] | 2022-05-13 | 78.98% | 8.22% | 6.72% | 6.08% | 0% | 24 | 0 | 1.4 | 14.5 | NO | 24 | 0 | 15.2 | 230.7 | NO | 23 | 0 | 135.5 | 322.2 | NO
[11 empty] | 2022-05-14 | 78.91% | 10.73% | 11.3% | -0.94% | 0% | 24 | 0 | 1.5 | 12.9 | NO | 24 | 0 | 10.8 | 225.4 | NO | 24 | 0 | 157.5 | 308.6 | NO
[11 empty] | 2022-05-15 | 75.55% | 16.45% | 7.71% | 0.28% | 0% | 24 | 0 | 1.6 | 14.7 | NO | 24 | 0 | 8.3 | 244.8 | NO | 24 | 0 | 166.8 | 317.1 | NO
[11 empty] | 2022-05-16 | 73.98% | 10.11% | 3.17% | 12.74% | 0% | 24 | 0 | 1.5 | 16.8 | NO | 24 | 0 | 7.5 | 243.1 | NO | 24 | 0 | 154.6 | 332.9 | NO
[11 empty] | 2022-05-17 | 81.57% | 8.8% | 1.24% | 8.38% | 0% | 24 | 0 | 1.2 | 15.6 | NO | 24 | 0 | 6.2 | 242.7 | NO | 24 | 0 | 136.9 | 335.8 | NO
[11 empty] | 2022-05-18 | 79.46% | 9.61% | 0.73% | 10.2% | 0% | 24 | 0 | 1.3 | 16.2 | NO | 24 | 0 | 12.9 | 245.7 | NO | 24 | 0 | 137.7 | 337.2 | NO
[11 empty] | 2022-05-19 | 76.84% | 10.83% | 2.07% | 10.25% | 0% | 24 | 0 | 1.3 | 16.5 | NO | 24 | 0 | 15.9 | 246.4 | NO | 24 | 0 | 141.4 | 334.9 | NO
[11 empty] | 2022-05-20 | 57.58% | 12.69% | 9.01% | 10.53% | 10.19% | 24 | 6 | 1.5 | 17.7 | NO | 24 | 6 | 20.1 | 241.7 | NO | 24 | 6 | 141.9 | 302.7 | NO
[11 empty] | 2022-05-21 | 63.58% | 18.57% | 3.49% | 11.42% | 2.94% | 24 | 2 | 1.7 | 18.5 | NO | 24 | 2 | 39.7 | 260 | NO | 24 | 2 | 136.7 | 324.9 | NO
[11 empty] | 2022-05-22 | 78.65% | 14.63% | 1.3% | 5.41% | 0% | 24 | 0 | 1.4 | 15.9 | NO | 24 | 0 | 22.2 | 254 | NO | 24 | 0 | 150.1 | 333.2 | NO
[11 empty] | 2022-05-23 | 75.29% | 4.97% | 9.3% | 10.01% | 0.42% | 24 | 0 | 1.9 | 14.4 | NO | 24 | 0 | 11.2 | 217.8 | NO | 24 | 0 | 135.2 | 315.2 | NO
[11 empty] | 2022-05-24 | 76.47% | 4.36% | 13.28% | 5.89% | 0% | 24 | 0 | 1.5 | 12.7 | NO | 24 | 0 | 12.6 | 206.6 | NO | 24 | 0 | 61.8 | 303.5 | NO
[11 empty] | 2022-05-25 | 69.76% | 9.65% | 8.49% | 12.1% | 0% | 24 | 0 | 1.5 | 16.1 | NO | 24 | 0 | 10.7 | 231.1 | NO | 24 | 0 | 30.4 | 319.2 | NO
[11 empty] | 2022-05-26 | 81.02% | 8.74% | 1.32% | 8.91% | 0% | 24 | 0 | 1.4 | 15.6 | NO | 24 | 0 | 17.5 | 241.8 | NO | 24 | 0 | 24.4 | 334.7 | NO
[11 empty] | 2022-05-27 | 74.69% | 11.7% | 3.73% | 9.88% | 0% | 24 | 3 | 1.5 | 16.2 | NO | 24 | 3 | 18 | 243.6 | NO | 24 | 3 | 31.1 | 328.7 | NO
[11 empty] | 2022-05-28 | 76.57% | 8.41% | 1.14% | 13.88% | 0% | 24 | 0 | 1.5 | 16.7 | NO | 24 | 0 | 14.8 | 242.3 | NO | 24 | 0 | 24.9 | 336.4 | NO
[11 empty] | 2022-05-29 | 77.89% | 7.06% | 1.13% | 13.92% | 0% | 24 | 0 | 1.5 | 16.4 | NO | 24 | 0 | 13.4 | 239.4 | NO | 24 | 0 | 23.1 | 336.4 | NO
[11 empty] | 2022-05-30 | 77.8% | 8.31% | 3.53% | 10.36% | 0% | 24 | 1 | 1.5 | 15.7 | NO | 24 | 1 | 11 | 237.7 | NO | 24 | 1 | 20.6 | 330.4 | NO
[11 empty] | 2022-05-31 | 78.19% | 11.11% | 2.83% | 7.87% | 0% | 24 | 0 | 1.6 | 15.8 | NO | 24 | 0 | 17.1 | 244.7 | NO | 24 | 0 | 29.2 | 331.3 | NO
[11 empty] | 2022-06-01 | 61.29% | 15.21% | 13.1% | 10.4% | 0% | 24 | 9 | 2.3 | 16.9 | NO | 24 | 9 | 23.3 | 237.8 | NO | 24 | 9 | 31.4 | 310.7 | NO
[11 empty] | 2022-06-02 | 71.94% | 11.28% | 4.4% | 12.38% | 0% | 24 | 0 | 1.3 | 17.1 | NO | 24 | 0 | 15.3 | 244.1 | NO | 24 | 0 | 28.6 | 331.3 | NO
[11 empty] | 2022-06-03 | 75.9% | 9.43% | 0.81% | 13.86% | 0% | 24 | 0 | 1.3 | 17.1 | NO | 24 | 0 | 14.9 | 246.2 | NO | 24 | 0 | 35.7 | 338.6 | NO
[11 empty] | 2022-06-04 | 78.11% | 13.55% | 2.32% | 6.03% | 0% | 24 | 0 | 1.3 | 16 | NO | 24 | 0 | 21.1 | 251.1 | NO | 24 | 0 | 37.1 | 333.1 | NO
[11 empty] | 2022-06-05 | 75.07% | 13.75% | 3.61% | 7.57% | 0% | 24 | 0 | 1.9 | 16.3 | NO | 24 | 0 | 18.2 | 250.7 | NO | 24 | 0 | 37.1 | 330.4 | NO
[11 empty] | 2022-06-06 | 82.17% | 11.44% | 0.8% | 5.59% | 0% | 24 | 0 | 1.3 | 15.4 | NO | 24 | 0 | 23.2 | 248 | NO | 24 | 0 | 28.8 | 334.7 | NO
[11 empty] | 2022-06-07 | 87.56% | 9.68% | 0.77% | 1.98% | 0% | 24 | 0 | 1.2 | 14.1 | NO | 24 | 0 | 16.2 | 243.4 | NO | 24 | 0 | 31.9 | 333.6 | NO
[11 empty] | 2022-06-08 | 84.29% | 8.79% | 0.29% | 6.62% | 0% | 24 | 0 | 1.3 | 15.1 | NO | 24 | 0 | 14.1 | 243.6 | NO | 24 | 0 | 32.4 | 336.7 | NO
[11 empty] | 2022-06-09 | 76.31% | 7.35% | 0.43% | 15.91% | 0% | 24 | 0 | 1.5 | 17.4 | NO | 24 | 0 | 11.7 | 243.9 | NO | 24 | 0 | 27.7 | 341.9 | NO
[11 empty] | 2022-06-10 | 76.79% | 8.48% | 0.39% | 14.34% | 0% | 24 | 0 | 1.4 | 17.1 | NO | 24 | 0 | 15.1 | 245.1 | NO | 24 | 0 | 27.5 | 339.9 | NO
[11 empty] | 2022-06-11 | 79.36% | 8.1% | 0.52% | 12.02% | 0% | 24 | 0 | 1.4 | 16.4 | NO | 24 | 0 | 15.7 | 243.6 | NO | 24 | 0 | 24 | 338.9 | NO
[11 empty] | 2022-06-12 | 77.25% | 7.42% | 0.42% | 14.91% | 0% | 24 | 0 | 1.4 | 17.1 | NO | 24 | 0 | 12.7 | 243.4 | NO | 24 | 0 | 23.3 | 340.8 | NO
[11 empty] | 2022-06-13 | 78.23% | 8.27% | 0.81% | 12.69% | 0% | 24 | 0 | 1.3 | 16.7 | NO | 24 | 0 | 15 | 244.1 | NO | 24 | 0 | 23.8 | 339.2 | NO
[11 empty] | 2022-06-14 | 71.9% | 8.21% | 0.89% | 18.99% | 0% | 24 | 0 | 1.8 | 18.2 | NO | 24 | 0 | 14.5 | 245.4 | NO | 24 | 0 | 24 | 341.1 | NO
[11 empty] | 2022-06-15 | 77.93% | 11.95% | 1.23% | 8.89% | 0% | 24 | 0 | 1.4 | 16.4 | NO | 24 | 0 | 19.7 | 250.2 | NO | 24 | 0 | 41.4 | 336.4 | NO
[11 empty] | 2022-06-16 | 52.79% | 17.1% | 17.54% | 12.57% | 0% | 24 | 12 | 1.7 | 17.2 | NO | 24 | 12 | 20.8 | 230.6 | NO | 24 | 12 | 52.4 | 298.4 | NO
[11 empty] | 2022-06-17 | 81.74% | 15.01% | 1.97% | 1.28% | 0% | 24 | 0 | 1.2 | 15 | NO | 24 | 0 | 16 | 253.2 | NO | 24 | 0 | 32.3 | 331.3 | NO
[11 empty] | 2022-06-18 | 77.58% | 14.87% | 0.79% | 6.76% | 0% | 24 | 0 | 1.5 | 16.6 | NO | 24 | 0 | 16.3 | 257.1 | NO | 24 | 0 | 29.9 | 336.9 | NO
[11 empty] | 2022-06-19 | 76.27% | 14.02% | 0.91% | 8.81% | 0% | 24 | 0 | 1.4 | 16.9 | NO | 24 | 0 | 16.4 | 255.3 | NO | 24 | 0 | 27.3 | 337.3 | NO
[11 empty] | 2022-06-20 | 79.04% | 12.27% | 0.65% | 7.99% | 0.05% | 24 | 0 | 1.4 | 17.3 | NO | 24 | 0 | 14.6 | 258 | NO | 24 | 0 | 29.8 | 346.8 | NO
[11 empty] | 2022-06-21 | 80.66% | 10.82% | 0.6% | 7.92% | 0% | 24 | 0 | 1.3 | 16.3 | NO | 24 | 0 | 11 | 250.5 | NO | 24 | 0 | 28.4 | 340.4 | NO
[11 empty] | 2022-06-22 | 74.03% | 8.58% | 1.36% | 16.04% | 0% | 24 | 0 | 1.2 | 17.6 | NO | 24 | 0 | 12.4 | 245 | NO | 24 | 0 | 24.1 | 339.9 | NO
[11 empty] | 2022-06-23 | 73.29% | 9.22% | 1.15% | 16.34% | 0% | 24 | 0 | 1.5 | 17.8 | NO | 24 | 0 | 14.2 | 246.7 | NO | 24 | 0 | 20.5 | 340.2 | NO
[11 empty] | 2022-06-24 | 69.1% | 11.04% | 1.31% | 18.55% | 0% | 24 | 0 | 1.9 | 18.8 | NO | 24 | 0 | 12.7 | 253.7 | NO | 24 | 0 | 33.7 | 340.9 | NO
[11 empty] | 2022-06-25 | 76.31% | 8.43% | 3.1% | 12.16% | 0% | 24 | 0 | 1.5 | 16.5 | NO | 24 | 0 | 15 | 240.8 | NO | 24 | 0 | 25.4 | 335 | NO
[11 empty] | 2022-06-26 | 67.88% | 12.79% | 1.39% | 17.94% | 0% | 24 | 2 | 1.6 | 19 | NO | 24 | 2 | 15.3 | 256.7 | NO | 24 | 2 | 26.3 | 340.3 | NO
[11 empty] | 2022-06-27 | 67.22% | 20.09% | 7.95% | 4.74% | 0% | 24 | 0 | 1.7 | 16.8 | NO | 24 | 0 | 15.3 | 255.2 | NO | 24 | 0 | 46.1 | 319.9 | NO
[11 empty] | 2022-06-28 | 64.57% | 27.02% | 7.1% | 1.31% | 0% | 24 | 0 | 2.4 | 17.5 | NO | 24 | 0 | 14.4 | 275.5 | NO | 24 | 0 | 57.6 | 320.9 | NO
[11 empty] | 2022-06-29 | 48.1% | 18.54% | 29.03% | 4.33% | 0% | 24 | 17 | 1.8 | 14.9 | NO | 24 | 17 | 13.4 | 211 | NO | 24 | 17 | 55 | 270.7 | NO
[11 empty] | 2022-06-30 | 49.33% | 15.74% | 26.81% | 8.12% | 0% | 24 | 11 | 1.7 | 15.3 | NO | 24 | 11 | 11.3 | 209.2 | NO | 24 | 11 | 47.1 | 275.8 | NO
[11 empty] | 0 | 78.24% | 9.749% | 11.39% | 0.623% | 0% | 24 | 0 | 10.1572 | 15.7975 | NO | 24 | 0 | 23.5623 | 246.5504 | NO | 24 | 0 | 105.9315 | 338.0277 | NO
[11 empty] | 0 | 81.7% | 8.166% | 9.788% | 0.3446% | 0% | 24 | 0 | 9.5662 | 15.3783 | NO | 24 | 0 | 22.4609 | 243.8822 | NO | 24 | 0 | 102.4801 | 338.3518 | NO