## Notes
Reference conditions
All concentrations in this spreadsheet are reported in dry air at a temperature of 273K, at a pressure of 101.3 kPa and with an oxygen content of 3% dry
Uncertainty
Concentrations in this spreadsheet are reported after having subtracted the value of the 95% confidence interval (see Section 3.6.7 of the permit):
95% confidence interval for nitrogen oxides is taken to be 20%
95% confidence interval for sulphur dioxide is taken to be 20%
95% confidence interval for dust is taken to be 30%
95% confidence interval for carbon monoxide is taken to be 10%
Normal operating conditions
The document "Power Plant Boiler Abnormal Conditions" sets out the criteria for excluding emissions monitoring data from permitting or other reporting obligations:
| Parameter | Plant | Level representing abnormal conditions
| Boiler oxygen | All boilers | >17% oxygen
| Fuel input | A51, A52A, A52B, A53 and A62 | <50% BFG by thermal input
|  | A50 (Service Boilers) | <35% BFG by thermal input

## Summary
Dust concentrations in mg/m³ (except A55 as % obscuration), reported as measured (uncertainty not taken into account)
| Source | A1 | A2 | A8A | A8B | A9 | A10 | A10A | A14 | A15 | A16 | A55 | A63 | A1 | A1
| Description | Sinter plant main stack (particulate) | Sinter plant deduster stack | BF4 casthouse fume extraction North | BF4 casthouse fume extraction South | BF5 casthouse fume extraction | Iron desulphurisation/hot metal pouring fume extraction plant stack | Hot metal fume extraction no. 2 | Secondary fume extraction stack North | Secondary fume extraction stack Centre | Secondary fume extraction stack South | Morfa main stack | CASOB/ desulph fume extraction plant | Sinter plant main stack (SO2) | Sinter plant main stack (NOX)
Daily means | Minimum | 0 | 4.4551e-05 | 0.43827 | 0.313 | 0.42539 | 1.3146 | 0.9006 | 0.96084 | 2.3334 | 0.73153 |  | 0.081976 | 0 | 0
| Maximum | 76.5467 | 0.90713 | 3.2191 | 2.8576 | 2.352 | 10.4979 | 17.3212 | 14.3299 | 8.494 | 13.2159 |  | 7.0282 | 513.0447 | 184.8852
| Limit | 40 | 10 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 500 | 500
| No. > Limit | 47 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 1 | 0
Weekly mean | Minimum | [10 empty] | 19.43
| Maximum | [10 empty] | 42.19
| Limit | [10 empty] | 25
| No. > Limit | [10 empty] | 8

## Plots
NOTES

## Data
| Measured concentrations - daily means (mg/m³) | [12 empty] | Limits |  |  |  |  | Obscuration %
Source | A1 | A1 | A1 | A2 | A8A | A8B | A9 | A10 | A10A | A14 | A15 | A16 | A63 | A1 | A2 | BF and BOS plant sources | A1 | Source | A55
Description | Sinter plant main stack (Particulate) | Sinter plant main stack (SO2) | Sinter plant main stack (NOX) | Sinter plant deduster stack | BF4 casthouse fume extraction North | BF4 casthouse fume extraction South | BF5 casthouse fume extraction | Iron desulphurisation/hot metal pouring fume extraction plant stack | Hot metal fume extraction no. 2 | Secondary fume extraction stack North | Secondary fume extraction stack Centre | Secondary fume extraction stack South | CASOB/ desulph fume extraction plant | Sinter plant main stack | Sinter plant deduster stack |  | Sinter Plant Main Stack SO2 & NOX | Description | Morfa main stack
Date | [17 empty] | Week commencing | Measured | Limit
2022-01-01 | 40.8691 | 443.2413 | 142.7235 | 0.64091 | 1.5397 | 1.5425 | 1.4296 | 3.7797 | Fan out for inspection and repair as discussed with NRW - See submission: A10A Fume Extraction 004_28042022 | S5N_21_72A |  |  | S5N_21_48A | 40 | 10 | 15 | 500 | 2022-01-02 | 35.79 | 25 | S5N_22_01A
2022-01-02 | 45.6459 | 348.3409 | 147.5903 | 0.55181 | 1.1511 | 1.0535 | 1.3905 | 4.1503 | [5 empty] | 40 | 10 | 15 | 500 | 2022-01-09 | 42.19 | 25 | S5N_22_02A
2022-01-03 | 42.6101 | 311.3249 | 159.4528 | 0.53799 | 1.6795 | 1.5194 | 1.421 | 4.7458 | [5 empty] | 40 | 10 | 15 | 500 | 2022-01-16 | 29.13 | 25 | S5N_22_04A
2022-01-04 | 44.3548 | 100.1456 | 51.1177 | 0.51002 | 1.4271 | 1.2211 | 1.2128 | 4.8394 |  | 2.8444 | 3.0797 | 1.9608 |  | 40 | 10 | 15 | 500 | 2022-01-23 | 34.15 | 25 | S5N_22_07A
2022-01-05 | 45.3929 | 151.3945 | 76.0093 | 0.50521 | 1.2133 | 1.2042 | 1.5605 | 6.1354 |  | 4.5875 | 3.6027 | 2.8462 |  | 40 | 10 | 15 | 500 | 2022-01-30 | 32.16 | 25 | S5N_22_10A
2022-01-06 | 27.0641 | 246.8368 | 95.8898 | 0.43328 | 1.5968 | 1.399 | 1.8918 | 6.1873 |  | 5.8649 | 4.1678 | 3.1579 |  | 40 | 10 | 15 | 500 | 2022-02-06 | 34.78 | 25 | S5N_22_11A
2022-01-07 | 28.9371 | 312.9242 | 143.4883 | 0.54186 | 2.2878 | 2.4101 | 1.6269 | 6.1019 |  | 4.4046 | 3.6881 | 2.6369 |  | 40 | 10 | 15 | 500 | 2022-02-13 | 33.41 | 25 | S5N_22_14A
2022-01-08 | 29.2359 | 312.4432 | 146.212 | 0.51582 | 3.2191 | 2.8576 | 1.1596 | 4.8642 |  | 4.2597 | 3.6669 | 2.5861 |  | 40 | 10 | 15 | 500 | 2022-02-20 | 31.39 | 25 | S5N_22_15A
2022-01-09 | 35.775 | 303.6646 | 162.5204 | 0.52387 | 2.142 | 1.9811 | 1.3153 | 5.8072 |  | 4.447 | 3.7658 | 2.6863 |  | 40 | 10 | 15 | 500 | 2022-02-27 | 21.73 | 25
2022-01-10 | 44.8846 | 302.7822 | 160.538 | 0.54327 | 1.8265 | 1.4916 | 0.97985 | 6.4118 |  | 4.3102 | 3.6894 | 2.7511 |  | 40 | 10 | 15 | 500 | 2022-03-06 | 23.51 | 25
2022-01-11 | 58.9248 | 341.688 | 169.5175 | 0.63253 | 2.139 | 1.7854 | 1.8472 | 7.524 |  | 5.7903 | 4.1404 | 3.0182 |  | 40 | 10 | 15 | 500 | 2022-03-13 | 19.43 | 25
2022-01-12 | 51.9513 | 313.4881 | 122.7971 | 0.65785 | 1.4976 | 1.4284 | 1.9759 | 6.4839 |  | 4.4907 | 3.6618 | 2.5977 |  | 40 | 10 | 15 | 500 | 2022-03-20 | 23.92 | 25
2022-01-13 | 52.5739 | 353.4943 | 140.2496 | 0.73716 | 2.0702 | 1.8441 | 1.9662 | 4.42 |  | 5.1379 | 4.0877 | 2.9143 |  | 40 | 10 | 15 | 500 | 2022-03-27 | 20.38 | 25
2022-01-14 | 57.7167 | 448.3256 | 120.3702 | 0.79597 | 1.9083 | 1.7365 | 1.7381 | 4.533 |  | 5.1214 | 4.0125 | 3.0874 |  | 40 | 10 | 15 | 500
2022-01-15 | 53.4474 | 436.5767 | 131.2763 | 0.69356 | 1.3334 | 1.149 | 2.0939 | 7.1908 |  | 5.6478 | 4.166 | 3.0098 |  | 40 | 10 | 15 | 500
2022-01-16 | 48.4845 | 278.8382 | 78.3484 | 0.71236 | 2.0841 | 1.6013 | 1.7597 | 7.4659 |  | 4.8252 | 3.7463 | 2.6798 |  | 40 | 10 | 15 | 500
2022-01-17 | 42.7084 | 194.1164 | 59.0029 | 0.66079 | 1.6363 | 1.4365 | 1.5687 | 9.7818 |  | 5.6104 | 4.2034 | 2.8772 |  | 40 | 10 | 15 | 500
2022-01-18 | 0.0043258 | 0 | 0 | 4.4551e-05 | 1.8613 | 1.613 | 2.1954 | 7.8648 |  | 5.2739 | 4.2626 | 2.676 |  | 40 | 10 | 15 | 500
2022-01-19 | 40.4497 | 72.7 | 54.6931 | 0.46079 | 1.2912 | 1.1387 | 1.6706 | 5.3233 |  | 5.007 | 3.796 | 2.6335 |  | 40 | 10 | 15 | 500
2022-01-20 | 52.5773 | 201.3299 | 116.145 | 0.63171 | 1.3168 | 1.1181 | 1.9461 | 9.9944 |  | 5.0565 | 3.8104 | 2.7274 |  | 40 | 10 | 15 | 500
2022-01-21 | 36.4582 | 284.5065 | 130.4877 | 0.5927 | 1.2501 | 1.0647 | 1.7132 | 7.6767 |  | 6.1124 | 4.2342 | 2.8897 |  | 40 | 10 | 15 | 500
2022-01-22 | 32.8282 | 354.3428 | 125.8331 | 0.60505 | 1.187 | 1.0191 | 2.2172 | 9.2659 |  | 6.0611 | 4.1575 | 2.8964 |  | 40 | 10 | 15 | 500
2022-01-23 | 38.0035 | 382.0682 | 137.3432 | 0.61711 | 1.2335 | 1.1119 | 1.9168 | 8.8081 |  | 5.5602 | 4.1502 | 2.8065 |  | 40 | 10 | 15 | 500
2022-01-24 | 31.3075 | 165.9677 | 65.0918 | 0.57537 | 1.3331 | 1.0453 | 1.1832 | 6.2804 |  | 4.2835 | 3.6632 | 2.5135 |  | 40 | 10 | 15 | 500
2022-01-25 | 36.6356 | 193.5267 | 80.4129 | 0.66147 | 1.395 | 0.96979 | 1.5808 | 8.9457 |  | 4.0697 | 3.5406 | 2.4312 |  | 40 | 10 | 15 | 500
2022-01-26 | 35.5537 | 302.9837 | 128.2259 | 0.64683 | 2.3812 | 1.8311 | 1.7279 | 7.4919 |  | 4.8888 | 3.7592 | 2.6686 |  | 40 | 10 | 15 | 500
2022-01-27 | 37.7258 | 276.5583 | 92.9805 | 0.72745 | 2.9961 | 2.5765 | 1.6742 | 7.9468 |  | 5.5531 | 3.9989 | 2.7955 |  | 40 | 10 | 15 | 500
2022-01-28 | 46.0705 | 284.6931 | 89.8056 | 0.79873 | 2.4582 | 1.7958 | 1.7982 | 9.5883 |  | 5.4049 | 4.1048 | 2.7768 |  | 40 | 10 | 15 | 500
2022-01-29 | 56.2871 | 450.6496 | 128.5071 | 0.75847 | 2.9284 | 2.5022 | 1.5129 | 10.3269 |  | 5.0892 | 4.0834 | 2.7174 |  | 40 | 10 | 15 | 500
2022-01-30 | 34.2313 | 396.4353 | 98.6128 | 0.56541 | 2.404 | 1.8344 | 1.5517 | 10.4979 |  | 5.0549 | 3.9818 | 2.7205 |  | 40 | 10 | 15 | 500
2022-01-31 | 54.5931 | 296.4057 | 100.004 | 0.60751 | 1.2505 | 0.82016 | 1.7781 | 4.9494 |  | 3.868 | 3.4258 | 2.3406 |  | 40 | 10 | 15 | 500
2022-02-01 | 57.2781 | 387.1158 | 146.5586 | 0.66463 | 2.4168 | 0.48795 | 1.3983 | 2.4539 |  | 2.9905 | 2.9962 | 1.7546 |  | 40 | 10 | 15 | 500
2022-02-02 | 49.0327 | 387.6424 | 145.0099 | 0.70644 | 1.3731 | 0.36171 | 1.3837 | 2.6174 |  | 1.7855 | 2.7328 | 1.2293 | 2.8043 | 40 | 10 | 15 | 500
2022-02-03 | 34.6143 | 253.6765 | 104.4488 | 0.63867 | 0.81084 | 0.4871 | 1.2183 | 2.1166 |  | 0.96084 | 2.3334 | 0.7512 | 2.7096 | 40 | 10 | 15 | 500
2022-02-04 | 43.9336 | 84.4529 | 37.5681 | 0.64288 | 0.96715 | 0.6468 | 1.1244 | 2.8233 |  | 2.6515 | 2.9072 | 2.0318 | 5.3024 | 40 | 10 | 15 | 500
2022-02-05 | 46.1906 | S5N_22_33A | S5N_22_33A | 0.67381 | 0.67816 | 0.61723 | 0.42539 | 4.1507 |  | 3.733 | 3.2233 | 2.3699 | 6.529 | 40 | 10 | 15 | 500
2022-02-06 | 33.3794 |  |  | 0.66807 | 0.67984 | 0.55152 | 0.81965 | 2.9006 |  | 2.558 | 2.9279 | 1.6889 | 3.6206 | 40 | 10 | 15 | 500
2022-02-07 | 51.9653 | 230.9914 | 81.4178 | 0.68347 | 0.43827 | 0.35511 | 1.0869 | 4.6069 |  | 3.0341 | 3.1772 | 1.8497 | 0.81272 | 40 | 10 | 15 | 500
2022-02-08 | 44.4366 | 295.131 | 93.064 | 0.48663 | 0.44934 | 0.35357 | 1.1951 | 5.4076 |  | 3.7893 | 3.3813 | 2.1366 | 0.9445 | 40 | 10 | 15 | 500
2022-02-09 | 57.8344 | 378.7758 | 104.9927 | 0.4906 | 0.5053 | 0.34956 | 1.1491 | 2.1574 |  | 2.9914 | 2.9104 | 1.6885 | 2.0298 | 40 | 10 | 15 | 500
2022-02-10 | 18.1898 | 164.4186 | 56.4941 | 0.36894 | 0.92094 | 0.67296 | 0.52811 | 3.9025 |  | 3.3532 | 3.3471 | 2.1996 | 0.84612 | 40 | 10 | 15 | 500
2022-02-11 | 76.5467 | 377.4611 | 110.0447 | 0.49274 | 0.87999 | 0.73487 | 0.65697 | 4.7983 |  | 3.1546 | 3.3902 | 2.1714 | 0.42785 | 40 | 10 | 15 | 500
2022-02-12 | 67.4837 | 380.288 | 126.2881 | 0.4966 | 0.71345 | 0.58862 | 0.48665 | 2.3006 | 0.99433 | 2.5492 | 3.3105 | 1.8292 | 0.7324 | 40 | 10 | 15 | 500
2022-02-13 | 40.7259 | 464.3616 | 117.9947 | 0.56036 | 0.55562 | 0.41214 | 0.95682 | 3.0954 | 1.0236 | 3.3655 | 3.439 | 2.1352 | 7.0282 | 40 | 10 | 15 | 500
2022-02-14 | 50.4959 | 422.5137 | 114.0327 | 0.57887 | 0.46394 | 0.34164 | 1.393 | 7.6378 | 1.3576 | 3.1828 | 3.3026 | 2.2357 | 5.1333 | 40 | 10 | 15 | 500
2022-02-15 | 23.1435 | 196.5721 | 63.5579 | 0.50458 | 0.5734 | 0.38868 | 1.4045 | 6.794 | 1.14 | 3.4673 | 3.371 | 2.2106 | 5.7692 | 40 | 10 | 15 | 500
2022-02-16 | 41.8234 | 469.4336 | 150.1387 | 0.57311 | 0.76276 | 0.57119 | 0.90006 | 3.3689 | 0.95946 | 3.0498 | 3.567 | 1.9513 | 1.9224 | 40 | 10 | 15 | 500
2022-02-17 | 38.0732 | 427.2195 | 135.2139 | 0.5513 | 1.3328 | 0.9612 | 0.54283 | 6.8619 | 2.0053 | 4.8603 | 3.7219 | 2.4281 | 1.5549 | 40 | 10 | 15 | 500
2022-02-18 | 39.6063 | 375.329 | 117.5811 | 0.51555 | 0.96068 | 0.7363 | 0.65082 | 2.3137 | 1.1098 | 2.8348 | 3.0135 | 1.63 | 1.2101 | 40 | 10 | 15 | 500
2022-02-19 | 18.7446 | 151.2217 | 57.6502 | 0.42362 | 0.48911 | 0.313 | 0.8547 | 1.9277 | 0.9006 | 2.1184 | 2.8286 | 1.1935 | 1.5828 | 40 | 10 | 15 | 500
2022-02-20 | 42.3867 | 436.254 | 134.75 | 0.52966 | 1.15 | 1.2358 | 1.0811 | 2.6137 | 1.4641 | 5.062 | 3.7091 | 2.3616 | 1.9029 | 40 | 10 | 15 | 500
2022-02-21 | 0 | 0 | 0 | 0.076124 | 0.87382 | 0.52097 | 1.1524 | 3.6667 | 2.4526 | 4.8293 | 3.9296 | 2.4721 | 1.3878 | 40 | 10 | 15 | 500
2022-02-22 | 0 | 0 | 0 | 0.020908 | 1.2179 | 0.95015 | 1.3889 | 3.3127 | 3.8282 | 7.5119 | 4.605 | 3.0419 | 1.4985 | 40 | 10 | 15 | 500
2022-02-23 | 0 | 0 | 0 | 0.01911 | 1.6855 | 1.2657 | 1.5841 | 1.3146 | 11.8207 | 10.2932 | 6.3189 | 3.6244 | 1.1802 | 40 | 10 | 15 | 500
2022-02-24 | 0 | 0 | 0 | 0.48875 | 1.5943 | 1.6133 | 1.3128 | 1.8793 | 12.98 | 14.3299 | 7.5976 | 4.5688 | 1.053 | 40 | 10 | 15 | 500
2022-02-25 | 45.8055 | 218.3681 | 69.0324 | 0.37752 | 1.6588 | 1.6024 | 0.45283 | 1.8177 | 1.2 | 6.2993 | 5.4083 | 3.2618 | 0.80663 | 40 | 10 | 15 | 500
2022-02-26 | 20.3428 | 382.724 | 111.3159 | 0.38202 | 1.6715 | 1.4378 | 1.4142 | 5.5608 | 11.7378 | 6.5359 | 4.7056 | 2.8937 | 0.92008 | 40 | 10 | 15 | 500
2022-02-27 | 29.6199 | 383.4087 | 148.0082 | 0.52309 | 1.1816 | 0.82086 | 1.3899 | 3.638 | 8.0112 | 4.7315 | 4.3156 | 2.7707 | 0.62703 | 40 | 10 | 15 | 500
2022-02-28 | 47.2982 | 411.2704 | 160.588 | 0.55012 | 1.6237 | 1.2449 | 1.368 | 6.0174 | 13.133 | 6.7981 | 5.0847 | 3.1202 | 5.956 | 40 | 10 | 15 | 500
2022-03-01 | 40.4814 | 238.4802 | 96.088 | 0.41433 | 1.3293 | 1.2408 | 1.4241 | 5.4463 | 13.6983 | 5.5655 | 4.9982 | 2.7478 | 1.6378 | 40 | 10 | 15 | 500
2022-03-02 | 39.3594 | 431.1778 | 149.9785 | 0.50094 | 0.61826 | 0.55037 | 1.5038 | 2.4006 | 5.0873 | 3.0323 | 3.7617 | 1.813 | 0.84521 | 40 | 10 | 15 | 500
2022-03-03 | 43.2738 | 412.8087 | 143.6264 | 0.50993 | 1.2219 | 1.0188 | 1.1216 | 2.4214 | 4.3954 | 3.771 | 4.0804 | 2.3949 | 1.5241 | 40 | 10 | 15 | 500
2022-03-04 | 30.7193 | 207.7697 | 83.8176 | 0.54063 | 1.7378 | 1.3043 | 1.0807 | 3.6679 | 8.8731 | 7.0022 | 5.2742 | 3.1049 | 1.2262 | 40 | 10 | 15 | 500
2022-03-05 | 52.4585 | S5N_22_19A | S5N_22_19A | 0.53978 | 1.8575 | 1.5533 | 1.596 | 5.7697 | 13.3313 | 6.747 | 5.215 | 3.1077 | 0.70664 | 40 | 10 | 15 | 500
2022-03-06 | 24.8483 |  |  | 0.53124 | 1.8837 | 1.5398 | 1.4216 | 5.5346 | 9.7786 | 6.3545 | 5.0126 | 3.0492 | 0.72555 | 40 | 10 | 15 | 500
2022-03-07 | 43.8632 | 305.6907 | 124.8532 | 0.61775 | 2.5074 | 1.9162 | 1.6924 | 8.4838 | 13.8054 | 8.9204 | 6.4225 | 3.7218 | 0.87144 | 40 | 10 | 15 | 500
2022-03-08 | 37.8416 | 432.919 | 184.8852 | 0.56142 | 1.8427 | 1.6868 | 2.352 | 10.491 | 17.3212 | 7.9724 | 5.7536 | 3.3823 | 0.68289 | 40 | 10 | 15 | 500
2022-03-09 | 41.6089 | 513.0447 | 148.3531 | 0.5063 | 1.4694 | 1.3934 | 1.569 | 6.3465 | 14.4323 | 6.7659 | 5.3221 | 2.9389 | 0.54381 | 40 | 10 | 15 | 500
2022-03-10 | 39.6912 | 463.0544 | 154.0128 | 0.56451 | 1.9689 | 1.6289 | 1.6094 | 3.291 | 12.9104 | 4.8487 | 4.7064 | 2.5905 | 0.50694 | 40 | 10 | 15 | 500
2022-03-11 | 34.0286 | 479.4706 | 152.4212 | 0.4979 | 1.6137 | 1.0301 | 1.3557 | 3.0476 | 6.5023 | 5.3826 | 4.7107 | 2.7328 | 1.0796 | 40 | 10 | 15 | 500
2022-03-12 | 40.1652 | 463.2137 | 124.2661 | 0.55933 | 2.0332 | 1.1139 | 1.8489 | 3.1424 | 1.7985 | 5.5046 | 4.716 | 2.5674 | 0.68193 | 40 | 10 | 15 | 500
2022-03-13 | 48.4645 | 494.1942 | 147.0387 | 0.49308 | 1.7939 | 1.1538 | 1.3551 | 4.0618 | 1.7932 | 6.036 | 4.5127 | 2.8391 | 0.55908 | 40 | 10 | 15 | 500
2022-03-14 | 40.1142 | 441.2846 | 127.1932 | 0.51195 | 1.7241 | 1.1027 | 1.7548 | 5.6882 | 2.7489 | 7.497 | 5.4009 | 3.2083 | 0.55612 | 40 | 10 | 15 | 500
2022-03-15 | 53.3546 | 464.0659 | 154.1233 | 0.57007 | 2.0936 | 1.2375 | 1.9848 | 3.6106 | 2.4068 | 5.5331 | 4.7704 | 2.6769 | 0.49159 | 40 | 10 | 15 | 500
2022-03-16 | 50.9501 | 429.3928 | 161.4268 | 0.60869 | 2.2569 | 0.78413 | 1.6267 | 5.0851 | 3.2185 | 8.1177 | 5.8287 | 3.162 | 0.53218 | 40 | 10 | 15 | 500
2022-03-17 | 53.9264 | 374.0051 | 137.6686 | 0.60257 | 2.0817 | 1.1257 | 1.73 | 4.8652 | 1.7715 | 7.3631 | 5.9881 | 2.9145 | 0.4678 | 40 | 10 | 15 | 500
2022-03-18 | 45.2828 | 437.5314 | 161.0047 | 0.71032 | 2.0618 | 1.3081 | 1.352 | 3.4965 | 1.6541 | 5.5187 | 4.5397 | 2.251 | 0.59715 | 40 | 10 | 15 | 500
2022-03-19 | 25.9375 | 237.9511 | 100.1372 | 0.56969 | 2.2709 | 1.3124 | 1.8317 | 3.2105 | 1.7774 | 7.6582 | 5.0626 | 2.9299 | 0.19893 | 40 | 10 | 15 | 500
2022-03-20 | 44.8285 | 450.8123 | 137.1669 | 0.66893 | 1.8119 | 1.4108 | 2.2179 | 5.5404 | 2.8139 | 10.6608 | 5.9336 | 3.5229 | 0.10477 | 40 | 10 | 15 | 500
2022-03-21 | 46.997 | 451.4953 | 142.4773 | 0.64472 | 1.5197 | 1.0556 | 1.7339 | 6.3329 | 3.5945 | 10.6373 | 6.9845 | 3.5724 | 0.14878 | 40 | 10 | 15 | 500
2022-03-22 | 11.5261 | 84.3571 | 36.9977 | 0.19663 | 1.986 | 1.241 | 1.6926 | 7.2105 | 3.8517 | 7.9942 | 5.2923 | 3.0999 | 0.11525 | 40 | 10 | 15 | 500
2022-03-23 | 14.8934 | 43.9077 | 25.0722 | 0.13587 | 1.3884 | 0.96138 | 1.8769 | 4.5531 | 5.1725 | 10.4401 | 6.9865 | 2.243 | 0.11309 | 40 | 10 | 15 | 500
2022-03-24 | 27.3907 | 318.7799 | 100.635 | 0.53101 | 1.627 | 1.2744 | 1.8601 | 6.0949 | 9.1791 | 12.3015 | 8.494 | 0.73153 | 0.094753 | 40 | 10 | 15 | 500
2022-03-25 | 24.837 | 326.1147 | 104.3288 | 0.6894 | 2.482 | 2.1381 | 1.5812 | 9.6067 | 10.0146 | 9.7139 | 5.1609 | 8.9807 | 0.12122 | 40 | 10 | 15 | 500
2022-03-26 | 32.4105 | 479.4697 | 144.7923 | 0.88597 | 1.9621 | 1.7084 | 1.3381 | 8.2405 | 12.0733 | 8.3208 | 3.9803 | 13.2159 | 0.11034 | 40 | 10 | 15 | 500
2022-03-27 | 30.8118 | 443.5037 | 140.7105 | 0.74888 | 0.62483 | 0.43862 | 1.1686 | 4.7899 | 4.89 | 4.9353 | 2.6954 | 6.527 | 0.085508 | 40 | 10 | 15 | 500
2022-03-28 | 36.6473 | 449.4889 | 155.3409 | 0.89595 | 1.3894 | 1.0764 | 1.2596 | 7.0978 | 7.3495 | 6.2606 | 3.7238 | 2.555 | 0.096738 | 40 | 10 | 15 | 500
2022-03-29 | 25.4554 | 349.1385 | 111.3479 | 0.85712 | 1.1493 | 0.90784 | 1.4993 | 8.601 | 8.8359 | 7.7523 | 4.3446 | 1.4829 | 0.081976 | 40 | 10 | 15 | 500
2022-03-30 | 30.3369 | 469.8786 | 138.5834 | 0.90713 | 1.5295 | 1.3191 | 1.4926 | 6.1239 | 10.0736 | 8.1022 | 3.8845 | 1.6685 | 0.0831 | 40 | 10 | 15 | 500
2022-03-31 | 26.0209 | 389.2599 | 128.8539 | 0.72156 | 1.1853 | 0.94582 | 1.6769 | 7.1102 | 7.5628 | 7.4484 | 3.7621 | 2.4985 | 0.11136 | 40 | 10 | 15 | 500
2022-04-01
2022-04-02
Formulas:
Source = [Source, row above]+7
Note on C6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Monthly Part A: S5N_22_09A
Note on C23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Plant Stop
Note on C37: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Monthly Part A: S5N_22_18A
Note on C57: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Plant Shutdown
Note on C58: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Plant Shutdown
Note on C59: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Plant Shutdown
Note on C60: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Plant Shutdown
Note on C65: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Monthly Part A: S5N_22_31A
Note on K72: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: S5N_22_20A
Note on D73: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: S5N_22_21A