## Notes
Reference conditions
All concentrations in this spreadsheet are reported in dry air at a temperature of 273K, at a pressure of 101.3 kPa and with an oxygen content of 3% dry
Uncertainty
Concentrations in this spreadsheet are reported after having subtracted the value of the 95% confidence interval (see Section 3.6.7 of the permit):
95% confidence interval for nitrogen oxides is taken to be 20%
95% confidence interval for sulphur dioxide is taken to be 20%
95% confidence interval for dust is taken to be 30%
95% confidence interval for carbon monoxide is taken to be 10%
Normal operating conditions
The document "Power Plant Boiler Abnormal Conditions" sets out the criteria for excluding emissions monitoring data from permitting or other reporting obligations:
| Parameter | Plant | Level representing abnormal conditions
| Boiler oxygen | All boilers | >17% oxygen
| Fuel input | A51, A52A, A52B, A53 and A62 | <50% BFG by thermal input
|  | A50 (Service Boilers) | <35% BFG by thermal input

## Summary
Dust concentrations in mg/m³ (except A55 as % obscuration), reported as measured (uncertainty not taken into account)
| Source | A1 | A2 | A8A | A8B | A9 | A10 | A10A | A14 | A15 | A16 | A55 | A63 | A1 | A1
| Description | Sinter plant main stack (particulate) | Sinter plant deduster stack | BF4 casthouse fume extraction North | BF4 casthouse fume extraction South | BF5 casthouse fume extraction | Iron desulphurisation/hot metal pouring fume extraction plant stack | Hot metal fume extraction no. 2 | Secondary fume extraction stack North | Secondary fume extraction stack Centre | Secondary fume extraction stack South | Morfa main stack | CASOB/ desulph fume extraction plant | Sinter plant main stack (SO2) | Sinter plant main stack (NOX)
Daily means | Minimum | 1.09 | 0.34 | 0.77 | 0.4 | 0.37 | 0.7 | 0.15 | 0.61 | 1.26 | 1.21 |  | 3.498e-05 | 31.32 | 30.88
| Maximum | 61.69 | 1.41 | 3.26 | 2.35 | 2.76 | 9.25 | 12.74 | 12.15 | 5.81 | 3.61 |  | 0.59923 | 604.38 | 181.2
| Limit | 40 | 10 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 500 | 500
| No. > Limit | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 17 | 0
| No. > Limit w Uncert | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
Weekly mean | Minimum | [10 empty] | 20.13
| Maximum | [10 empty] | 42.13
| Limit | [10 empty] | 25
| No. > Limit | [10 empty] | 10
| No. > Limit w Uncert | [10 empty] | 1

## Plots
NOTES

## Data
| Measured concentrations - daily means (mg/m³) | [25 empty] | Limits |  |  |  |  | Obscuration %
Source | A1 | A1 | A1 | A1 | A1 | A1 | A2 | A2 | A8A | A8A | A8B | A8B | A9 | A9 | A10 | A10 | A10A | A10A | A14 | A14 | A15 | A15 | A16 | A16 | A63 | A63 | A1 | A2 | BF and BOS plant sources | A1 | Source | A55
Description | Sinter plant main stack (Particulate) | Sinter plant main stack (Particulate) Uncertainty Applied | Sinter plant main stack (SO2) | Sinter plant main stack (SO2) Uncertainty Applied | Sinter plant main stack (NOX) | Sinter plant main stack (NOx) Uncertainty Applied | Sinter plant deduster stack | Sinter plant deduster stack Uncertainty Applied | BF4 casthouse fume extraction North | BF4 casthouse fume extraction North Uncertainty Applied | BF4 casthouse fume extraction South | BF4 casthouse fume extraction South Uncertainty Applied | BF5 casthouse fume extraction | BF5 casthouse fume extraction | Iron desulphurisation/hot metal pouring fume extraction plant stack | Iron desulphurisation/hot metal pouring fume extraction plant stack Uncertainty Applied | Hot metal fume extraction no. 2 | Hot metal fume extraction no. 2 Uncetainty Applied | Secondary fume extraction stack North | Secondary fume extraction stack North Uncertainty Applied | Secondary fume extraction stack Centre | Secondary fume extraction stack Centre Uncertainty Applied | Secondary fume extraction stack South | Secondary fume extraction stack South Uncertainty Applied | CASOB/ desulph fume extraction plant | CASOB/ desulph fume extraction plant Uncertainty Applied | Sinter plant main stack | Sinter plant deduster stack |  | Sinter Plant Main Stack SO2 & NOX | Description | Morfa main stack
Date / Uncertainty |  | 30% |  | 20% |  | 20% |  | 30% |  | 30% |  | 30% |  | 30% |  | 30% |  | 30% |  | 30% |  | 30% |  | 30% |  | 30% |  |  |  |  | Week commencing | Measured | Uncertainty Applied 30% | Limit
2022-04-01 | 1.09 |  | 118.87 |  | 46.73 |  | 0.41 |  | 1.03 |  | 0.84 |  | 1.34 |  | 5.53 |  | 12.74 |  | 6.37 |  | 3.29 |  | 2.49 |  | 0.10335 |  | 40 | 10 | 15 | 500 | 2022-04-02 | 20.38 |  | 25
2022-04-02 | 30.79 |  | 462.53 |  | 142.33 |  | 0.74 |  | 2.85 |  | 2.19 |  | 1.6 |  | 7.08 |  | 11.48 |  | 6.94 |  | 3.28 |  | 1.49 |  | 0.11351 |  | 40 | 10 | 15 | 500 | 2022-04-09 | 33.64 | 23.548 | 25
2022-04-03 | 27.02 |  | 335.25 |  | 108.47 |  | 0.62 |  | 1.68 |  | 1.43 |  | 1.71 |  | 7.3 |  | 12.09 |  | 7.96 |  | 3.6 |  | 1.66 |  | 0.10135 |  | 40 | 10 | 15 | 500 | 2022-04-16 | 21.87 |  | 25
2022-04-04 | 21.54 |  | 436.98 |  | 160 |  | 0.88 |  | 2.09 |  | 1.83 |  | 1.58 |  | 7.47 |  | 9.88 |  | 6.5 |  | 2.91 |  | 3.32 |  | 0.092909 |  | 40 | 10 | 15 | 500 | 2022-04-23 | 25.85 | 18.095 | 25
2022-04-05 | 26.4 |  | 476.46 |  | 163.14 |  | 1.05 |  | 1.23 |  | 1.08 |  | 1.48 |  | 5.11 |  | 5.71 |  | 7.14 |  | 3.16 |  | 2.25 |  | 0.10574 |  | 40 | 10 | 15 | 500 | 2022-04-30 | 31.57 | 22.099 | 25
2022-04-06 | 22.66 |  | 412.82 |  | 147.81 |  | 0.93 |  | 1.57 |  | 1.42 |  | 1.6 |  | 7.93 |  | 0.89 |  | 4.9 |  | 2.63 |  | 1.64 |  | 0.10452 |  | 40 | 10 | 15 | 500 | 2022-05-07 | 29.99 | 20.993 | 25
2022-04-07 | 24.94 |  | 416.43 |  | 134.22 |  | 0.86 |  | 1.66 |  | 1.21 |  | 1.92 |  | 3.8 |  | 1.19 |  | 5.49 |  | 2.69 |  | 2.04 |  | 0.12549 |  | 40 | 10 | 15 | 500 | 2022-05-14 | 29.59 | 20.713 | 25
2022-04-08 | 23.55 |  | 467.43 |  | 120.68 |  | 0.81 |  | 0.9 |  | 0.8 |  | 1.41 |  | 2.94 |  | 1.1 |  | 5.93 |  | 2.67 |  | 1.61 |  | 0.096448 |  | 40 | 10 | 15 | 500 | 2022-05-21 | 31.76 | 22.232 | 25
2022-04-09 | 32.31 |  | 511.69 | 409.352 | 145.31 |  | 1.08 |  | 1.54 |  | 1.09 |  | 1.5 |  | 2.25 |  | 0.15 |  | 5.45 |  | 2.7 |  | 1.96 |  | 0.090205 |  | 40 | 10 | 15 | 500 | 2022-05-28 | 42.13 | 29.491 | 25 | S5N_22_46A
2022-04-10 | 28.14 |  | 407.32 |  | 119.62 |  | 0.87 |  | 3.26 |  | 2.35 |  | 1.61 |  | 2.83 |  | 1.33 |  | 6.03 |  | 3.06 |  | 1.31 |  | 0.11188 |  | 40 | 10 | 15 | 500 | 2022-06-04 | 30.38 | 21.266 | 25
2022-04-11 | 13.32 |  | 214.57 |  | 65.32 |  | 0.6 |  | 1.47 |  | 1.08 |  | 1.74 |  | 4.12 |  | 4.15 |  | 7.65 |  | 3.79 |  | 2.17 |  | 0.44853 |  | 40 | 10 | 15 | 500 | 2022-06-11 | 28.89 | 20.223 | 25
2022-04-12 | 35.2 |  | 494.12 |  | 135.64 |  | 0.89 |  | 2.31 |  | 1.68 |  | 1.66 |  | 3.85 |  | 6.08 |  | 3.6 |  | 3.4 |  | 2.6 |  | 0.59923 |  | 40 | 10 | 15 | 500 | 2022-06-18 | 27.99 | 19.593 | 25
2022-04-13 | 38.35 |  | 524.92 | 419.936 | 148.76 |  | 0.9 |  | 1.1 |  | 0.82 |  | 1.34 |  | 2.09 |  | 3.44 |  | 3.33 |  | 2.44 |  | 2.1 |  | 0.062956 |  | 40 | 10 | 15 | 500 | 2022-06-25 | 20.13 |  | 25
2022-04-14 | 42.56 | 29.792 | 489.56 |  | 150.43 |  | 0.89 |  | 1.51 |  | 1.14 |  | 1.12 |  | 2.18 |  | 3.14 |  | 2.74 |  | 2.37 |  | 2.05 |  | 0.001457 |  | 40 | 10 | 15 | 500
2022-04-15 | 38.05 |  | 496.93 |  | 159.19 |  | 1 |  | 2.32 |  | 1.73 |  | 1.07 |  | 3.08 |  | 3.95 |  | 2.21 |  | 2.88 |  | 2.53 |  | 0.0014759 |  | 40 | 10 | 15 | 500
2022-04-16 | 31.78 |  | 556.85 | 445.48 | 127.18 |  | 1.04 |  | 2.21 |  | 1.48 |  | 1.29 |  | 2.38 |  | 2.21 |  | 1.62 |  | 2.66 |  | 2.35 |  | 0.0025049 |  | 40 | 10 | 15 | 500
2022-04-17 | 36.7 |  | 573.64 | 458.912 | 123.16 |  | 0.77 |  | 1.95 |  | 1.47 |  | 1.52 |  | 3.38 |  | 4.16 |  | 1.59 |  | 3.24 |  | 2.69 |  | 0.0010807 |  | 40 | 10 | 15 | 500
2022-04-18 | 36.45 |  | 580.3 | 464.24 | 125.19 |  | 0.8 |  | 1.76 |  | 1.35 |  | 1.57 |  | 4.06 |  | 5.55 |  | 1.72 |  | 2.96 |  | 2.67 |  | 0.00086616 |  | 40 | 10 | 15 | 500
2022-04-19 | 36.74 |  | 555.52 | 444.416 | 131 |  | 0.92 |  | 1.39 |  | 1.04 |  | 1.53 |  | 5.13 |  | 5.6 |  | 1.63 |  | 2.77 |  | 2.56 |  | 0.00062401 |  | 40 | 10 | 15 | 500
2022-04-20 | 37.25 |  | 601.18 | 480.944 | 154.39 |  | 0.95 |  | 2.22 |  | 1.54 |  | 2.22 |  | 4.68 |  | 6.68 |  | 1.71 |  | 2.78 |  | 2.74 |  | 0.00048429 |  | 40 | 10 | 15 | 500
2022-04-21 | 49.95 | 34.965 | 572.54 | 458.032 | 156.1 |  | 1.1 |  | 1.66 |  | 1.24 |  | 1.55 |  | 6.2 |  | 7.08 |  | 1.93 |  | 2.98 |  | 3.33 |  | 0.00088064 |  | 40 | 10 | 15 | 500
2022-04-22 | 43.72 | 30.604 | 570.96 | 456.768 | 168.73 |  | 1.18 |  | 2.44 |  | 1.93 |  | 1.02 |  | 2.18 |  | 4.31 |  | 1.82 |  | 2.77 |  | 3.23 |  | 0.00043248 |  | 40 | 10 | 15 | 500
2022-04-23 | 40.94 | 28.658 | 467.9 |  | 161.4 |  | 1.01 |  | 2.25 |  | 1.99 |  | 1.26 |  | 3.34 |  | 7.13 |  | 2.01 |  | 2.92 |  | 3.41 |  | 0.00011818 |  | 40 | 10 | 15 | 500
2022-04-24 | 14.49 |  | 179.56 |  | 75.33 |  | 0.81 |  | 2.3 |  | 1.78 |  | 1.39 |  | 4.75 |  | 7.3 |  | 2.08 |  | 3.2 |  | 3.31 |  | 0.00015697 |  | 40 | 10 | 15 | 500
2022-04-25 | 42.92 | 30.044 | 480.79 |  | 155.44 |  | 0.96 |  | 1.69 |  | 1.34 |  | 1.21 |  | 6.13 |  | 6.87 |  | 2.94 |  | 4.26 |  | 3.61 |  | 0.0011594 |  | 40 | 10 | 15 | 500
2022-04-26 | 46.35 | 32.445 | 543.12 | 434.496 | 181.2 |  | 1.19 |  | 1.64 |  | 1.32 |  | 1.75 |  | 4.8 |  | 5.86 |  | Abatement Form: Fume extraction 14/15/16 BOS 002_15/04/22 |  | 3.67 |  | 2.86 |  | 0.0012133 |  | 40 | 10 | 15 | 500
2022-04-27 | 30 |  | 146.94 |  | 58.7 |  | 0.69 |  | 1.31 |  | 1.07 |  | 1.2 |  | 6.06 |  | 5.52 |  |  |  | 3.26 |  | 3.14 |  | 0.0014119 |  | 40 | 10 | 15 | 500
2022-04-28 | 41.73 | 29.211 | 484.09 |  | 142.71 |  | 0.62 |  | 1.77 |  | 1.28 |  | 1.44 |  | 7.41 |  | 9.12 |  |  |  | 3.72 |  | 3.47 |  | 0.0016887 |  | 40 | 10 | 15 | 500
2022-04-29 | 39.36 |  | 560.69 | 448.552 | 147.86 |  | 0.65 |  | 1.48 |  | 1.15 |  | 1.84 |  | 5.17 |  | 10.56 |  |  |  | 3.61 |  | 3.07 |  | 0.0014827 |  | 40 | 10 | 15 | 500
2022-04-30 | 40.08 | 28.056 | 561.65 | 449.32 | 158.91 |  | 0.75 |  | 1.77 |  | 1.28 |  | 1.92 |  | 5.8 |  | 9.43 |  |  |  | 3.49 |  | 2.92 |  | 0.0014962 |  | 40 | 10 | 15 | 500
2022-05-01 | 44.08 | 30.856 | 561.92 | 449.536 | 169.42 |  | 0.69 |  | 1.64 |  | 1.24 |  | 1.95 |  | 7 |  | 9.72 |  |  |  | 3.45 |  | 2.72 |  | 0.0016227 |  | 40 | 10 | 15 | 500
2022-05-02 | 48.8 | 34.16 | 586.82 | 469.456 | 148.58 |  | 0.68 |  | 1.54 |  | 1.05 |  | 1.28 |  | 5.27 |  | 6.35 |  |  |  | 3.01 |  | 2.56 |  | 0.00095729 |  | 40 | 10 | 15 | 500
2022-05-03 | 45.27 | 31.689 | 604.38 | 483.504 | 144.52 |  | 0.73 |  | 1.87 |  | 1.32 |  | 1.47 |  | 5.94 |  | 5.76 |  |  |  | 3 |  | 2.31 |  | 0.0010969 |  | 40 | 10 | 15 | 500
2022-05-04 | 50.58 | 35.406 | 594.73 | 475.784 | 158.4 |  | 0.8 |  | 2.55 |  | 1.9 |  | 0.37 |  | 5.58 |  | 4.23 |  |  |  | 3.11 |  | 2.42 |  | 0.00050111 |  | 40 | 10 | 15 | 500
2022-05-05 | 61.69 | 43.183 | 550.93 | 440.744 | 168.22 |  | 0.85 |  | 1.58 |  | 1.03 |  | 0.62 |  | 2.41 |  | 5.54 |  |  |  | 4.29 |  | 2.7 |  | 0.00073956 |  | 40 | 10 | 15 | 500
2022-05-06 | 60.07 | 42.049 | 431.44 |  | 152.1 |  | 0.9 |  | 1.45 |  | 1 |  | 0.94 |  | 3.14 |  | 4.2 |  |  |  | 3.41 |  | 2.27 |  | 0.00074841 |  | 40 | 10 | 15 | 500
2022-05-07 | 58.32 | 40.824 | 353.8 |  | 142.63 |  | 0.92 |  | 1.38 |  | 0.95 |  | 1.39 |  | 5.03 |  | 4.92 |  |  |  | 4.4 |  | 2.62 |  | 0.00038038 |  | 40 | 10 | 15 | 500
2022-05-08 | 58.61 | 41.027 | 357.72 |  | 141.01 |  | 1.04 |  | 2.07 |  | 1.27 |  | 1.54 |  | 6.63 |  | 6.2 |  |  |  | 5.48 |  | 3.13 |  | 0.00059615 |  | 40 | 10 | 15 | 500
2022-05-09 | 55.14 | 38.598 | 337.22 |  | 152.9 |  | 1.08 |  | 1.31 |  | 0.8 |  | 1.34 |  | 4.77 |  | 5.14 |  |  |  | 4.7 |  | 3.08 |  | 0.00076995 |  | 40 | 10 | 15 | 500
2022-05-10 | 57.61 | 40.327 | 325.01 |  | 152.14 |  | 1.04 |  | 1.07 |  | 0.68 |  | 0.49 |  | 5.37 |  | 2.37 |  |  |  | 2.82 |  | 2.3 |  | 0.0010469 |  | 40 | 10 | 15 | 500
2022-05-11 | 30.51 |  | 130.46 |  | 78.14 |  | 0.67 |  | 1.54 |  | 0.85 |  | 0.66 |  | 4.73 |  | 2.56 |  |  |  | 2.63 |  | 2.1 |  | 0.0012515 |  | 40 | 10 | 15 | 500
2022-05-12 | 35.4 |  | 292.08 |  | 111.71 |  | 0.78 |  | 1.37 |  | 1 |  | 1.03 |  | 5.14 |  | 6.01 |  |  |  | 2.81 |  | 2.32 |  | 0.00019308 |  | 40 | 10 | 15 | 500
2022-05-13 | 46.09 | 32.263 | 337.96 |  | 139.07 |  | 0.81 |  | 1.08 |  | 1 |  | 1.55 |  | 4.66 |  | 8.17 |  |  |  | 3.62 |  | 2.53 |  | 0.00040925 |  | 40 | 10 | 15 | 500
2022-05-14 | 41.07 | 28.749 | 291.54 |  | 114.74 |  | 0.64 |  | 0.91 |  | 0.82 |  | 1.75 |  | 3.81 |  | 6.45 |  |  |  | 3.87 |  | 2.81 |  | 0.00035589 |  | 40 | 10 | 15 | 500
2022-05-15 | 45.56 | 31.892 | 331.68 |  | 161.75 |  | 1.02 |  | 0.96 |  | 0.85 |  | 1.37 |  | 6.21 |  | 5.63 |  |  |  | 3.53 |  | 2.43 |  | 0.0009514 |  | 40 | 10 | 15 | 500
2022-05-16 | 33.27 |  | 215.55 |  | 111.24 |  | 0.8 |  | 1.01 |  | 0.87 |  | 1.09 |  | 7.8 |  | 5.56 |  |  |  | 3.38 |  | 2.18 |  | 0.0010497 |  | 40 | 10 | 15 | 500
2022-05-17 | 36.71 |  | 177.89 |  | 80.48 |  | 0.54 |  | 1.73 |  | 1.49 |  | 1.2 |  | 5.73 |  | 4.25 |  |  |  | 3.32 |  | 2.24 |  | 0.00085675 |  | 40 | 10 | 15 | 500
2022-05-18 | 43.45 | 30.415 | 295.22 |  | 109.43 |  | 0.65 |  | 1.06 |  | 0.99 |  | 1.3 |  | 2.87 |  | 5.51 |  |  |  | 2.72 |  | 2.04 |  | 0.0011074 |  | 40 | 10 | 15 | 500
2022-05-19 | 53.7 | 37.59 | 296.68 |  | 136.71 |  | 0.76 |  | 1.16 |  | 0.85 |  | 1.33 |  | 4.98 |  | 5.8 |  |  |  | 2.79 |  | 2.08 |  | 0.0010967 |  | 40 | 10 | 15 | 500
2022-05-20 | 29.29 |  | 192.09 |  | 106 |  | 0.63 |  | 1.4 |  | 1.1 |  | 1.13 |  | 4.07 |  | 5.33 |  |  |  | 2.76 |  | 2.09 |  | 0.00086482 |  | 40 | 10 | 15 | 500
2022-05-21 | 37.11 |  | 322.3 |  | 161 |  | 0.79 |  | 0.77 |  | 0.6 |  | 1.22 |  | 6.42 |  | 4.92 |  |  |  | 3.01 |  | 2.08 |  | 0.00042217 |  | 40 | 10 | 15 | 500
2022-05-22 | 48.68 | 34.076 | 288.53 |  | 178.58 |  | 0.99 |  | 1.64 |  | 1.32 |  | 1.05 |  | 6.68 |  | 5.18 |  |  |  | 3.28 |  | 2.24 |  | 0.0005192 |  | 40 | 10 | 15 | 500
2022-05-23 | 49.6 | 34.72 | 290.01 |  | 150.94 |  | 0.94 |  | 1.39 |  | 1.21 |  | 1.03 |  | 4.41 |  | 5.68 |  |  |  | 2.75 |  | 1.98 |  | 0.00047129 |  | 40 | 10 | 15 | 500
2022-05-24 | 47.13 | 32.991 | 301.91 |  | 145.04 |  | 0.98 |  | 1.41 |  | 1.33 |  | 0.83 |  | 3.27 |  | 3.94 |  |  |  | 2.28 |  | 2.1 |  | 0.00046687 |  | 40 | 10 | 15 | 500
2022-05-25 | 23.09 |  | 31.32 |  | 34.7 |  | 0.34 |  | 1.23 |  | 0.98 |  | 0.48 |  | 4.44 |  | 5.95 |  |  |  | 2.33 |  | 1.78 |  | 0.0008816 |  | 40 | 10 | 15 | 500
2022-05-26 | 40.37 | 28.259 | 258.46 |  | 128.52 |  | 0.83 |  | 1.11 |  | 0.92 |  | 0.8 |  | 2.58 |  | 5.82 |  |  |  | 2.7 |  | 2.15 |  | 0.00057605 |  | 40 | 10 | 15 | 500
2022-05-27 | 46.63 | 32.641 | 289.57 |  | 136.78 |  | 0.92 |  | 1.17 |  | 0.82 |  | 1.66 |  | 2.29 |  | 6.74 |  |  |  | 3.1 |  | 2.32 |  | 0.00041094 |  | 40 | 10 | 15 | 500
2022-05-28 | 48.44 | 33.908 | 203.81 |  | 100.04 |  | 0.95 |  | 1.47 |  | 1.05 |  | 1.73 |  | 1.25 |  | 8.38 |  |  |  | 3.48 |  | 2.49 |  | 0.00029245 |  | 40 | 10 | 15 | 500
2022-05-29 | 35.5 |  | 54.66 |  | 30.88 |  | 0.88 |  | 1.29 |  | 1 |  | 2.2 |  | 2.19 |  | 8.3 |  |  |  | 5.13 |  | 3.04 |  | 0.00085004 |  | 40 | 10 | 15 | 500
2022-05-30 | 20.35 |  | 37.27 |  | 52.36 |  | 0.63 |  | 1.64 |  | 1.26 |  | 1.82 |  | 4.22 |  | 9.19 |  |  |  | 4.13 |  | 2.65 |  | 0.026137 |  | 40 | 10 | 15 | 500
2022-05-31 | 43.98 | 30.786 | 264.94 |  | 140.87 |  | 0.85 |  | 1.19 |  | 0.91 |  | 2.2 |  | 3.97 |  | 3.8 |  |  |  | 4.2 |  | 2.74 |  | 0.030537 |  | 40 | 10 | 15 | 500
2022-06-01 | 37.3 |  | 257.26 |  | 134.36 |  | 0.73 |  | 1.31 |  | 1.09 |  | 2.13 |  | 4.01 |  | 1.22 |  |  |  | 3.58 |  | 2.44 |  | 0.015687 |  | 40 | 10 | 15 | 500
2022-06-02 | 24.3 |  | 147.61 |  | 90.64 |  | 0.64 |  | 1.49 |  | 1.16 |  | 2.07 |  | 3.99 |  | 1.08 |  |  |  | 4.27 |  | 2.43 |  | 0.025837 |  | 40 | 10 | 15 | 500
2022-06-03 | 36.1 |  | 281.51 |  | 140.76 |  | 0.76 |  | 2.25 |  | 2.08 |  | 1.89 |  | 6.38 |  | 1.09 |  |  |  | 5.54 |  | 2.87 |  | 0.018466 |  | 40 | 10 | 15 | 500
2022-06-04 | 35.16 |  | 236.63 |  | 132.94 |  | 0.81 |  | 1.7 |  | 1.23 |  | 1.94 |  | 6.6 |  | 1.17 |  |  |  | 5.07 |  | 2.94 |  | 0.019785 |  | 40 | 10 | 15 | 500
2022-06-05 | 44.04 | 30.828 | 254.81 |  | 139.17 |  | 0.92 |  | 1.78 |  | 1.44 |  | 1.77 |  | 9.25 |  | 1.24 |  |  |  | 4.5 |  | 2.68 |  | 0.0022914 |  | 40 | 10 | 15 | 500
2022-06-06 | 42.09 | 29.463 | 263.4 |  | 144.71 |  | 0.88 |  | 2.15 |  | 1.88 |  | 1.18 |  | 6.68 |  | 1.15 |  |  |  | 4.52 |  | 2.67 |  | 0.0022373 |  | 40 | 10 | 15 | 500
2022-06-07 | 38.21 |  | 250.85 |  | 138.48 |  | 0.96 |  | 2.18 |  | 1.65 |  | 1.87 |  | 7.71 |  | 1.13 |  |  |  | 4.55 |  | 2.49 |  | 0.0043732 |  | 40 | 10 | 15 | 500
2022-06-08 | 43.65 | 30.555 | 278.35 |  | 151.86 |  | 0.91 |  | 1.98 |  | 1.43 |  | 1.81 |  | 7 |  | 1.18 |  |  |  | 5.81 |  | 2.94 |  | 0.012105 |  | 40 | 10 | 15 | 500
2022-06-09 | 41.53 | 29.071 | 245.73 |  | 150.49 |  | 1.15 |  | 1.82 |  | 1.41 |  | 1.48 |  | 6.09 |  | 1.22 |  |  |  | 4.08 |  | 2.72 |  | 0.00089081 |  | 40 | 10 | 15 | 500
2022-06-10 | 44.5 | 31.15 | 238.77 |  | 159.15 |  | 1.41 |  | 1.75 |  | 1.33 |  | 1.56 |  | 4.92 |  | 1.17 |  | 4.7 |  | 3.86 |  | 2.49 |  | 0.0014627 |  | 40 | 10 | 15 | 500
2022-06-11 | 20.72 |  | 37.83 |  | 66.45 |  | 0.67 |  | 2.04 |  | 1.38 |  | 1.61 |  | 5.66 |  | 1.17 |  | 4.6 |  | 3.45 |  | 2.33 |  | 0.0012944 |  | 40 | 10 | 15 | 500
2022-06-12 | Extended Sinter Plant Maintenance Stop |  | Extended Sinter Plant Maintenance Stop |  | Extended Sinter Plant Maintenance Stop |  | Extended Sinter Plant Maintenance Stop |  | 1.79 |  | 0.85 |  | 1.85 |  | 6.43 |  | 1.18 |  | 6 |  | 3.85 |  | 2.49 |  | 0.00019398 |  | 40 | 10 | 15 | 500
2022-06-13 | [8 empty] | 1.92 |  | 0.8 |  | 2.25 |  | 5.52 |  | 1.2 |  | 5.37 |  | 3.78 |  | 2.65 |  | 0.00033534 |  | 40 | 10 | 15 | 500
2022-06-14 | [8 empty] | 1.64 |  | 0.72 |  | 2.06 |  | 5.7 |  | 1.16 |  | 6.33 |  | 4.03 |  | 2.36 |  | 0.00049743 |  | 40 | 10 | 15 | 500
2022-06-15 | [8 empty] | 2.17 |  | 0.85 |  | 2.76 |  | 4.23 |  | 1.15 |  | 3.5 |  | 3.37 |  | 2.16 |  | 0.00053863 |  | 40 | 10 | 15 | 500
2022-06-16 | [8 empty] | 1.35 |  | 0.59 |  | 2.34 |  | 2.12 |  | 1.07 |  | 4.42 |  | 2.85 |  | 2.12 |  | 0.021329 |  | 40 | 10 | 15 | 500
2022-06-17 | [8 empty] | 1.63 |  | 0.63 |  | 2.54 |  | 1.77 |  | 1.04 |  | 6.35 |  | 3.25 |  | 2.28 |  | 8.537e-05 |  | 40 | 10 | 15 | 500
2022-06-18 | [8 empty] | 1.79 |  | 0.75 |  | 2.04 |  | 4.31 |  | 1.23 |  | 4.85 |  | 3.23 |  | 2.3 |  | 0.00026564 |  | 40 | 10 | 15 | 500
2022-06-19 | [8 empty] | 2.64 |  | 1.08 |  | 2.18 |  | 8.42 |  | 1.13 |  | 12.15 |  | 4.29 |  | 2.59 |  | 0.00038048 |  | 40 | 10 | 15 | 500
2022-06-20 | [8 empty] | 2.7 |  | 1.07 |  | 2.18 |  | 4.14 |  | 1.07 |  | 8.96 |  | Abatement Form: Fume extraction A15 BOS 015_20 |  | 2.63 |  | 0.00013214 |  | 40 | 10 | 15 | 500
2022-06-21 | [8 empty] | 2.03 |  | 0.83 |  | 2.59 |  | 5.77 |  | 1.09 |  | 1.45 |  |  |  | 2.54 |  | 0.00028164 |  | 40 | 10 | 15 | 500
2022-06-22 | [8 empty] | 1.82 |  | 0.8 |  | 1.95 |  | 5.28 |  | 1.02 |  | 6.56 |  |  |  | 2.74 |  | 7.626e-05 |  | 40 | 10 | 15 | 500
2022-06-23 | [8 empty] | 2.17 |  | 0.75 |  | 1.61 |  | 5.98 |  | 3.93 |  | 10.56 |  | 2.06 |  | 2.87 |  | 3.498e-05 |  | 40 | 10 | 15 | 500
2022-06-24 | [8 empty] | 2.63 |  | 1.02 |  | 1.87 |  | 9.06 |  | 7.05 |  | 5.07 |  | 2.2 |  | 2.49 |  | 0.00054589 |  | 40 | 10 | 15 | 500
2022-06-25 | [8 empty] | 1.79 |  | 0.75 |  | 1.98 |  | 7.52 |  | 7.09 |  | 3.66 |  | 3.27 |  | 2.3 |  | 0.0010381 |  | 40 | 10 | 15 | 500
2022-06-26 | [8 empty] | 1.28 |  | 0.49 |  | 2.18 |  | 6.78 |  | 7.09 |  | 2.32 |  | 3.05 |  | 2.14 |  | 0.0013834 |  | 40 | 10 | 15 | 500
2022-06-27 | [8 empty] | 1.11 |  | 0.46 |  | 1.53 |  | 2.42 |  | 7.11 |  | 1.65 |  | 2.41 |  | 2.13 |  | 0.0007889 |  | 40 | 10 | 15 | 500
2022-06-28 | [8 empty] | 1.82 |  | 0.77 |  | 1.49 |  | 1.7 |  | 7.06 |  | 2.05 |  | 1.95 |  | 1.68 |  | 0.0032649 |  | 40 | 10 | 15 | 500
2022-06-29 | 24.85 |  | 107.44 |  | 71.15 |  | 0.85 |  | 2.89 |  | 0.4 |  | 1.8 |  | 0.7 |  | 7.03 |  | 0.61 |  | 1.26 |  | 1.21 |  | 0.0018155 |  | 40 | 10 | 15 | 500
2022-06-30 | 26.66 |  | 219.67 |  | 121.28 |  | 0.64 |  | 1.83 |  | 0.4 |  | 1.69 |  | 1.46 |  | 7.05 |  | 1.98 |  | 2.12 |  | 1.87 |  | 0.00058705 |  | 40 | 10 | 15 | 500
Formulas:
Source = [Source, row above]+7
Note on C6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sinter Plant Maintenance Stop during 1st April
Note on W31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Abatement Form: Fume extraction 14/15/16 BOS 002_15/04/22
Note on Y31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Abatement Form: Fume extraction 14/15/16 BOS 002_15/04/22
Note on D40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Monthly Part A for Particulate Breaches for May 2022 - Reference: S5N_22_49A
Note on E60: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sinter Plant Maintenance Stop during 25th May
Note on E63: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: A1 Sinter Plant SO2 & NOX Monitor 003_280422
Note on G63: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: A1 Sinter Plant SO2 & NOX Monitor 003_280422
Note on S66: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Monitor probe change