## Notes
Reference conditions
All concentrations in this spreadsheet are reported in dry air at a temperature of 273K, at a pressure of 101.3 kPa and with an oxygen content of 3% dry
Uncertainty
Concentrations in this spreadsheet are reported after having subtracted the value of the 95% confidence interval (see Section 3.6.7 of the permit):
95% confidence interval for nitrogen oxides is taken to be 20%
95% confidence interval for sulphur dioxide is taken to be 20%
95% confidence interval for dust is taken to be 30%
95% confidence interval for carbon monoxide is taken to be 10%
Normal operating conditions
The document "Power Plant Boiler Abnormal Conditions" sets out the criteria for excluding emissions monitoring data from permitting or other reporting obligations:
| Parameter | Plant | Level representing abnormal conditions
| Boiler oxygen | All boilers | >17% oxygen
| Fuel input | A51, A52A, A52B, A53 and A62 | <50% BFG by thermal input
|  | A50 (Service Boilers) | <35% BFG by thermal input

## A50 Service Boilers
|  | Concentrations in mg/m³ at reference conditions after subtracting uncertainty | [9 empty] | Daily means, excluding hours outside normal operating conditions
|  | 2021-10-01 |  |  | 2021-11-01 |  |  | 2021-12-01 |  |  | Date | Fuel mix |  |  |  |  | Particulate Matter concentration (mg/m³) after subtracting uncertainty |  |  |  |  | Sulphur dioxide concentration (mg/m³) after subtracting uncertainty |  |  |  |  | Oxides of nitrogen concentration (mg/m³) after subtracting uncertainty
|  | PM | SO2 | NOx | PM | SO2 | NOx | PM | SO2 | NOx |  | % BFG | % COG | % BOSg | % NG | % HFO | No.valid hours | No.hours OTNOC | Measured | Limit | Breach? | No.valid hours | No.hours OTNOC | Measured | Limit | Breach? | No.valid hours | No.hours OTNOC | Measured | Limit | Breach?
Daily means | Minimum | 0 | 0 | 0 | 0.70948 | 46.5057 | 74.442 | 0 | 0 | 0 | 2021-10-01 | 65.78% | 13.92% |  | 20.3% |  | 24 | 0 | 0.90437 | 12.9461 | NO | 24 | 0 | 89.863 | 213.7858 | NO | 24 | 0 | 92.9512 | 285.3477 | NO
| Maximum | 2.4772 | 312.0872 | 168.4414 | 1.4358 | 209.4331 | 154.0527 | 1.6482 | 304.1052 | 155.3336 | 2021-10-02 | 65.17% | 14.64% |  | 20.19% |  | 24 | 0 | 0.83453 | 13.1112 | NO | 24 | 0 | 74.4172 | 215.5718 | NO | 24 | 0 | 102.224 | 285.5817 | NO
| No. > Limit | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2021-10-03 | 64.59% | 15.37% |  | 20.04% |  | 24 | 0 | 0.84115 | 13.2782 | NO | 24 | 0 | 103.5407 | 217.4297 | NO | 24 | 0 | 65.1031 | 285.9089 | NO
Monthly mean |  | 1.0675 | 120.0455 | 111.3094 | 0.97219 | 96.0141 | 103.0108 | 0.98631 | 99.8875 | 108.9131 | 2021-10-04 | 54.88% | 23.15% |  | 21.97% |  | 24 | 3 | 0.80647 | 14.8846 | NO | 24 | 3 | 70.224 | 231.0577 | NO | 24 | 3 | 78.4488 | 281.6725 | NO
Monthly mean limit |  | 14.9663 | 223.7434 | 254.9216 | 13.3558 | 206.8689 | 253.5834 | 13.9729 | 203.7506 | 237.4285 | 2021-10-05 | 17.96% | 59.37% |  | 22.67% |  | 24 | 22 | 0.8748 | 22.8136 | NO | 24 | 22 | 227.9881 | 309.4536 | NO | 24 | 22 | 84.0826 | 280.1174 | NO
[11 empty] | 2021-10-06 | 8.002% | 50.32% |  | 41.68% |  | 24 | 24 | 0 | 19.7768 | NO | 24 | 24 | 0 | 255.0394 | NO | 24 | 24 | 0 | 238.2975 | NO
[11 empty] | 2021-10-07 | 27.04% | 48.49% |  | 24.47% |  | 24 | 23 | 0.95075 | 20.3227 | NO | 24 | 23 | 274.8072 | 282.2774 | NO | 24 | 23 | 168.4414 | 276.1753 | NO
[11 empty] | 2021-10-08 | 32.05% | 49.45% |  | 18.5% |  | 24 | 15 | 2.4772 | 20.8607 | NO | 24 | 15 | 312.0872 | 295.203 | YES | 24 | 15 | 165.3331 | 289.2981 | NO
[11 empty] | 2021-10-09 | 30% | 51.64% |  | 18.36% |  | 24 | 15 | 0.93907 | 21.3501 | NO | 24 | 15 | 230.472 | 300.2712 | NO | 24 | 15 | 123.164 | 289.6008 | NO
[11 empty] | 2021-10-10 | 41.04% | 37.37% |  | 21.59% |  | 24 | 7 | 0.83945 | 18.0329 | NO | 24 | 7 | 178.8984 | 263.0163 | NO | 24 | 7 | 135.5314 | 282.4997 | NO
[11 empty] | 2021-10-11 | 37.68% | 37.4% |  | 24.92% |  | 24 | 7 | 0.83572 | 17.8581 | NO | 24 | 7 | 180.2577 | 257.0606 | NO | 24 | 7 | 104.7835 | 275.1816 | NO
[11 empty] | 2021-10-12 | 50.41% | 24.54% |  | 25.05% |  | 24 | 2 | 0.83834 | 15.0213 | NO | 24 | 2 | 119.5434 | 228.5242 | NO | 24 | 2 | 104.4485 | 274.8883 | NO
[11 empty] | 2021-10-13 | 48.86% | 26.41% |  | 24.73% |  | 24 | 0 | 1.2059 | 15.4502 | NO | 24 | 0 | 115.5188 | 233.2232 | NO | 24 | 0 | 106.6827 | 275.6019 | NO
[11 empty] | 2021-10-14 | 31.11% | 43.21% |  | 25.68% |  | 24 | 20 | 0.90348 | 19.0929 | NO | 24 | 20 | 183.2311 | 268.4442 | NO | 24 | 20 | 127.2382 | 273.5045 | NO
[11 empty] | 2021-10-15 | 29.19% | 47.15% |  | 23.66% |  | 24 | 14 | 1.6642 | 20.0709 | NO | 24 | 14 | 132.1255 | 280.7761 | NO | 24 | 14 | 126.4989 | 277.943 | NO
[11 empty] | 2021-10-16 | 41.74% | 40.15% |  | 18.11% |  | 24 | 0 | 1.8436 | 18.8369 | NO | 24 | 0 | 183.4457 | 275.4586 | NO | 24 | 0 | 137.2574 | 290.1566 | NO
[11 empty] | 2021-10-17 | 42.31% | 40.6% |  | 17.09% |  | 24 | 0 | 1.8532 | 18.9923 | NO | 24 | 0 | 204.0014 | 278.3038 | NO | 24 | 0 | 131.123 | 292.4008 | NO
[11 empty] | 2021-10-18 | 51.08% | 30.43% |  | 18.5% |  | 24 | 0 | 1.2427 | 16.6762 | NO | 24 | 0 | 126.7102 | 253.3624 | NO | 24 | 0 | 144.2728 | 289.3049 | NO
[11 empty] | 2021-10-19 | 62.72% | 15.27% |  | 22.01% |  | 24 | 0 | 0.95505 | 13.1499 | NO | 24 | 0 | 67.1618 | 213.6602 | NO | 24 | 0 | 106.9066 | 281.5845 | NO
[11 empty] | 2021-10-20 | 63.71% | 16.4% |  | 19.89% |  | 24 | 0 | 0.77069 | 13.5139 | NO | 24 | 0 | 52.7388 | 219.9755 | NO | 24 | 0 | 95.2777 | 286.2381 | NO
[11 empty] | 2021-10-21 | 41.74% | 40.72% |  | 17.54% |  | 24 | 0 | 1.088 | 18.9944 | NO | 24 | 0 | 184.9346 | 277.7603 | NO | 24 | 0 | 144.2644 | 291.4201 | NO
[11 empty] | 2021-10-22 | 67.64% | 11.32% |  | 21.03% |  | 24 | 0 | 0.86208 | 12.3341 | NO | 24 | 0 | 146.8772 | 206.734 | NO | 24 | 0 | 98.2458 | 283.7264 | NO
[11 empty] | 2021-10-23 | 68.61% | 10.59% |  | 20.8% |  | 24 | 0 | 0.88485 | 12.1869 | NO | 24 | 0 | 55.8781 | 205.5576 | NO | 24 | 0 | 102.1354 | 284.2415 | NO
[11 empty] | 2021-10-24 | 69.66% | 11.73% |  | 18.61% |  | 24 | 0 | 1.043 | 12.5565 | NO | 24 | 0 | 66.9572 | 212.0214 | NO | 24 | 0 | 101.4766 | 289.0543 | NO
[11 empty] | 2021-10-25 | 50.29% | 25.41% |  | 24.3% |  | 24 | 6 | 0.88493 | 15.2538 | NO | 24 | 6 | 99.2174 | 231.8001 | NO | 24 | 6 | 108.4566 | 276.5434 | NO
[11 empty] | 2021-10-26 | 46.61% | 31.95% |  | 21.44% |  | 24 | 8 | 0.85987 | 16.8488 | NO | 24 | 8 | 144.9128 | 251.3619 | NO | 24 | 8 | 103.9595 | 282.8245 | NO
[11 empty] | 2021-10-27 | 57.41% | 18.33% |  | 24.26% |  | 24 | 0 | 1.0627 | 13.6983 | NO | 24 | 0 | 72.6591 | 216.2962 | NO | 24 | 0 | 118.2792 | 276.6325 | NO
[11 empty] | 2021-10-28 | 53.93% | 20.22% |  | 25.84% |  | 24 | 0 | 1.1184 | 14.0279 | NO | 24 | 0 | 67.422 | 217.5856 | NO | 24 | 0 | 115.3367 | 273.1424 | NO
[11 empty] | 2021-10-29 | 49.24% | 26.54% |  | 24.22% |  | 24 | 0 | 1.0703 | 15.5062 | NO | 24 | 0 | 154.254 | 234.4251 | NO | 24 | 0 | 94.7226 | 276.7179 | NO
[11 empty] | 2021-10-30 | 41.93% | 34.11% |  | 23.96% |  | 24 | 4 | 1.0189 | 17.186 | NO | 24 | 4 | 101.54 | 251.551 | NO | 24 | 4 | 124.6656 | 277.2895 | NO
[11 empty] | 2021-10-31 | 44.42% | 28.28% |  | 27.3% |  | 24 | 6 | 0.93262 | 15.7201 | NO | 24 | 6 | 98.8404 | 232.6612 | NO | 24 | 6 | 123.7192 | 269.9316 | NO
[11 empty] | 2021-11-01 | 29.17% | 20.97% |  | 49.86% |  | 24 | 17 | 1.0023 | 12.8712 | NO | 24 | 17 | 60.9954 | 175.6386 | NO | 24 | 17 | 107.547 | 220.3074 | NO
[11 empty] | 2021-11-02 | 31.2% | 14.87% |  | 53.94% |  | 24 | 21 | 1.1956 | 11.3037 | NO | 24 | 21 | 51.6225 | 154.8055 | NO | 24 | 21 | 74.442 | 211.3361 | NO
[11 empty] | 2021-11-03 | 50.38% | 19.7% |  | 29.92% |  | 24 | 0 | 1.0908 | 13.689 | NO | 24 | 0 | 62.85 | 209.0454 | NO | 24 | 0 | 87.6563 | 264.1829 | NO
[11 empty] | 2021-11-04 | 61.43% | 14.69% |  | 23.88% |  | 24 | 0 | 1.0257 | 12.9182 | NO | 24 | 0 | 101.4116 | 208.977 | NO | 24 | 0 | 89.4545 | 277.469 | NO
[11 empty] | 2021-11-05 | 60.93% | 17.71% |  | 21.36% |  | 24 | 0 | 0.86411 | 13.7203 | NO | 24 | 0 | 72.0749 | 220.1828 | NO | 24 | 0 | 76.369 | 283.0078 | NO
[11 empty] | 2021-11-06 | 59.73% | 18.08% |  | 22.19% |  | 24 | 0 | 0.94594 | 13.7572 | NO | 24 | 0 | 54.1753 | 219.5041 | NO | 24 | 0 | 85.8958 | 281.1866 | NO
[11 empty] | 2021-11-07 | 63.82% | 15.83% |  | 20.35% |  | 24 | 0 | 0.86614 | 13.3635 | NO | 24 | 0 | 79.7087 | 217.889 | NO | 24 | 0 | 108.484 | 285.2248 | NO
[11 empty] | 2021-11-08 | 34.93% | 43.01% |  | 22.06% |  | 24 | 13 | 0.98502 | 19.2494 | NO | 24 | 13 | 63.2431 | 274.5911 | NO | 24 | 13 | 90.6638 | 281.4725 | NO
[11 empty] | 2021-11-09 | 39.37% | 41.49% |  | 19.14% |  | 24 | 4 | 0.8367 | 19.0747 | NO | 24 | 4 | 191.4321 | 276.5301 | NO | 24 | 4 | 154.0527 | 287.8828 | NO
[11 empty] | 2021-11-10 | 41.99% | 42.9% |  | 15.11% |  | 24 | 14 | 0.70948 | 19.6061 | NO | 24 | 14 | 64.7501 | 286.945 | NO | 24 | 14 | 108.871 | 296.7544 | NO
[11 empty] | 2021-11-11 | 64.12% | 16.07% |  | 19.81% |  | 24 | 0 | 0.75478 | 13.4465 | NO | 24 | 0 | 61.7308 | 219.407 | NO | 24 | 0 | 104.9402 | 286.4206 | NO
[11 empty] | 2021-11-12 | 53.89% | 26.26% |  | 19.85% |  | 24 | 0 | 0.80345 | 15.6856 | NO | 24 | 0 | 164.9668 | 241.7458 | NO | 24 | 0 | 118.9084 | 286.3293 | NO
[11 empty] | 2021-11-13 | 55.93% | 20.64% |  | 23.43% |  | 24 | 0 | 0.92635 | 14.2515 | NO | 24 | 0 | 73.6646 | 222.872 | NO | 24 | 0 | 114.6924 | 278.4463 | NO
[11 empty] | 2021-11-14 | 52.79% | 24.3% |  | 22.91% |  | 24 | 0 | 0.86436 | 15.0865 | NO | 24 | 0 | 119.4094 | 231.8866 | NO | 24 | 0 | 109.4411 | 279.6022 | NO
[11 empty] | 2021-11-15 | 56.9% | 18.93% |  | 24.16% |  | 24 | 0 | 1.0425 | 13.8358 | NO | 24 | 0 | 104.5981 | 217.7904 | NO | 24 | 0 | 121.9011 | 276.8386 | NO
[11 empty] | 2021-11-16 | 59.26% | 16.27% |  | 24.47% |  | 24 | 0 | 0.93137 | 13.2347 | NO | 24 | 0 | 93.472 | 211.394 | NO | 24 | 0 | 99.021 | 276.1694 | NO
[11 empty] | 2021-11-17 | 59.75% | 15.45% |  | 24.81% |  | 24 | 0 | 0.9739 | 13.0346 | NO | 24 | 0 | 62.0184 | 208.9674 | NO | 24 | 0 | 101.5278 | 275.4289 | NO
[11 empty] | 2021-11-18 | 27.27% | 38.17% |  | 34.56% |  | 24 | 14 | 0.87028 | 17.4973 | NO | 24 | 14 | 84.6389 | 241.2613 | NO | 24 | 14 | 110.4864 | 253.9789 | NO
[11 empty] | 2021-11-19 | 59.66% | 18.4% |  | 21.95% |  | 24 | 0 | 0.86129 | 13.8405 | NO | 24 | 0 | 71.5451 | 220.6431 | NO | 24 | 0 | 108.5975 | 281.7178 | NO
[11 empty] | 2021-11-20 | 62.3% | 16.23% |  | 21.47% |  | 24 | 0 | 0.90067 | 13.3896 | NO | 24 | 0 | 62.8807 | 216.7368 | NO | 24 | 0 | 100.3566 | 282.7661 | NO
[11 empty] | 2021-11-21 | 66.32% | 14.24% |  | 19.43% |  | 24 | 0 | 1.0388 | 13.0651 | NO | 24 | 0 | 52.0837 | 216.0694 | NO | 24 | 0 | 89.8055 | 287.2499 | NO
[11 empty] | 2021-11-22 | 68.29% | 13.27% |  | 18.45% |  | 24 | 0 | 0.94393 | 12.9047 | NO | 24 | 0 | 87.3194 | 215.714 | NO | 24 | 0 | 77.2878 | 289.4206 | NO
[11 empty] | 2021-11-23 | 63.34% | 15.42% |  | 21.25% |  | 24 | 0 | 0.85162 | 13.2237 | NO | 24 | 0 | 46.5057 | 215.3613 | NO | 24 | 0 | 78.0483 | 283.2603 | NO
[11 empty] | 2021-11-24 | 63.42% | 20.5% |  | 16.08% |  | 24 | 0 | 0.98178 | 14.626 | NO | 24 | 0 | 105.2497 | 235.923 | NO | 24 | 0 | 103.1608 | 294.6314 | NO
[11 empty] | 2021-11-25 | 58.31% | 28.64% |  | 13.04% |  | 24 | 0 | 1.2355 | 16.5842 | NO | 24 | 0 | 126.562 | 259.342 | NO | 24 | 0 | 122.8609 | 301.3042 | NO
[11 empty] | 2021-11-26 | 53.85% | 29.01% |  | 17.14% |  | 24 | 0 | 1.4358 | 16.4401 | NO | 24 | 0 | 146.1912 | 252.7179 | NO | 24 | 0 | 107.4206 | 292.2896 | NO
[11 empty] | 2021-11-27 | 43.12% | 38.26% |  | 18.62% |  | 24 | 9 | 1.3602 | 18.3926 | NO | 24 | 9 | 209.4331 | 270.3694 | NO | 24 | 9 | 112.5904 | 289.0319 | NO
[11 empty] | 2021-11-28 | 66.96% | 15.41% |  | 17.62% |  | 24 | 0 | 1.1308 | 13.422 | NO | 24 | 0 | 201.8563 | 221.9275 | NO | 24 | 0 | 110.6389 | 291.2303 | NO
[11 empty] | 2021-11-29 | 64.08% | 16.97% |  | 18.95% |  | 24 | 0 | 0.89637 | 13.6907 | NO | 24 | 0 | 66.945 | 222.9306 | NO | 24 | 0 | 86.0196 | 288.3011 | NO
[11 empty] | 2021-11-30 | 53.81% | 25.74% |  | 20.45% |  | 24 | 0 | 0.9741 | 15.5373 | NO | 24 | 0 | 89.251 | 239.5044 | NO | 24 | 0 | 120.5897 | 285.0108 | NO
[11 empty] | 2021-12-01 | 56.66% | 26.76% |  | 16.58% |  | 24 | 1 | 1.0229 | 15.974 | NO | 24 | 1 | 113.5964 | 248.7604 | NO | 24 | 1 | 120.8467 | 293.5144 | NO
[11 empty] | 2021-12-02 | 49.08% | 36.13% |  | 14.79% |  | 24 | 0 | 1.0162 | 18.1361 | NO | 24 | 0 | 162.6619 | 272.653 | NO | 24 | 0 | 106.5738 | 297.4649 | NO
[11 empty] | 2021-12-03 | 69.75% | 13.04% |  | 17.21% |  | 24 | 0 | 0.72161 | 12.9222 | NO | 24 | 0 | 57.5668 | 217.4543 | NO | 24 | 0 | 75.0249 | 292.1432 | NO
[11 empty] | 2021-12-04 | 69.91% | 12.63% |  | 17.46% |  | 24 | 0 | 0.96422 | 12.8191 | NO | 24 | 0 | 38.016 | 216.1091 | NO | 24 | 0 | 79.8141 | 291.5967 | NO
[11 empty] | 2021-12-05 | 69.75% | 12.58% |  | 17.67% |  | 24 | 0 | 1.0033 | 12.7956 | NO | 24 | 0 | 92.7379 | 215.5995 | NO | 24 | 0 | 74.089 | 291.1185 | NO
[11 empty] | 2021-12-06 | 44.19% | 27.06% |  | 28.75% |  | 24 | 8 | 1.0246 | 15.3708 | NO | 24 | 8 | 71.6296 | 227.3338 | NO | 24 | 8 | 88.8424 | 266.7401 | NO
[11 empty] | 2021-12-07 | 37.72% | 3.405% |  | 58.88% |  | 24 | 3 | 1.3329 | 8.5108 | NO | 24 | 3 | 30.5214 | 120.6281 | NO | 24 | 3 | 124.5441 | 200.4694 | NO
[11 empty] | 2021-12-08 | 35.88% | 7.432% |  | 56.69% |  | 24 | 4 | 1.6257 | 9.5173 | NO | 24 | 4 | 27.2262 | 133.4642 | NO | 24 | 4 | 155.3336 | 205.2899 | NO
[11 empty] | 2021-12-09 | 34.36% | 13.15% |  | 52.49% |  | 24 | 19 | 1.6482 | 11.006 | NO | 24 | 19 | 19.3228 | 153.6557 | NO | 24 | 19 | 109.7987 | 214.5147 | NO
[11 empty] | 2021-12-10 | 34.88% | 15.04% |  | 50.08% |  | 24 | 10 | 1.5555 | 11.555 | NO | 24 | 10 | 23.8452 | 162.1974 | NO | 24 | 10 | 113.8693 | 219.822 | NO
[11 empty] | 2021-12-11 | 32.24% | 17.91% |  | 49.85% |  | 24 | 24 | 0 | 12.1981 | NO | 24 | 24 | 0 | 168.9242 | NO | 24 | 24 | 0 | 220.3352 | NO
[11 empty] | 2021-12-12 | 38.08% | 22.04% |  | 39.89% |  | 24 | 12 | 0.87565 | 13.6542 | NO | 24 | 12 | 138.0283 | 196.0839 | NO | 24 | 12 | 127.0453 | 242.2468 | NO
[11 empty] | 2021-12-13 | 45.55% | 15.46% |  | 38.99% |  | 24 | 4 | 0.88503 | 12.2562 | NO | 24 | 4 | 143.0882 | 183.2364 | NO | 24 | 4 | 120.1121 | 244.2167 | NO
[11 empty] | 2021-12-14 | 32.38% | 23.25% |  | 44.37% |  | 24 | 21 | 1.0651 | 13.6751 | NO | 24 | 21 | 56.4053 | 190.6244 | NO | 24 | 21 | 93.9359 | 232.3888 | NO
[11 empty] | 2021-12-15 | 25.32% | 45% |  | 29.68% |  | 24 | 12 | 0.96755 | 19.2669 | NO | 24 | 12 | 64.6333 | 265.1209 | NO | 24 | 12 | 92.0602 | 264.6985 | NO
[11 empty] | 2021-12-16 | 1.374% | 52.93% |  | 45.7% |  | 24 | 24 | 0 | 20.1315 | NO | 24 | 24 | 0 | 253.5102 | NO | 24 | 24 | 0 | 229.4705 | NO
[11 empty] | 2021-12-17 | 5.439% | 59.79% |  | 34.77% |  | 24 | 24 | 0 | 22.2424 | NO | 24 | 24 | 0 | 288.4427 | NO | 24 | 24 | 0 | 253.5109 | NO
[11 empty] | 2021-12-18 | 40.63% | 40.95% |  | 18.42% |  | 24 | 0 | 0.87017 | 18.9965 | NO | 24 | 0 | 304.1052 | 276.6684 | YES | 24 | 0 | 134.6509 | 289.4842 | NO
[11 empty] | 2021-12-19 | 26.75% | 56.21% |  | 17.03% |  | 24 | 19 | 0.96933 | 22.4302 | NO | 24 | 19 | 154.0035 | 312.7569 | NO | 24 | 19 | 128.4153 | 292.5296 | NO
[11 empty] | 2021-12-20 | 16.01% | 50.64% |  | 33.35% |  | 24 | 19 | 0.98203 | 20.3073 | NO | 24 | 19 | 62.2202 | 270.8892 | NO | 24 | 19 | 152.4664 | 256.6363 | NO
[11 empty] | 2021-12-21 | 43.99% | 35.07% |  | 20.94% |  | 24 | 3 | 0.8695 | 17.5631 | NO | 24 | 3 | 172.8749 | 259.1381 | NO | 24 | 3 | 110.294 | 283.925 | NO
[11 empty] | 2021-12-22 | 47.76% | 32.39% |  | 19.86% |  | 24 | 3 | 1.1275 | 17.0333 | NO | 24 | 3 | 46.4216 | 255.2161 | NO | 24 | 3 | 102.0019 | 286.3187 | NO
[11 empty] | 2021-12-23 | 48.93% | 27.62% |  | 23.45% |  | 24 | 0 | 0.91083 | 15.7861 | NO | 24 | 0 | 105.5818 | 238.1958 | NO | 24 | 0 | 114.4847 | 278.4075 | NO
[11 empty] | 2021-12-24 | 48.45% | 25.1% |  | 26.45% |  | 24 | 0 | 0.83258 | 15.0676 | NO | 24 | 0 | 82.841 | 227.2212 | NO | 24 | 0 | 128.9914 | 271.817 | NO
[11 empty] | 2021-12-25 | 50.2% | 24.48% |  | 25.32% |  | 24 | 0 | 0.85366 | 14.9942 | NO | 24 | 0 | 109.9449 | 227.9166 | NO | 24 | 0 | 115.9789 | 274.3045 | NO
[11 empty] | 2021-12-26 | 41.05% | 29.05% |  | 29.9% |  | 24 | 3 | 0.8479 | 15.7455 | NO | 24 | 3 | 120.4653 | 229.6273 | NO | 24 | 3 | 100.0739 | 264.213 | NO
[11 empty] | 2021-12-27 | 40.52% | 28.73% |  | 30.75% |  | 24 | 0 | 0.83904 | 15.6289 | NO | 24 | 0 | 65.9631 | 227.3897 | NO | 24 | 0 | 137.8482 | 262.3487 | NO
[11 empty] | 2021-12-28 | 35.78% | 34.64% |  | 29.58% |  | 24 | 6 | 1.0257 | 16.9938 | NO | 24 | 6 | 157.3639 | 242.5133 | NO | 24 | 6 | 90.643 | 264.9142 | NO
[11 empty] | 2021-12-29 | 44.2% | 29.6% |  | 26.19% |  | 24 | 8 | 0.82026 | 16.0718 | NO | 24 | 8 | 130.6358 | 237.5831 | NO | 24 | 8 | 83.1881 | 272.3733 | NO
[11 empty] | 2021-12-30 | 64.02% | 12.49% |  | 23.49% |  | 24 | 0 | 0.80943 | 12.4568 | NO | 24 | 0 | 67.7466 | 204.8558 | NO | 24 | 0 | 99.554 | 278.3265 | NO
[11 empty] | 2021-12-31 | 64.2% | 13.62% |  | 22.17% |  | 24 | 0 | 0 | 12.7774 | NO | 24 | 0 | 65.5579 | 209.7238 | NO | 24 | 0 | 99.7316 | 281.2178 | NO
Note on E7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Part A S5N_21_56A
Note on K7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Part A - S5N_21_74A

## A51 Boiler 5
|  | Concentrations in mg/m³ at reference conditions after subtracting uncertainty | [9 empty] | Daily means, excluding hours outside normal operating conditions
|  | 2021-10-01 |  |  | 2021-11-01 |  |  | 2021-12-01 |  |  | Date | Fuel mix |  |  |  |  | Particulate Matter concentration (mg/m³) after subtracting uncertainty
|  | PM | SO2 | NOx | PM | SO2 | NOx | PM | SO2 | NOx |  | % BFG | % COG | % BOSg | % NG | % HFO | No.valid hours | No.hours OTNOC | Measured | Limit | Breach?
Daily means | Minimum | 0.49066 | Discontinuous monitoring only |  | 0.69829 | Discontinuous monitoring only |  | 0.90026 | Discontinuous monitoring only |  | 2021-10-01 | 88.14% | 6.28% | 0% | 5.59% | 0% | 24 | 0 | 0.69659 | 12.3472 | NO
| Maximum | 4.2083 |  |  | 6.7097 |  |  | 5.811 |  |  | 2021-10-02 | 89.43% | 9.25% | 0% | 1.32% | 0% | 24 | 0 | 0.74712 | 13.3245 | NO
| No. > Limit | 0 |  |  | 0 |  |  | 0 |  |  | 2021-10-03 | 88.32% | 10.45% | 0% | 1.23% | 0% | 24 | 0 | 0.75971 | 13.6383 | NO
Monthly mean |  | 0.97595 |  |  | 1.1483 |  |  | 1.2419 |  |  | 2021-10-04 | 87.69% | 10.97% | 0% | 1.34% | 0% | 24 | 0 | 0.85249 | 15.759 | NO
Monthly mean limit |  | 13.2855 |  |  | 13.621 |  |  | 12.3432 |  |  | 2021-10-05 | 86.24% | 12.45% | 0% | 1.31% | 0% | 24 | 0 | 0.82449 | 15.0042 | NO
[11 empty] | 2021-10-06 | 48.41% | 17.92% | 0% | 16.15% | 17.52% | 24 | 11 | 1.6651 | 24.1913 | NO
[11 empty] | 2021-10-07 | 79.41% | 13.17% | 0% | 4.13% | 3.29% | 24 | 2 | 2.146 | 15.5435 | NO
[11 empty] | 2021-10-08 | 87.45% | 11.34% | 0% | 1.21% | 0% | 24 | 0 | 0.77367 | 13.7373 | NO
[11 empty] | 2021-10-09 | 87.51% | 11.29% | 0% | 1.2% | 0% | 24 | 0 | 0.49066 | 13.7723 | NO
[11 empty] | 2021-10-10 | 86.66% | 12.14% | 0% | 1.2% | 0% | 24 | 0 | 0.52255 | 14.1108 | NO
[11 empty] | 2021-10-11 | 80.54% | 18.31% | 0% | 1.15% | 0% | 24 | 0 | 0.6271 | 15.6407 | NO
[11 empty] | 2021-10-12 | 82.58% | 16.45% | 0% | 0.97% | 0% | 24 | 0 | 0.57428 | 15.1754 | NO
[11 empty] | 2021-10-13 | 84.08% | 14.92% | 0% | 1% | 0% | 24 | 0 | 0.54309 | 14.7888 | NO
[11 empty] | 2021-10-14 | 53.54% | 21.05% | 0% | 15.81% | 9.6% | 24 | 5 | 4.2083 | 19.3127 | NO
[11 empty] | 2021-10-15 | 81.26% | 12.8% | 0% | 5.94% | 0% | 24 | 0 | 1.1113 | 13.9147 | NO
[11 empty] | 2021-10-16 | 89.98% | 8.86% | 0% | 1.15% | 0% | 24 | 0 | 1.2568 | 13.3977 | NO
[11 empty] | 2021-10-17 | 89.58% | 9.31% | 0% | 1.12% | 0% | 24 | 0 | 0.64892 | 13.5121 | NO
[11 empty] | 2021-10-18 | 90.15% | 8.71% | 0% | 1.14% | 0% | 24 | 0 | 0.76839 | 13.5284 | NO
[11 empty] | 2021-10-19 | 90.67% | 8.16% | 0% | 1.17% | 0% | 24 | 0 | 0.89711 | 13.4767 | NO
[11 empty] | 2021-10-20 | 89.12% | 2.75% | 0% | 8.13% | 0% | 24 | 0 | 0.87015 | 11.6232 | NO
[11 empty] | 2021-10-21 | 86.37% | 10.22% | 0% | 3.41% | 0% | 24 | 0 | 0.9613 | 13.6965 | NO
[11 empty] | 2021-10-22 | 87.69% | 11.21% | 0% | 1.1% | 0% | 24 | 0 | 1.1704 | 14.056 | NO
[11 empty] | 2021-10-23 | 87.64% | 11.27% | 0% | 1.09% | 0% | 24 | 0 | 1.1686 | 13.9136 | NO
[11 empty] | 2021-10-24 | 85.68% | 13.05% | 0% | 1.27% | 0% | 24 | 0 | 1.0524 | 14.418 | NO
[11 empty] | 2021-10-25 | 86.45% | 12.41% | 0% | 1.14% | 0% | 24 | 0 | 0.87642 | 14.3856 | NO
[11 empty] | 2021-10-26 | 86.07% | 12.72% | 0% | 1.21% | 0% | 24 | 0 | 0.93299 | 14.2262 | NO
[11 empty] | 2021-10-27 | 88.81% | 10.13% | 0% | 1.07% | 0% | 24 | 0 | 0.78117 | 13.7499 | NO
[11 empty] | 2021-10-28 | 89.23% | 9.7% | 0% | 1.06% | 0% | 24 | 0 | 0.77933 | 13.6245 | NO
[11 empty] | 2021-10-29 | 88.06% | 10.94% | 0% | 1% | 0% | 24 | 0 | 0.82657 | 14.0586 | NO
[11 empty] | 2021-10-30 | 88.11% | 10.86% | 0% | 1.03% | 0% | 24 | 0 | 0.83061 | 13.9382 | NO
[11 empty] | 2021-10-31 | 70.57% | 12.04% | 0% | 9.28% | 8.11% | 24 | 5 | 0.97792 | 17.1696 | NO
[11 empty] | 2021-11-01 | 71.55% | 12.89% | 0% | 7.938% | 7.63% | 24 | 4 | 2.4408 | 17.5369 | NO
[11 empty] | 2021-11-02 | 87.95% | 11.06% | 0% | 0.9928% | 0% | 24 | 0 | 1.6561 | 14.2209 | NO
[11 empty] | 2021-11-03 | 88.37% | 10.56% | 0% | 1.063% | 0% | 24 | 0 | 1.2751 | 14.0163 | NO
[11 empty] | 2021-11-04 | 88.6% | 10.34% | 0% | 1.051% | 0% | 24 | 0 | 1.104 | 13.8619 | NO
[11 empty] | 2021-11-05 | 88.68% | 10.28% | 0% | 1.042% | 0% | 24 | 0 | 1.1018 | 13.8748 | NO
[11 empty] | 2021-11-06 | 89.43% | 9.458% | 0% | 1.108% | 0% | 24 | 0 | 0.95755 | 13.6551 | NO
[11 empty] | 2021-11-07 | 89.66% | 9.23% | 0% | 1.106% | 0% | 24 | 0 | 0.91834 | 13.6493 | NO
[11 empty] | 2021-11-08 | 89.52% | 9.528% | 0% | 0.9481% | 0% | 24 | 0 | 0.91655 | 13.5681 | NO
[11 empty] | 2021-11-09 | 86.37% | 12.85% | 0% | 0.7837% | 0% | 24 | 0 | 0.7607 | 14.1571 | NO
[11 empty] | 2021-11-10 | 85.39% | 13.85% | 0% | 0.757% | 0% | 24 | 0 | 0.69829 | 14.6257 | NO
[11 empty] | 2021-11-11 | 85.87% | 13.2% | 0% | 0.923% | 0% | 24 | 0 | 0.71155 | 14.4241 | NO
[11 empty] | 2021-11-12 | 86.02% | 13.04% | 0% | 0.9338% | 0% | 24 | 0 | 0.80686 | 14.6261 | NO
[11 empty] | 2021-11-13 | 86.03% | 13.06% | 0% | 0.9179% | 0% | 24 | 0 | 0.71529 | 14.5242 | NO
[11 empty] | 2021-11-14 | 85.78% | 13.3% | 0% | 0.9208% | 0% | 24 | 0 | 0.73613 | 14.5353 | NO
[11 empty] | 2021-11-15 | 85.96% | 13.1% | 0% | 0.9377% | 0% | 24 | 0 | 0.83314 | 14.4957 | NO
[11 empty] | 2021-11-16 | 86.19% | 12.89% | 0% | 0.9212% | 0% | 24 | 0 | 0.72236 | 14.4455 | NO
[11 empty] | 2021-11-17 | 86.37% | 12.7% | 0% | 0.9223% | 0% | 24 | 0 | 0.81175 | 14.4173 | NO
[11 empty] | 2021-11-18 | 87.5% | 11.5% | 0% | 0.9959% | 0% | 24 | 0 | 0.86909 | 14.2176 | NO
[11 empty] | 2021-11-19 | 89.05% | 9.868% | 0% | 1.083% | 0% | 24 | 0 | 0.79591 | 13.809 | NO
[11 empty] | 2021-11-20 | 88.96% | 9.937% | 0% | 1.103% | 0% | 24 | 0 | 0.94359 | 13.8946 | NO
[11 empty] | 2021-11-21 | 87.78% | 11.01% | 0% | 1.21% | 0% | 24 | 0 | 1.1885 | 14.137 | NO
[11 empty] | 2021-11-22 | 89.27% | 9.647% | 0% | 1.088% | 0% | 24 | 0 | 1.2394 | 13.7528 | NO
[11 empty] | 2021-11-23 | 89.44% | 9.496% | 0% | 1.069% | 0% | 24 | 0 | 1.169 | 13.711 | NO
[11 empty] | 2021-11-24 | 89.24% | 9.657% | 0% | 1.099% | 0% | 24 | 0 | 1.0231 | 13.9123 | NO
[11 empty] | 2021-11-25 | 89.35% | 9.532% | 0% | 1.122% | 0% | 24 | 0 | 1.1352 | 13.7979 | NO
[11 empty] | 2021-11-26 | 87.42% | 11.17% | 0% | 1.411% | 0% | 24 | 0 | 2.4371 | 14.3158 | NO
[11 empty] | 2021-11-27 | 87.75% | 12.02% | 0% | 0.2265% | 0% | 24 | 0 | 1.8989 | 15.5433 | NO
[11 empty] | 2021-11-28 | 86.68% | 12.24% | 0% | 1.08% | 0% | 24 | 0 | 1.4889 | 14.4491 | NO
[11 empty] | 2021-11-29 | 86.92% | 12% | 0% | 1.076% | 0% | 24 | 0 | 1.8767 | 14.4499 | NO
[11 empty] | 2021-11-30 | 8.312% | 21.39% | 0% | 25.55% | 44.74% | 24 | 22 | 6.7097 | 34.8641 | NO
[11 empty] | 2021-12-01 | 29.05% | 23.56% | 0% | 31.01% | 16.37% | 24 | 16 | 5.811 | 21.0369 | NO
[11 empty] | 2021-12-02 | 88.17% | 10.62% | 0% | 1.213% | 0% | 24 | 0 | 1.942 | 14.0441 | NO
[11 empty] | 2021-12-03 | 88.32% | 10.54% | 0% | 1.135% | 0% | 24 | 0 | 1.296 | 14.0114 | NO
[11 empty] | 2021-12-04 | 90.27% | 8.502% | 0% | 1.23% | 0% | 24 | 0 | 1.11 | 13.6044 | NO
[11 empty] | 2021-12-05 | 88.76% | 10.04% | 0% | 1.194% | 0% | 24 | 0 | 1.4924 | 14.0014 | NO
[11 empty] | 2021-12-06 | 88.21% | 1.513% | 0% | 10.27% | 0% | 24 | 0 | 1.3343 | 11.6274 | NO
[11 empty] | 2021-12-07 | 88.11% | 0% | 0% | 11.89% | 0% | 24 | 0 | 1.3361 | 11.1224 | NO
[11 empty] | 2021-12-08 | 87.93% | 0% | 0% | 12.07% | 0% | 24 | 0 | 1.2475 | 11.1399 | NO
[11 empty] | 2021-12-09 | 87.62% | 0% | 0% | 12.38% | 0% | 24 | 0 | 1.171 | 11.1265 | NO
[11 empty] | 2021-12-10 | 86.42% | 0% | 0% | 13.58% | 0% | 24 | 0 | 1.3779 | 11.1776 | NO
[11 empty] | 2021-12-11 | 85.69% | 0% | 0% | 14.31% | 0% | 24 | 0 | 1.1354 | 10.9914 | NO
[11 empty] | 2021-12-12 | 86.81% | 4.148% | 0% | 9.041% | 0% | 24 | 0 | 0.99958 | 12.0763 | NO
[11 empty] | 2021-12-13 | 85.33% | 4.756% | 0% | 9.916% | 0% | 24 | 0 | 1.188 | 12.0977 | NO
[11 empty] | 2021-12-14 | 85.38% | 0.356% | 0% | 14.26% | 0% | 24 | 0 | 1.0629 | 10.9924 | NO
[11 empty] | 2021-12-15 | 84.98% | 13.92% | 0% | 1.101% | 0% | 24 | 0 | 1.214 | 14.6883 | NO
[11 empty] | 2021-12-16 | 84.56% | 14.36% | 0% | 1.081% | 0% | 24 | 0 | 1.0978 | 14.9614 | NO
[11 empty] | 2021-12-17 | 87.59% | 9.619% | 0% | 2.793% | 0% | 24 | 0 | 1.1911 | 13.7793 | NO
[11 empty] | 2021-12-18 | 90.16% | 8.713% | 0% | 1.128% | 0% | 24 | 0 | 1.1192 | 13.605 | NO
[11 empty] | 2021-12-19 | 89.22% | 9.665% | 0% | 1.111% | 0% | 24 | 0 | 1.3992 | 13.9174 | NO
[11 empty] | 2021-12-20 | 89.57% | 9.356% | 0% | 1.075% | 0% | 24 | 0 | 1.355 | 13.8597 | NO
[11 empty] | 2021-12-21 | 85.37% | 7.883% | 0% | 6.751% | 0% | 24 | 0 | 1.4955 | 13.2472 | NO
[11 empty] | 2021-12-22 | 83.07% | 13.18% | 0% | 3.747% | 0% | 24 | 0 | 1.0744 | 14.545 | NO
[11 empty] | 2021-12-23 | 83.4% | 12.67% | 0% | 3.926% | 0% | 24 | 0 | 0.90026 | 14.3017 | NO
[11 empty] | 2021-12-24 | 81.61% | 13.92% | 0% | 4.463% | 0% | 24 | 0 | 0.91941 | 14.7494 | NO
[11 empty] | 2021-12-25 | 81.67% | 13.73% | 0% | 4.592% | 0% | 24 | 0 | 0.94773 | 14.7391 | NO
[11 empty] | 2021-12-26 | 81.38% | 13.91% | 0% | 4.716% | 0% | 24 | 0 | 1.0956 | 14.6719 | NO
[11 empty] | 2021-12-27 | 80.76% | 14.44% | 0% | 4.794% | 0% | 24 | 0 | 1.01 | 14.6958 | NO
[11 empty] | 2021-12-28 | 83.12% | 12.56% | 0% | 4.313% | 0% | 24 | 0 | 0.97118 | 14.3291 | NO
[11 empty] | 2021-12-29 | 84.21% | 11.66% | 0% | 4.127% | 0% | 24 | 0 | 1.127 | 14.1525 | NO
[11 empty] | 2021-12-30 | 84.28% | 11.73% | 0% | 3.991% | 0% | 24 | 0 | 1.0459 | 14.124 | NO
[11 empty] | 2021-12-31 | 84.56% | 11.42% | 0% | 4.022% | 0% | 24 | 0 | 1.0763 | 13.9727 | NO

## A53 Mitchell Boiler
|  | Concentrations in mg/m³ at reference conditions after subtracting uncertainty | [9 empty] | Daily means, excluding hours outside normal operating conditions
|  | 2021-10-01 |  |  | 2021-11-01 |  |  | 2021-12-01 |  |  | Date | Fuel mix |  |  |  |  | Particulate Matter concentration (mg/m³) after subtracting uncertainty
|  | PM | SO2 | NOx | PM | SO2 | NOx | PM | SO2 | NOx |  | % BFG | % COG | % BOSg | % NG | % HFO | No.valid hours | No.hours OTNOC | Measured | Limit | Breach?
Daily means | Minimum | 1.4806 | Discontinuous monitoring only |  | 0.69829 | Discontinuous monitoring only |  | 1.8721 | Discontinuous monitoring only |  | 2021-10-01 | 93.14% | 3.786% | Nil | 3.072% | 0.005503% | 24 | 0 | 2.1256 | 10.6049 | NO
| Maximum | 8.1393 |  |  | 6.7097 |  |  | 4.466 |  |  | 2021-10-02 | 94.69% | 4.62% | Nil | 0.6827% | 0.01071% | 24 | 0 | 1.9933 | 10.8973 | NO
| No. > Limit | 0 |  |  | 0 |  |  | 0 |  |  | 2021-10-03 | 93.81% | 5.13% | Nil | 1.054% | 0.006758% | 24 | 0 | 2.5124 | 10.976 | NO
Monthly mean |  | 2.416 |  |  | 1.9759 |  |  | 2.2825 |  |  | 2021-10-04 | 92.87% | 5.593% | Nil | 1.521% | 0.01292% | 24 | 0 | 2.2609 | 11.0544 | NO
Monthly mean limit |  | 11.9365 |  |  | 10.9241 |  |  | 10.965 |  |  | 2021-10-05 | 91.96% | 6.065% | Nil | 1.962% | 0.01348% | 24 | 0 | 2.2861 | 11.1228 | NO
[11 empty] | 2021-10-06 | 49.12% | 9.6% | Nil | 14.69% | 26.6% | 24 | 11 | 3.4321 | 21.8889 | NO
[11 empty] | 2021-10-07 | 89.41% | 3.435% | Nil | 4.435% | 2.725% | 24 | 2 | 2.1557 | 12.2754 | NO
[11 empty] | 2021-10-08 | 94.21% | 5.136% | Nil | 0.6448% | 0.006621% | 24 | 0 | 1.6052 | 11.0045 | NO
[11 empty] | 2021-10-09 | 93.3% | 5.737% | Nil | 0.9493% | 0.01204% | 24 | 0 | 1.6834 | 11.1203 | NO
[11 empty] | 2021-10-10 | 93.45% | 5.453% | Nil | 1.087% | 0.008871% | 24 | 0 | 1.6222 | 11.0419 | NO
[11 empty] | 2021-10-11 | 93.03% | 5.403% | Nil | 1.568% | 0.003272% | 24 | 0 | 2.1109 | 11.0723 | NO
[11 empty] | 2021-10-12 | 93.95% | 4.663% | Nil | 1.381% | 0.00417% | 24 | 0 | 1.7619 | 10.8702 | NO
[11 empty] | 2021-10-13 | 94.35% | 4.022% | Nil | 1.625% | 0.006312% | 24 | 0 | 1.756 | 10.7367 | NO
[11 empty] | 2021-10-14 | 10.57% | 7.596% | Nil | 31.2% | 50.64% | 24 | 22 | 8.1393 | 30.3095 | NO
[11 empty] | 2021-10-15 | 85.57% | 4.536% | Nil | 6.195% | 3.7% | 23 | 2 | 4.9922 | 12.8427 | NO
[11 empty] | 2021-10-16 | 95.84% | 3.398% | Nil | 0.7466% | 0.0115% | 24 | 0 | 1.6305 | 10.6467 | NO
[11 empty] | 2021-10-17 | 95.43% | 3.768% | Nil | 0.7917% | 0.009931% | 24 | 0 | 1.4806 | 10.7182 | NO
[11 empty] | 2021-10-18 | 95.77% | 3.122% | Nil | 1.097% | 0.01% | 24 | 0 | 1.6134 | 10.5741 | NO
[11 empty] | 2021-10-19 | 95.79% | 2.666% | Nil | 1.54% | 0.006017% | 24 | 0 | 1.9466 | 10.4825 | NO
[11 empty] | 2021-10-20 | 91.69% | 1.781% | Nil | 6.516% | 0.01217% | 24 | 0 | 2.7729 | 10.0418 | NO
[11 empty] | 2021-10-21 | 93.3% | 5.782% | Nil | 0.9069% | 0.006215% | 24 | 0 | 2.1883 | 11.131 | NO
[11 empty] | 2021-10-22 | 92.39% | 6.065% | Nil | 1.539% | 0.006401% | 24 | 0 | 2.0656 | 11.1727 | NO
[11 empty] | 2021-10-23 | 93.61% | 4.478% | Nil | 1.913% | 0.002117% | 24 | 0 | 2.0158 | 10.8112 | NO
[11 empty] | 2021-10-24 | 94.16% | 3.377% | Nil | 2.453% | 0.007614% | 24 | 0 | 2.4048 | 10.5578 | NO
[11 empty] | 2021-10-25 | 90.36% | 4.466% | Nil | 3.984% | 1.188% | 23 | 0 | 5.2062 | 11.295 | NO
[11 empty] | 2021-10-26 | 94.9% | 4.695% | Nil | 0.4012% | 0.007017% | 24 | 0 | 2.0477 | 10.9236 | NO
[11 empty] | 2021-10-27 | 96.11% | 3.473% | Nil | 0.4101% | 0.007643% | 24 | 0 | 2.2532 | 10.6851 | NO
[11 empty] | 2021-10-28 | 96.25% | 3.361% | Nil | 0.3779% | 0.007219% | 24 | 0 | 1.8777 | 10.6567 | NO
[11 empty] | 2021-10-29 | 95.17% | 4.251% | Nil | 0.5653% | 0.009227% | 24 | 0 | 2.4753 | 10.8574 | NO
[11 empty] | 2021-10-30 | 94.9% | 4.649% | Nil | 0.4396% | 0.008151% | 24 | 0 | 2.1846 | 10.9132 | NO
[11 empty] | 2021-10-31 | 83.62% | 4.479% | Nil | 11.9% | 0.007623% | 22 | 4 | 6.9563 | 10.747 | NO
[11 empty] | 2021-11-01 | 82.17% | 7.3% | Nil | 10.53% | 0.003829% | 23 | 3 | 2.4408 | 17.5369 | NO
[11 empty] | 2021-11-02 | 94.88% | 4.333% | Nil | 0.7785% | 0.007402% | 24 | 0 | 1.6561 | 14.2209 | NO
[11 empty] | 2021-11-03 | 94.44% | 4.49% | Nil | 1.066% | 0.008034% | 24 | 0 | 1.2751 | 14.0163 | NO
[11 empty] | 2021-11-04 | 93.25% | 5.329% | Nil | 1.415% | 0.006452% | 24 | 0 | 1.104 | 13.8619 | NO
[11 empty] | 2021-11-05 | 92.11% | 6.09% | Nil | 1.799% | 0.002967% | 24 | 0 | 1.1018 | 13.8748 | NO
[11 empty] | 2021-11-06 | 90.42% | 7.168% | Nil | 2.404% | 0.00888% | 24 | 0 | 0.95755 | 13.6551 | NO
[11 empty] | 2021-11-07 | 89.04% | 8.025% | Nil | 2.932% | 0.007655% | 24 | 0 | 0.91834 | 13.6493 | NO
[11 empty] | 2021-11-08 | 87.24% | 8.522% | Nil | 3.34% | 0.8969% | 24 | 0 | 0.91655 | 13.5681 | NO
[11 empty] | 2021-11-09 | 91.35% | 7.668% | Nil | 0.9771% | 0.007303% | 24 | 0 | 0.7607 | 14.1571 | NO
[11 empty] | 2021-11-10 | 92% | 6.314% | Nil | 1.675% | 0.006752% | 24 | 0 | 0.69829 | 14.6257 | NO
[11 empty] | 2021-11-11 | 94.18% | 4.787% | Nil | 1.029% | 0.004264% | 24 | 0 | 0.71155 | 14.4241 | NO
[11 empty] | 2021-11-12 | 93.13% | 5.329% | Nil | 1.524% | 0.01695% | 24 | 0 | 0.80686 | 14.6261 | NO
[11 empty] | 2021-11-13 | 94.5% | 4.203% | Nil | 1.298% | 0.003989% | 24 | 0 | 0.71529 | 14.5242 | NO
[11 empty] | 2021-11-14 | 94.25% | 4.229% | Nil | 1.511% | 0.006979% | 24 | 0 | 0.73613 | 14.5353 | NO
[11 empty] | 2021-11-15 | 94.31% | 4.044% | Nil | 1.645% | 0.003139% | 24 | 0 | 0.83314 | 14.4957 | NO
[11 empty] | 2021-11-16 | 94.32% | 3.749% | Nil | 1.922% | 0.005202% | 24 | 0 | 0.72236 | 14.4455 | NO
[11 empty] | 2021-11-17 | 94.39% | 3.561% | Nil | 2.039% | 0.004924% | 24 | 0 | 0.81175 | 14.4173 | NO
[11 empty] | 2021-11-18 | 89.86% | 4.847% | Nil | 5.293% | 0.003691% | 24 | 0 | 0.86909 | 14.2176 | NO
[11 empty] | 2021-11-19 | 96.56% | 2.877% | Nil | 0.5527% | 0.00654% | 24 | 0 | 0.79591 | 13.809 | NO
[11 empty] | 2021-11-20 | 96.24% | 2.953% | Nil | 0.8037% | 0.001771% | 24 | 0 | 0.94359 | 13.8946 | NO
[11 empty] | 2021-11-21 | 95.32% | 3.544% | Nil | 1.133% | 0.005156% | 24 | 0 | 1.1885 | 14.137 | NO
[11 empty] | 2021-11-22 | 94.65% | 3.708% | Nil | 1.635% | 0.003273% | 24 | 0 | 1.2394 | 13.7528 | NO
[11 empty] | 2021-11-23 | 95.65% | 3.333% | Nil | 1.013% | 0.002058% | 24 | 0 | 1.169 | 13.711 | NO
[11 empty] | 2021-11-24 | 95.95% | 3.62% | Nil | 0.4255% | 0.003344% | 24 | 0 | 1.0231 | 13.9123 | NO
[11 empty] | 2021-11-25 | 95.13% | 4.274% | Nil | 0.5873% | 0.005843% | 24 | 0 | 1.1352 | 13.7979 | NO
[11 empty] | 2021-11-26 | 95.46% | 4.029% | Nil | 0.5051% | 0.002085% | 24 | 0 | 2.4371 | 14.3158 | NO
[11 empty] | 2021-11-27 | 94.19% | 5.245% | Nil | 0.5574% | 0.003518% | 24 | 0 | 1.8989 | 15.5433 | NO
[11 empty] | 2021-11-28 | 95.19% | 4.352% | Nil | 0.4561% | 0.002421% | 24 | 0 | 1.4889 | 14.4491 | NO
[11 empty] | 2021-11-29 | 95.25% | 4.312% | Nil | 0.4274% | 0.007213% | 24 | 0 | 1.8767 | 14.4499 | NO
[11 empty] | 2021-11-30 | 96.48% | 3.054% | Nil | 0.4569% | 0.008735% | 24 | 0 | 6.7097 | 34.8641 | NO
[11 empty] | 2021-12-01 | 78.24% | 4.983% | Nil | 7.878% | 8.902% | 23 | 4 | 4.466 | 14.895 | NO
[11 empty] | 2021-12-02 | 93.31% | 5.758% | Nil | 0.931% | 0.00514% | 24 | 0 | 2.3107 | 11.1175 | NO
[11 empty] | 2021-12-03 | 92.78% | 5.873% | Nil | 1.346% | 0.006441% | 24 | 0 | 2.3512 | 11.1279 | NO
[11 empty] | 2021-12-04 | 92.18% | 6.11% | Nil | 1.705% | 0.00802% | 24 | 0 | 2.4587 | 11.1432 | NO
[11 empty] | 2021-12-05 | 91.93% | 5.932% | Nil | 2.132% | 0.005429% | 24 | 0 | 2.403 | 11.0832 | NO
[11 empty] | 2021-12-06 | 91.8% | 1.118% | Nil | 7.073% | 0.00915% | 24 | 0 | 2.078 | 9.8514 | NO
[11 empty] | 2021-12-07 | 92.87% | 0.4919% | Nil | 6.621% | 0.01609% | 24 | 0 | 2.451 | 9.7752 | NO
[11 empty] | 2021-12-08 | 89.33% | 0.9491% | Nil | 9.715% | 0.001881% | 24 | 0 | 2.5919 | 9.7139 | NO
[11 empty] | 2021-12-09 | 89.22% | 1.17% | Nil | 9.61% | 0.004621% | 24 | 0 | 2.2542 | 9.7572 | NO
[11 empty] | 2021-12-10 | 91.5% | 1.214% | Nil | 7.28% | 0.004499% | 24 | 0 | 2.2878 | 9.881 | NO
[11 empty] | 2021-12-11 | 92.67% | 1.544% | Nil | 5.779% | 0.004576% | 24 | 0 | 1.8885 | 10.0217 | NO
[11 empty] | 2021-12-12 | 93.43% | 2.98% | Nil | 3.577% | 0.008131% | 24 | 0 | 1.9327 | 10.4361 | NO
[11 empty] | 2021-12-13 | 92.52% | 2.599% | Nil | 4.876% | 0.001797% | 24 | 0 | 2.1066 | 10.248 | NO
[11 empty] | 2021-12-14 | 92.21% | 1.335% | Nil | 6.449% | 0.007155% | 24 | 0 | 2.1733 | 9.9474 | NO
[11 empty] | 2021-12-15 | 89.71% | 8.532% | Nil | 1.752% | 0.002178% | 24 | 0 | 2.3219 | 11.7946 | NO
[11 empty] | 2021-12-16 | 92.38% | 5.805% | Nil | 1.806% | 0.007691% | 24 | 0 | 1.925 | 11.0843 | NO
[11 empty] | 2021-12-17 | 93.75% | 4.178% | Nil | 2.062% | 0.01304% | 24 | 0 | 2.0993 | 10.7399 | NO
[11 empty] | 2021-12-18 | 94.24% | 4.674% | Nil | 1.081% | 0.003979% | 24 | 0 | 2.1402 | 10.8837 | NO
[11 empty] | 2021-12-19 | 93.03% | 5.238% | Nil | 1.729% | 0.001801% | 24 | 0 | 2.3512 | 10.9931 | NO
[11 empty] | 2021-12-20 | 87.83% | 7.367% | Nil | 4.787% | 0.01208% | 24 | 0 | 2.5981 | 11.3016 | NO
[11 empty] | 2021-12-21 | 88.36% | 7.679% | Nil | 3.953% | 0.00688% | 24 | 0 | 2.483 | 11.3661 | NO
[11 empty] | 2021-12-22 | 90.34% | 7.878% | Nil | 1.769% | 0.01294% | 24 | 0 | 2.7047 | 11.5325 | NO
[11 empty] | 2021-12-23 | 92.76% | 6.556% | Nil | 0.6749% | 0.01116% | 24 | 0 | 2.073 | 11.3076 | NO
[11 empty] | 2021-12-24 | 92.64% | 6.747% | Nil | 0.6094% | 0.001774% | 24 | 0 | 1.8721 | 11.3217 | NO
[11 empty] | 2021-12-25 | 91.86% | 7.232% | Nil | 0.8973% | 0.01335% | 24 | 0 | 2.0712 | 11.4471 | NO
[11 empty] | 2021-12-26 | 92.19% | 6.819% | Nil | 0.973% | 0.01363% | 24 | 0 | 2.1254 | 11.3448 | NO
[11 empty] | 2021-12-27 | 92.51% | 6.495% | Nil | 0.9916% | 0.007086% | 24 | 0 | 2.0291 | 11.253 | NO
[11 empty] | 2021-12-28 | 91.96% | 6.834% | Nil | 1.207% | 0.002491% | 24 | 0 | 2.326 | 11.3246 | NO
[11 empty] | 2021-12-29 | 92.11% | 6.389% | Nil | 1.497% | 0.005536% | 24 | 0 | 2.1448 | 11.2683 | NO
[11 empty] | 2021-12-30 | 93.73% | 5.191% | Nil | 1.078% | 0.006667% | 24 | 0 | 1.948 | 10.9871 | NO
[11 empty] | 2021-12-31 | 92.76% | 5.789% | Nil | 1.444% | 0.004511% | 24 | 0 | 2.1552 | 11.1145 | NO

## A62 Boiler 3
|  | Concentrations in mg/m³ at reference conditions after subtracting uncertainty | [9 empty] | Daily means, excluding hours outside normal operating conditions
|  | 2021-10-01 |  |  | 2021-11-01 |  |  | 2021-12-01 |  |  | Date | Fuel mix |  |  |  |  | Particulate Matter concentration (mg/m³) after subtracting uncertainty |  |  |  |  | Sulphur dioxide concentration (mg/m³) after subtracting uncertainty |  |  |  |  | Oxides of nitrogen concentration (mg/m³) after subtracting uncertainty
|  | PM | SO2 | NOx | PM | SO2 | NOx | PM | SO2 | NOx |  | % BFG | % COG | % BOSg | % NG | % HFO | No.valid hours | No.hours OTNOC | Measured | Limit | Breach? | No.valid hours | No.hours OTNOC | Measured | Limit | Breach? | No.valid hours | No.hours OTNOC | Measured | Limit | Breach?
Daily means | Minimum | 0.35445 | 22.731 | 17.5188 | 0 | 21.4733 | Monitor out of calibration (Part A - S5N_21_76A) | 0 | 11.7034 | Monitor out of calibration (Part A - S5N_21_76A) | 2021-10-01 | 94.91% | 0.9505% | 0% | 4.135% |  | 24 | 0 | 1.6869 | 10.9817 | NO | 24 | 0 |  | 214.5865 | NO | 24 | 0 | 71.1796 | 215.4518 | NO
| Maximum | 2.6956 | 39.9262 | 100.6201 | 4.2761 | 54.9487 |  | 3.8587 | 54.3673 |  | 2021-10-02 | 99.27% | 0.7335% | 0% | 0% |  | 24 | 0 | 1.0779 | 11.1614 | NO | 24 | 0 |  | 221.6136 | NO | 24 | 0 | 42.2986 | 220 | NO
| No. > Limit | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 2021-10-03 | 97.21% | 2.792% | 0% | 0% |  | 24 | 0 | 0.94044 | 11.6143 | NO | 24 | 0 |  | 226.1427 | NO | 24 | 0 | 46.2255 | 220 | NO
Monthly mean |  | 1.5439 | 30.2 | 64 | 2.0647 | 31.9197 |  | 1.9302 | 27.3821 |  | 2021-10-04 | 96.81% | 3.19% | 0% | 0.0006227% |  | 24 | 0 | 0.95432 | 11.7017 | NO | 24 | 0 |  | 227.0165 | NO | 24 | 0 | 36.2384 | 219.9993 | NO
Monthly mean limit |  | 9.336 | 183.2945 | 186.721 | 8.9064 | 171.4174 | 178.1272 | 8.7236 | 165.226 | 174.4718 | 2021-10-05 | 91.64% | 8.359% | 0% | 0.0003485% |  | 24 | 0 | 0.91615 | 12.8389 | NO | 24 | 0 |  | 238.3889 | NO | 24 | 0 | 52.25 | 219.9996 | NO
[11 empty] | 2021-10-06 | 51.47% | 17.89% | 0% | 30.64% |  | 24 | 11 | 2.0575 | 13.2517 | NO | 24 | 11 |  | 203.7577 | NO | 24 | 11 | 78.3336 | 186.2962 | NO
[11 empty] | 2021-10-07 | 81.51% | 11.69% | 0% | 6.801% |  | 24 | 3 | 0.99413 | 13.198 | NO | 24 | 3 |  | 233.3774 | NO | 24 | 3 | 54.5138 | 212.5193 | NO
[11 empty] | 2021-10-08 | 77.26% | 20.03% | 0% | 2.714% |  | 24 | 0 | 1.4285 | 15.2574 | NO | 24 | 0 |  | 259.1405 | NO | 24 | 0 | 99.0749 | 217.0144 | NO
[11 empty] | 2021-10-09 | 94.06% | 5.936% | 0% | 0% |  | 24 | 0 | 2.6465 | 12.3058 | NO | 24 | 0 |  | 233.0581 | NO | 24 | 0 | 49.5592 | 220 | NO
[11 empty] | 2021-10-10 | 97.37% | 0.3456% | 0% | 2.287% |  | 24 | 0 | 1.2842 | 10.9503 | NO | 24 | 0 |  | 216.6099 | NO | 24 | 0 | 90.9721 | 217.4846 | NO
[11 empty] | 2021-10-11 | 99.95% | 0.0496% | 0% | 0% |  | 24 | 0 | 1.4706 | 11.0109 | NO | 24 | 0 |  | 220.1091 | NO | 24 | 0 | 59.2287 | 220 | NO
[11 empty] | 2021-10-12 | 99.96% | 0.03767% | 0% | 0% |  | 24 | 0 | 0.93992 | 11.0083 | NO | 24 | 0 |  | 220.0829 | NO | 24 | 0 | 50.6696 | 220 | NO
[11 empty] | 2021-10-13 | 98.36% | 1.643% | 0% | 0% |  | 24 | 0 | 0.71383 | 11.3614 | NO | 24 | 0 |  | 223.6142 | NO | 24 | 0 | 52.9268 | 220 | NO
[11 empty] | 2021-10-14 | 26.78% | 24.04% | 0% | 49.18% |  | 24 | 22 | 1.2431 | 13.5832 | NO | 24 | 22 |  | 183.615 | NO | 24 | 22 | 94.6357 | 165.898 | NO
[11 empty] | 2021-10-15 | 64.56% | 13.99% | 0% | 21.46% |  | 24 | 10 | 1.9296 | 12.8973 | NO | 24 | 10 |  | 211.8314 | NO | 24 | 10 | 17.5188 | 196.3986 | NO
[11 empty] | 2021-10-16 | 96.2% | 0.861% | 0% | 2.935% |  | 24 | 0 | 1.9127 | 11.028 | NO | 24 | 0 |  | 216.5665 | NO | 24 | 0 | 100.6201 | 216.771 | NO
[11 empty] | 2021-10-17 | 99.98% | 0.02203% | 0% | 0% |  | 24 | 0 | 0.86845 | 11.0048 | NO | 24 | 0 |  | 220.0485 | NO | 24 | 0 | 59.7744 | 220 | NO
[11 empty] | 2021-10-18 | 99.96% | 0.04018% | 0% | 0% |  | 24 | 0 | 1.008 | 11.0088 | NO | 24 | 0 |  | 220.0884 | NO | 24 | 0 | 54.9063 | 220 | NO
[11 empty] | 2021-10-19 | 99.94% | 0.05989% | 0% | 0% |  | 24 | 0 | 1.3204 | 11.0132 | NO | 24 | 0 |  | 220.1318 | NO | 24 | 0 | 65.6784 | 220 | NO
[11 empty] | 2021-10-20 | 99.92% | 0.08336% | 0% | 0% |  | 24 | 0 | 1.0961 | 11.0183 | NO | 24 | 0 |  | 220.1834 | NO | 24 | 0 | 63.0641 | 220 | NO
[11 empty] | 2021-10-21 | 87.61% | 4.493% | 0% | 7.896% |  | 24 | 3 | 2.6956 | 11.5543 | NO | 24 | 3 |  | 215.5549 | NO | 24 | 3 | 63.0436 | 211.3148 | NO
[11 empty] | 2021-10-22 | 99.82% | 0.1825% | 0% | 0% |  | 24 | 0 | 1.8375 | 11.0402 | NO | 24 | 0 |  | 220.4015 | NO | 24 | 0 | 67.6442 | 220 | NO
[11 empty] | 2021-10-23 | 96.96% | 0.8642% | 0% | 2.18% |  | 24 | 0 | 1.7475 | 11.0702 | NO | 24 | 0 |  | 217.9447 | NO | 24 | 0 | 87.1749 | 217.6021 | NO
[11 empty] | 2021-10-24 | 98.29% | 1.71% | 0% | 0% |  | 24 | 0 | 2.19 | 11.3762 | NO | 24 | 0 |  | 223.7624 | NO | 24 | 0 | 64.992 | 220 | NO
[11 empty] | 2021-10-25 | 94.17% | 3.758% | 0% | 2.072% |  | 24 | 0 | 2.5428 | 11.7127 | NO | 24 | 0 |  | 224.5053 | NO | 24 | 0 | 87.2475 | 217.7204 | NO
[11 empty] | 2021-10-26 | 99.99% | 0.01219% | 0% | 0% |  | 24 | 0 | 2.5455 | 11.0027 | NO | 24 | 0 | 33.626 | 220.0268 | NO | 24 | 0 | 53.2356 | 220 | NO
[11 empty] | 2021-10-27 | 90.95% | 0.06261% | 0% | 8.99% |  | 24 | 2 | 0.35445 | 10.5193 | NO | 24 | 2 | 22.731 | 203.8217 | NO | 24 | 2 |  | 210.1115 | NO
[11 empty] | 2021-10-28 | 99.95% | 0.04934% | 0% | 0% |  | 24 | 0 | 1.7379 | 11.0109 | NO | 24 | 0 | 27.9346 | 220.1085 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2021-10-29 | 99.95% | 0.05466% | 0% | 0% |  | 24 | 0 | 2.0141 | 11.012 | NO | 24 | 0 | 23.0871 | 220.1202 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2021-10-30 | 99.92% | 0.08095% | 0% | 0% |  | 24 | 0 | 1.3767 | 11.0178 | NO | 24 | 0 | 33.9028 | 220.1781 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2021-10-31 | 77.77% | 0.1051% | 0% | 22.13% |  | 24 | 5 | 2.6582 | 9.8062 | NO | 24 | 5 | 39.9262 | 180.074 | NO | 24 | 5 |  | 195.6623 | NO
[11 empty] | 2021-11-01 | 30.48% | 0.07407% | 0% | 69.44% |  | 24 | 16 | 1.7042 | 7.197 | NO | 24 | 16 | 21.4733 | 94.1264 | NO | 24 | 16 |  | 143.6142 | NO
[11 empty] | 2021-11-02 | 99.96% | 0.04156% | 0% | 0% |  | 24 | 0 | 1.4235 | 11.0091 | NO | 24 | 0 | 36.0464 | 220.0914 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2021-11-03 | 99.97% | 0.03413% | 0% | 0% |  | 24 | 0 | 1.342 | 11.0075 | NO | 24 | 0 | 38.9048 | 220.0751 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2021-11-04 | 99.94% | 0.06104% | 0% | 0% |  | 24 | 0 | 2.6386 | 11.0134 | NO | 24 | 0 | 22.3216 | 220.1343 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2021-11-05 | 99.89% | 0.1142% | 0% | 0% |  | 24 | 0 | 1.7508 | 11.0251 | NO | 24 | 0 | 34.2478 | 220.2513 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2021-11-06 | 99.54% | 0.4615% | 0% | 0% |  | 24 | 0 | 1.2091 | 11.1015 | NO | 24 | 0 | 40.892 | 221.0152 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2021-11-07 | 99.13% | 0.8736% | 0% | 0% |  | 24 | 0 | 1.3961 | 11.1922 | NO | 24 | 0 | 33.9713 | 221.9219 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2021-11-08 | 35.09% | 20.93% | 0% | 43.98% |  | 24 | 17 | 1.6478 | 13.185 | NO | 24 | 17 | 35.5677 | 186.2124 | NO | 24 | 17 |  | 171.6198 | NO
[11 empty] | 2021-11-09 | 1.225% | 37.96% | 0% | 60.82% |  | 24 | 24 | 0 | 16.0055 | NO | 24 | 24 |  | 193.1197 | NO | 24 | 24 |  | 153.0998 | NO
[11 empty] | 2021-11-10 | 48.27% | 27.2% | 0% | 24.53% |  | 24 | 10 | 1.8935 | 15.6356 | NO | 24 | 10 | 27.2113 | 235.3286 | NO | 24 | 10 |  | 193.0193 | NO
[11 empty] | 2021-11-11 | 98.32% | 0.672% | 0% | 1.008% |  | 24 | 0 | 2.3332 | 11.0924 | NO | 24 | 0 | 35.8499 | 219.6484 | NO | 24 | 0 |  | 218.8909 | NO
[11 empty] | 2021-11-12 | 81.73% | 6.951% | 0% | 11.32% |  | 24 | 4 | 1.794 | 11.9068 | NO | 24 | 4 | 45.2167 | 214.7537 | NO | 24 | 4 |  | 207.5529 | NO
[11 empty] | 2021-11-13 | 99.86% | 0.1375% | 0% | 0% |  | 24 | 0 | 1.4109 | 11.0303 | NO | 24 | 0 | 33.0178 | 220.3025 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2021-11-14 | 99.68% | 0.3167% | 0% | 0% |  | 24 | 0 | 1.4045 | 11.0697 | NO | 24 | 0 | 33.1521 | 220.6967 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2021-11-15 | 99.47% | 0.5286% | 0% | 0% |  | 24 | 0 | 1.1699 | 11.1163 | NO | 24 | 0 | 30.3642 | 221.163 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2021-11-16 | 99.02% | 0.9762% | 0% | 0% |  | 24 | 0 | 1.9351 | 11.2148 | NO | 24 | 0 | 24.4702 | 222.1476 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2021-11-17 | 98.92% | 1.076% | 0% | 0% |  | 24 | 0 | 1.4833 | 11.2368 | NO | 24 | 0 | 36.9999 | 222.3679 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2021-11-18 | 55.83% | 12.77% | 0% | 31.4% |  | 24 | 10 | 3.5677 | 12.0819 | NO | 24 | 10 | 54.9487 | 191.0987 | NO | 24 | 10 |  | 185.4602 | NO
[11 empty] | 2021-11-19 | 99.97% | 0.03377% | 0% | 0% |  | 24 | 0 | 1.3101 | 11.0074 | NO | 24 | 0 | 24.0637 | 220.0743 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2021-11-20 | 99.93% | 0.06739% | 0% | 0% |  | 24 | 0 | 2.0896 | 11.0148 | NO | 24 | 0 | 23.7672 | 220.1483 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2021-11-21 | 95.9% | 4.102% | 0% | 0% |  | 24 | 1 | 1.5378 | 11.9025 | NO | 24 | 1 | 31.9113 | 229.0254 | NO | 24 | 1 |  | 220 | NO
[11 empty] | 2021-11-22 | 99.96% | 0.03807% | 0% | 0% |  | 24 | 0 | 1.8494 | 11.0084 | NO | 24 | 0 | 33.8696 | 220.0838 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2021-11-23 | 99.99% | 0.01042% | 0% | 0% |  | 24 | 0 | 2.3378 | 11.0023 | NO | 24 | 0 | 29.1574 | 220.0229 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2021-11-24 | 99.94% | 0.05823% | 0% | 0% |  | 24 | 0 | 1.7118 | 11.0128 | NO | 24 | 0 | 29.3395 | 220.1281 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2021-11-25 | 99.71% | 0.04989% | 0% | 0.2361% |  | 24 | 0 | 2.1546 | 10.998 | NO | 24 | 0 | 25.0788 | 219.6812 | NO | 24 | 0 |  | 219.7403 | NO
[11 empty] | 2021-11-26 | 97.52% | 1.041% | 0% | 1.436% |  | 24 | 0 | 4.2396 | 11.1501 | NO | 24 | 0 | 27.4767 | 219.6853 | NO | 24 | 0 |  | 218.4209 | NO
[11 empty] | 2021-11-27 | 64.3% | 19.09% | 0% | 16.61% |  | 24 | 9 | 4.2761 | 14.2865 | NO | 24 | 9 | 28.7578 | 231.8538 | NO | 24 | 9 |  | 201.7298 | NO
[11 empty] | 2021-11-28 | 99.95% | 0.04717% | 0% | 0% |  | 24 | 0 | 3.0514 | 11.0104 | NO | 24 | 0 | 26.9689 | 220.1038 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2021-11-29 | 99.55% | 0.4474% | 0% | 0% |  | 24 | 0 | 3.7142 | 11.0984 | NO | 24 | 0 | 30.8568 | 220.9843 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2021-11-30 | 14% | 37.09% | 0% | 48.91% |  | 24 | 22 | 3.8148 | 16.4698 | NO | 24 | 22 | 33.9501 | 212.8281 | NO | 24 | 22 |  | 166.1998 | NO
[11 empty] | 2021-12-01 | 2.579% | 35.87% | 0% | 61.55% |  | 24 | 24 | 0 | 15.5058 | NO | 24 | 24 |  | 187.194 | NO | 24 | 24 |  | 152.2924 | NO
[11 empty] | 2021-12-02 | 44.76% | 20.71% | 0% | 34.52% |  | 24 | 14 | 3.8587 | 13.6575 | NO | 24 | 14 | 34.5641 | 202.9016 | NO | 24 | 14 |  | 182.0228 | NO
[11 empty] | 2021-12-03 | 99.04% | 0.6025% | 0% | 0.3545% |  | 24 | 0 | 3.1634 | 11.113 | NO | 24 | 0 | 26.6431 | 220.6821 | NO | 24 | 0 |  | 219.6101 | NO
[11 empty] | 2021-12-04 | 99.67% | 0.3338% | 0% | 0% |  | 24 | 0 | 1.6738 | 11.0734 | NO | 24 | 0 | 23.6145 | 220.7344 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2021-12-05 | 99.04% | 0.9562% | 0% | 0% |  | 24 | 0 | 2.2331 | 11.2104 | NO | 24 | 0 | 25.5176 | 222.1037 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2021-12-06 | 13.48% | 3.932% | 0% | 82.58% |  | 24 | 21 | 2.2642 | 7.3229 | NO | 24 | 21 | 54.3673 | 78.7603 | NO | 24 | 21 |  | 129.1575 | NO
[11 empty] | 2021-12-07 | 77.38% | 0.5116% | 0% | 22.11% |  | 24 | 6 | 3.7958 | 9.8963 | NO | 24 | 6 | 25.597 | 180.9902 | NO | 24 | 6 |  | 195.6755 | NO
[11 empty] | 2021-12-08 | 96.7% | 0.7513% | 0% | 2.55% |  | 24 | 0 | 1.9556 | 11.025 | NO | 24 | 0 | 23.8354 | 217.0241 | NO | 24 | 0 |  | 217.1947 | NO
[11 empty] | 2021-12-09 | 99.1% | 0.8995% | 0% | 0% |  | 24 | 0 | 1.6301 | 11.1979 | NO | 24 | 0 | 28.9325 | 221.9788 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2021-12-10 | 98.83% | 1.168% | 0% | 0% |  | 24 | 0 | 1.5341 | 11.2569 | NO | 24 | 0 | 25.0196 | 222.5692 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2021-12-11 | 98.51% | 1.494% | 0% | 0% |  | 24 | 0 | 1.4442 | 11.3286 | NO | 24 | 0 | 17.3464 | 223.2864 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2021-12-12 | 98.93% | 1.07% | 0% | 0% |  | 24 | 0 | 1.3461 | 11.2353 | NO | 24 | 0 | 34.7948 | 222.353 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2021-12-13 | 84.79% | 0.459% | 0% | 14.75% |  | 24 | 4 | 1.441 | 10.2898 | NO | 24 | 4 | 22.6135 | 194.2401 | NO | 24 | 4 |  | 203.7759 | NO
[11 empty] | 2021-12-14 | 99.06% | 0.9391% | 0% | 0% |  | 24 | 0 | 1.3865 | 11.2066 | NO | 24 | 0 | 29.9196 | 222.066 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2021-12-15 | 65.65% | 1.375% | 0% | 32.98% |  | 24 | 8 | 1.2703 | 9.4887 | NO | 24 | 8 | 28.8591 | 163.1718 | NO | 24 | 8 |  | 183.7255 | NO
[11 empty] | 2021-12-16 | 99.63% | 0.3748% | 0% | 0% |  | 24 | 0 | 1.4306 | 11.0825 | NO | 24 | 0 | 44.0701 | 220.8246 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2021-12-17 | 99.17% | 0.8267% | 0% | 0% |  | 24 | 0 | 1.2914 | 11.1819 | NO | 24 | 0 | 27.3888 | 221.8187 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2021-12-18 | 98.5% | 1.502% | 0% | 0% |  | 24 | 0 | 1.5114 | 11.3305 | NO | 24 | 0 | 17.5581 | 223.3055 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2021-12-19 | 59.85% | 21.73% | 0% | 18.42% |  | 24 | 8 | 2.386 | 14.7673 | NO | 24 | 8 | 33.5674 | 234.3708 | NO | 24 | 8 |  | 199.7369 | NO
[11 empty] | 2021-12-20 | 22.09% | 32.42% | 0% | 45.49% |  | 24 | 19 | 2.2874 | 15.6299 | NO | 24 | 19 | 40.2326 | 208.751 | NO | 24 | 19 |  | 169.9587 | NO
[11 empty] | 2021-12-21 | 58.58% | 14.99% | 0% | 26.43% |  | 24 | 10 | 3.4819 | 12.8446 | NO | 24 | 10 | 24.2352 | 205.0111 | NO | 24 | 10 |  | 190.9262 | NO
[11 empty] | 2021-12-22 | 83.38% | 0.1426% | 0% | 16.48% |  | 24 | 5 | 2.6882 | 10.1252 | NO | 24 | 5 | 11.7034 | 190.41 | NO | 24 | 5 |  | 201.8765 | NO
[11 empty] | 2021-12-23 | 82.22% | 0.4054% | 0% | 17.37% |  | 24 | 4 | 1.7779 | 10.1338 | NO | 24 | 4 | 25.6401 | 189.3643 | NO | 24 | 4 |  | 200.8924 | NO
[11 empty] | 2021-12-24 | 99.46% | 0.5418% | 0% | 0% |  | 24 | 0 | 2.0713 | 11.1192 | NO | 24 | 0 | 33.4681 | 221.192 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2021-12-25 | 85.63% | 0.8612% | 0% | 13.5% |  | 24 | 4 | 1.4517 | 10.4467 | NO | 24 | 4 | 37.3271 | 197.3851 | NO | 24 | 4 |  | 205.1458 | NO
[11 empty] | 2021-12-26 | 90.52% | 1.385% | 0% | 8.093% |  | 24 | 2 | 3.3359 | 10.8596 | NO | 24 | 2 | 20.7863 | 208.3585 | NO | 24 | 2 |  | 211.0982 | NO
[11 empty] | 2021-12-27 | 98.95% | 1.047% | 0% | 0% |  | 24 | 0 | 1.3119 | 11.2303 | NO | 24 | 0 | 27.0413 | 222.3034 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2021-12-28 | 76.9% | 10.24% | 0% | 12.87% |  | 24 | 5 | 1.2838 | 12.5443 | NO | 24 | 5 | 29.2924 | 219.1652 | NO | 24 | 5 |  | 205.845 | NO
[11 empty] | 2021-12-29 | 71.51% | 11.82% | 0% | 16.67% |  | 24 | 7 | 1.2074 | 12.6831 | NO | 24 | 7 | 35.7332 | 215.743 | NO | 24 | 7 |  | 201.6625 | NO
[11 empty] | 2021-12-30 | 99.79% | 0.2056% | 0% | 0% |  | 24 | 0 | 1.3433 | 11.0452 | NO | 24 | 0 | 22.8636 | 220.4524 | NO | 24 | 0 |  | 220 | NO
[11 empty] | 2021-12-31 | 99.53% | 0.4709% | 0% | 0% |  | 24 | 0 | 2.2054 | 11.1036 | NO | 24 | 0 | 25.3225 | 221.036 | NO | 24 | 0 |  | 220 | NO
Note on E5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Based on data from 26th to 31st Oct as per Part A number S5N_21_75A
Note on F5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Based on data from 1st to 26th Oct as per Part A number S5N_21_76A
Note on E6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Based on data from 26th to 31st Oct as per Part A number S5N_21_75A
Note on F6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Based on data from 1st to 26th Oct as per Part A number S5N_21_76A
Note on E8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Based on data from 26th to 31st Oct as per Part A number S5N_21_75A
Note on F8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Based on data from 1st to 26th Oct as per Part A number S5N_21_76A

## A52A Boiler 6
|  | Concentrations in mg/m³ at reference conditions after subtracting uncertainty | [9 empty] | Daily means, excluding hours outside normal operating conditions
|  | 2021-10-01 |  |  | 2021-11-01 |  |  | 2021-12-01 |  |  | Date | Fuel mix |  |  |  |  | Particulate Matter concentration (mg/m³) after subtracting uncertainty |  |  |  |  | Sulphur dioxide concentration (mg/m³) after subtracting uncertainty |  |  |  |  | Oxides of nitrogen concentration (mg/m³) after subtracting uncertainty
|  | PM | SO2 | NOx | PM | SO2 | NOx | PM | SO2 | NOx |  | % BFG | % COG | % BOSg | % NG | % HFO | No.valid hours | No.hours OTNOC | Measured | Limit | Breach? | No.valid hours | No.hours OTNOC | Measured | Limit | Breach? | No.valid hours | No.hours OTNOC | Measured | Limit | Breach?
Daily means | Minimum | Not operating as per Derogation and as discussed with NRW |  |  | 0.45702 | 40.017 | 44.6805 | 1.1695 | 35.7872 | 37.3974 | 2021-10-01 | Nil | Nil | Nil | Nil | Nil
| Maximum |  |  |  | 2.1099 | 136.4954 | 210.0722 | 2.5713 | 88.0262 | 164.7258 | 2021-10-02 | Nil | Nil | Nil | Nil | Nil
| No. > Limit |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2021-10-03 | Nil | Nil | Nil | Nil | Nil
Monthly mean |  |  |  |  | 1.1502 | 63.0036 | 80.4395 | 1.4701 | 57.1468 | 75.8219 | 2021-10-04 | Nil | Nil | Nil | Nil | Nil
Monthly mean limit |  |  |  |  | 14.6108 | 208.4021 | 284.5147 | 13.7876 | 201.3871 | 280.414 | 2021-10-05 | Nil | Nil | Nil | Nil | Nil
[11 empty] | 2021-10-06 | Nil | Nil | Nil | Nil | Nil
[11 empty] | 2021-10-07 | Nil | Nil | Nil | Nil | Nil
[11 empty] | 2021-10-08 | Nil | Nil | Nil | Nil | Nil
[11 empty] | 2021-10-09 | Nil | Nil | Nil | Nil | Nil
[11 empty] | 2021-10-10 | Nil | Nil | Nil | Nil | Nil
[11 empty] | 2021-10-11 | Nil | Nil | Nil | Nil | Nil
[11 empty] | 2021-10-12 | Nil | Nil | Nil | Nil | Nil
[11 empty] | 2021-10-13 | Nil | Nil | Nil | Nil | Nil
[11 empty] | 2021-10-14 | Nil | Nil | Nil | Nil | Nil
[11 empty] | 2021-10-15 | Nil | Nil | Nil | Nil | Nil
[11 empty] | 2021-10-16 | Nil | Nil | Nil | Nil | Nil
[11 empty] | 2021-10-17 | Nil | Nil | Nil | Nil | Nil
[11 empty] | 2021-10-18 | Nil | Nil | Nil | Nil | Nil
[11 empty] | 2021-10-19 | Nil | Nil | Nil | Nil | Nil
[11 empty] | 2021-10-20 | Nil | Nil | Nil | Nil | Nil
[11 empty] | 2021-10-21 | Nil | Nil | Nil | Nil | Nil
[11 empty] | 2021-10-22 | Nil | Nil | Nil | Nil | Nil
[11 empty] | 2021-10-23 | Nil | Nil | Nil | Nil | Nil
[11 empty] | 2021-10-24 | Nil | Nil | Nil | Nil | Nil
[11 empty] | 2021-10-25 | Nil | Nil | Nil | Nil | Nil
[11 empty] | 2021-10-26 | Nil | Nil | Nil | Nil | Nil
[11 empty] | 2021-10-27 | Nil | Nil | Nil | Nil | Nil
[11 empty] | 2021-10-28 | Nil | Nil | Nil | Nil | Nil
[11 empty] | 2021-10-29 | Nil | Nil | Nil | Nil | Nil
[11 empty] | 2021-10-30 | Nil | Nil | Nil | Nil | Nil
[11 empty] | 2021-10-31 | Nil | Nil | Nil | Nil | Nil
[11 empty] | 2021-11-01 | 47.15% | 9.396% | 2.891% | 27.13% | 13.44% | 24 | 14 | 0.53092 | 14.4394 | NO |  |  |  | 198.994 | NO |  |  |  | 255.6595 | NO
[11 empty] | 2021-11-02 | 67.28% | 5.389% | 9.774% | 17.55% | 0% | 24 | 0 | 0.64304 | 13.3633 | NO |  |  |  | 199.9486 | NO |  |  |  | 291.3282 | NO
[11 empty] | 2021-11-03 | 69.09% | 8.084% | 15.85% | 6.984% | 0% | 24 | 0 | 0.63779 | 15.8889 | NO | 8 | 0 | 53.1488 | 225.1052 | NO | 8 | 0 | 67.1922 | 314.7029 | NO
[11 empty] | 2021-11-04 | 75.02% | 8.334% | 11.17% | 5.47% | 0% | 24 | 0 | 0.68071 | 14.9977 | NO | 24 | 0 | 103.7992 | 228.3994 | NO | 24 | 0 | 154.0215 | 318.0253 | NO
[11 empty] | 2021-11-05 | 77.98% | 8.661% | 10.11% | 3.245% | 0% | 24 | 0 | 0.63581 | 14.9485 | NO | 24 | 0 | 65.2774 | 233.1646 | NO | 24 | 0 | 87.9842 | 322.8318 | NO
[11 empty] | 2021-11-06 | 73.35% | 6.512% | 17.4% | 2.737% | 0% | 24 | 0 | 0.45702 | 16.1097 | NO | 24 | 0 | 40.017 | 229.3237 | NO | 24 | 0 | 44.6805 | 323.9697 | NO
[11 empty] | 2021-11-07 | 65.38% | 6.295% | 25.14% | 3.19% | 0% | 24 | 0 | 0.52388 | 17.7407 | NO | 24 | 0 | 79.5029 | 228.0883 | NO | 24 | 0 | 112.3707 | 322.9935 | NO
[11 empty] | 2021-11-08 | 51.55% | 18.59% | 13.01% | 16.85% | 0% | 24 | 16 | 0.54313 | 16.8365 | NO | 24 | 16 | 125.5048 | 230.961 | NO | 24 | 16 | 191.2312 | 291.4133 | NO
[11 empty] | 2021-11-09 | 57.67% | 21.1% | 8.25% | 12.97% | 0% | 24 | 5 | 0.61581 | 16.7058 | NO | 24 | 5 | 108.0185 | 242.81 | NO | 24 | 5 | 161.2546 | 301.1536 | NO
[11 empty] | 2021-11-10 | 62.07% | 16.51% | 9.984% | 11.43% | 0% | 24 | 6 | 1.0398 | 16.1638 | NO | 21 | 6 | 72.3898 | 235.365 | NO | 23 | 6 | 100.1769 | 304.5615 | NO
[11 empty] | 2021-11-11 | 68.79% | 11.14% | 16.36% | 3.712% | 0% | 24 | 0 | 1.3556 | 16.8557 | NO | 21 | 0 | 84.4339 | 237.8382 | NO | 23 | 0 | 120.8239 | 321.922 | NO
[11 empty] | 2021-11-12 | 62.26% | 12.76% | 17.41% | 7.561% | 0% | 24 | 5 | 1.2704 | 17.2031 | NO | 24 | 5 | 77.2446 | 234.3779 | NO | 24 | 5 | 108.4994 | 313.2084 | NO
[11 empty] | 2021-11-13 | 76.25% | 9.309% | 11.41% | 3.036% | 0% | 24 | 0 | 1.3269 | 15.3961 | NO | 24 | 0 | 60.7793 | 234.9403 | NO | 24 | 0 | 80.2731 | 323.3621 | NO
[11 empty] | 2021-11-14 | 71.61% | 7.331% | 18.43% | 2.635% | 0% | 24 | 0 | 1.305 | 16.5309 | NO | 24 | 0 | 91.1102 | 231.4073 | NO | 24 | 0 | 132.2689 | 324.2771 | NO
[11 empty] | 2021-11-15 | 75.82% | 7.334% | 13.96% | 2.882% | 0% | 24 | 0 | 1.2686 | 15.5264 | NO | 24 | 0 | 63.1675 | 230.8949 | NO | 24 | 0 | 84.3671 | 323.6566 | NO
[11 empty] | 2021-11-16 | 73.88% | 10.97% | 12.14% | 3.01% | 0% | 24 | 0 | 1.27 | 15.9147 | NO | 24 | 0 | 89.8671 | 238.7011 | NO | 24 | 0 | 130.1378 | 323.3433 | NO
[11 empty] | 2021-11-17 | 76.76% | 7.942% | 11.36% | 3.941% | 0% | 24 | 0 | 1.4019 | 15.0349 | NO | 24 | 0 | 56.8553 | 230.2327 | NO | 24 | 0 | 73.5462 | 321.3711 | NO
[11 empty] | 2021-11-18 | 63.94% | 13.7% | 12.64% | 9.712% | 0% | 24 | 0 | 1.556 | 16.1645 | NO | 24 | 0 | 136.4954 | 232.6863 | NO | 24 | 0 | 210.0722 | 307.8535 | NO
[11 empty] | 2021-11-19 | 68.71% | 9.055% | 19.7% | 2.536% | 0% | 24 | 0 | 1.2781 | 17.1876 | NO | 24 | 0 | 69.6192 | 235.404 | NO | 24 | 0 | 95.4272 | 324.4341 | NO
[11 empty] | 2021-11-20 | 69.18% | 8.35% | 18.96% | 3.505% | 0% | 24 | 0 | 1.5024 | 16.8184 | NO | 24 | 0 | 76.5521 | 231.9752 | NO | 24 | 0 | 107.3122 | 322.3038 | NO
[11 empty] | 2021-11-21 | 67.67% | 8.652% | 17.59% | 6.086% | 0% | 24 | 0 | 1.6663 | 16.4639 | NO | 24 | 0 | 69.254 | 228.1057 | NO | 24 | 0 | 94.8011 | 316.8098 | NO
[11 empty] | 2021-11-22 | 69.86% | 8.133% | 18.35% | 3.659% | 0% | 24 | 0 | 1.5437 | 16.6237 | NO | 24 | 0 | 83.057 | 231.2956 | NO | 24 | 0 | 118.4634 | 321.943 | NO
[11 empty] | 2021-11-23 | 68.08% | 7.239% | 20.39% | 4.289% | 0.001201% | 24 | 0 | 1.6429 | 16.8421 | NO | 24 | 0 | 49.0573 | 228.1104 | NO | 24 | 0 | 60.1782 | 320.5511 | NO
[11 empty] | 2021-11-24 | 71.27% | 9.677% | 15.55% | 3.503% | 0% | 24 | 0 | 1.4772 | 16.3556 | NO | 24 | 0 | 92.0804 | 235.0382 | NO | 24 | 0 | 133.932 | 322.2723 | NO
[11 empty] | 2021-11-25 | 62.58% | 12.23% | 16.08% | 9.109% | 0% | 24 | 3 | 1.5232 | 16.6898 | NO | 24 | 3 | 100.2077 | 230.3997 | NO | 24 | 3 | 147.8646 | 309.6654 | NO
[11 empty] | 2021-11-26 | 67.27% | 7.738% | 11.74% | 13.25% | 0% | 24 | 0 | 1.5714 | 14.5988 | NO | 24 | 0 | 64.9121 | 213.2181 | NO | 24 | 0 | 87.3579 | 301.18 | NO
[11 empty] | 2021-11-27 | 53.7% | 16.17% | 12.79% | 15.63% | 1.712% | 24 | 8 | 2.1099 | 16.7298 | NO | 23 | 8 | 113.4107 | 228.8095 | NO | 24 | 8 | 170.4983 | 293.2024 | NO
[11 empty] | 2021-11-28 | 71.13% | 10.38% | 15.37% | 3.126% | 0% | 24 | 0 | 1.5132 | 16.493 | NO | 24 | 0 | 58.3259 | 237.2173 | NO | 24 | 0 | 76.0673 | 323.1302 | NO
[11 empty] | 2021-11-29 | 72.04% | 7.333% | 14.91% | 5.719% | 0% | 24 | 0 | 1.5543 | 15.6001 | NO | 24 | 0 | 61.0604 | 225.9203 | NO | 24 | 0 | 80.755 | 317.5884 | NO
[11 empty] | 2021-11-30 | 66.37% | 11.18% | 13.62% | 8.833% | 0% | 24 | 1 | 1.3949 | 15.9336 | NO | 24 | 1 | 88.9635 | 228.5364 | NO | 24 | 1 | 128.5889 | 310.2725 | NO
[11 empty] | 2021-12-01 | 63.67% | 14.45% | 9.957% | 11.92% | 0% | 24 | 2 | 1.4117 | 15.6909 | NO | 24 | 2 | 75.9773 | 230.107 | NO | 24 | 2 | 91.5114 | 303.5899 | NO
[11 empty] | 2021-12-02 | 64.71% | 19.01% | 7.034% | 9.245% | 0% | 24 | 1 | 1.5782 | 16.1834 | NO | 24 | 1 | 88.0262 | 245.967 | NO | 24 | 1 | 98.8867 | 309.3627 | NO
[11 empty] | 2021-12-03 | 71.58% | 8.144% | 17.68% | 2.596% | 0% | 24 | 0 | 1.4732 | 16.5371 | NO | 24 | 0 | 69.4373 | 233.1864 | NO | 24 | 0 | 62.4137 | 324.2853 | NO
[11 empty] | 2021-12-04 | 74.81% | 7.988% | 14.26% | 2.936% | 0% | 24 | 0 | 1.3175 | 15.7354 | NO | 24 | 0 | 46.7101 | 232.2072 | NO | 24 | 0 | 62.2401 | 323.5503 | NO
[11 empty] | 2021-12-05 | 68.04% | 13.12% | 15.28% | 3.565% | 0% | 24 | 0 | 1.4696 | 17.0505 | NO | 24 | 0 | 78.2189 | 242.4565 | NO | 24 | 0 | 68.5635 | 322.1493 | NO
[11 empty] | 2021-12-06 | 58.25% | 4.533% | 13.32% | 23.44% | 0.4503% | 24 | 4 | 1.4978 | 13.5697 | NO | 24 | 4 | 54.8178 | 185.7219 | NO | 24 | 4 | 78.2534 | 276.822 | NO
[11 empty] | 2021-12-07 | 70.53% | 0.1334% | 13.34% | 16% | 0% | 24 | 1 | 1.4843 | 12.9596 | NO | 24 | 1 | 35.7872 | 190.4352 | NO | 24 | 1 | 47.3856 | 293.8125 | NO
[11 empty] | 2021-12-08 | 67.3% | 0.254% | 13.72% | 18.73% | 0% | 24 | 0 | 1.4225 | 12.8816 | NO | 24 | 0 | 36.6622 | 185.5189 | NO | 24 | 0 | 75.1391 | 287.5014 | NO
[11 empty] | 2021-12-09 | 75.4% | 0.3614% | 10.12% | 14.12% | 0% | 24 | 0 | 1.3468 | 12.533 | NO | 24 | 0 | 49.6277 | 195.1946 | NO | 24 | 0 | 43.0183 | 298.9686 | NO
[11 empty] | 2021-12-10 | 71.22% | 0.4796% | 14.78% | 13.51% | 0% | 24 | 0 | 1.3978 | 13.6125 | NO | 24 | 0 | 39.1095 | 196.5166 | NO | 23 | 0 | 66.9496 | 300.2547 | NO
[11 empty] | 2021-12-11 | 72.94% | 0.6% | 13.42% | 13.04% | 0% | 24 | 0 | 1.2672 | 13.3668 | NO | 24 | 0 | 41.5899 | 197.6563 | NO | 23 | 0 | 52.6515 | 301.3139 | NO
[11 empty] | 2021-12-12 | 68.03% | 2.77% | 15.73% | 13.46% | 0% | 24 | 0 | 1.2939 | 14.3827 | NO | 24 | 0 | 51.5988 | 202.1073 | NO | 24 | 0 | 44.9637 | 300.8032 | NO
[11 empty] | 2021-12-13 | 69% | 2.403% | 12.29% | 16.31% | 0% | 24 | 0 | 1.2809 | 13.3267 | NO | 24 | 0 | 39.8249 | 195.761 | NO | 24 | 0 | 59.1015 | 294.0558 | NO
[11 empty] | 2021-12-14 | 72.33% | 1.537% | 14.7% | 11.44% | 0% | 24 | 0 | 1.3541 | 13.9457 | NO | 24 | 0 | 39.1403 | 202.6232 | NO | 24 | 0 | 67.1697 | 304.8577 | NO
[11 empty] | 2021-12-15 | 59.91% | 9.464% | 12.76% | 17.87% | 0% | 24 | 2 | 1.9413 | 14.8315 | NO | 24 | 2 | 47.736 | 208.7136 | NO | 24 | 2 | 82.8814 | 290.0903 | NO
[11 empty] | 2021-12-16 | 69.96% | 8.806% | 15.28% | 5.952% | 0% | 24 | 0 | 1.3106 | 15.942 | NO | 24 | 0 | 67.6528 | 228.2831 | NO | 24 | 0 | 40.3679 | 316.6704 | NO
[11 empty] | 2021-12-17 | 76.4% | 8.119% | 10.1% | 5.383% | 0% | 24 | 0 | 1.4558 | 14.7236 | NO | 24 | 0 | 44.8554 | 228.1802 | NO | 24 | 0 | 89.0186 | 318.2526 | NO
[11 empty] | 2021-12-18 | 67.12% | 14.59% | 14.96% | 3.327% | 0% | 24 | 0 | 1.413 | 17.3232 | NO | 24 | 0 | 66.8414 | 246.4807 | NO | 24 | 0 | 73.951 | 322.7212 | NO
[11 empty] | 2021-12-19 | 61.97% | 13.92% | 17.34% | 6.77% | 0% | 24 | 3 | 1.7767 | 17.3126 | NO | 24 | 3 | 56.7557 | 238.7995 | NO | 24 | 3 | 128.6867 | 313.5599 | NO
[11 empty] | 2021-12-20 | 51.42% | 16.4% | 9.434% | 21.13% | 1.619% | 24 | 12 | 2.5713 | 15.5583 | NO | 24 | 12 | 66.5196 | 217.9778 | NO | 24 | 12 | 164.7258 | 279.9931 | NO
[11 empty] | 2021-12-21 | 66.14% | 10.26% | 13.13% | 10.47% | 0% | 24 | 2 | 1.8495 | 15.5198 | NO | 24 | 2 | 52.4451 | 223.7286 | NO | 24 | 2 | 59.0719 | 306.5653 | NO
[11 empty] | 2021-12-22 | 64.41% | 10.79% | 15.33% | 9.467% | 0% | 24 | 5 | 1.691 | 16.105 | NO | 24 | 5 | 56.475 | 226.4988 | NO | 24 | 5 | 75.8886 | 308.2064 | NO
[11 empty] | 2021-12-23 | 71.12% | 12.61% | 9.023% | 7.243% | 0% | 24 | 2 | 1.2824 | 15.2827 | NO | 24 | 2 | 54.551 | 234.4547 | NO | 24 | 2 | 162.4655 | 313.4373 | NO
[11 empty] | 2021-12-24 | 74.93% | 9.835% | 12.16% | 3.081% | 0% | 24 | 0 | 1.2168 | 15.67 | NO | 24 | 0 | 59.474 | 236.0481 | NO | 24 | 0 | 57.1909 | 323.2344 | NO
[11 empty] | 2021-12-25 | 75.69% | 11.58% | 6.91% | 5.823% | 0% | 24 | 0 | 1.3113 | 14.7131 | NO | 24 | 0 | 70.2207 | 234.5708 | NO | 24 | 0 | 66.2283 | 316.9223 | NO
[11 empty] | 2021-12-26 | 67.73% | 13.89% | 12.31% | 6.069% | 0% | 24 | 0 | 1.3104 | 16.4045 | NO | 24 | 0 | 85.5876 | 239.1025 | NO | 24 | 0 | 37.3974 | 316.4433 | NO
[11 empty] | 2021-12-27 | 69.85% | 12.75% | 10.64% | 6.765% | 0% | 24 | 0 | 1.2586 | 15.7791 | NO | 24 | 0 | 78.9755 | 235.8164 | NO | 24 | 0 | 79.8539 | 315.1646 | NO
[11 empty] | 2021-12-28 | 65.98% | 10.6% | 17.77% | 5.644% | 0% | 24 | 0 | 1.7391 | 16.8448 | NO | 24 | 0 | 61.4309 | 232.6333 | NO | 24 | 0 | 75.8378 | 316.884 | NO
[11 empty] | 2021-12-29 | 69.55% | 12.28% | 10.3% | 7.875% | 0% | 24 | 2 | 1.4005 | 15.1952 | NO | 24 | 2 | 66.2498 | 230.4295 | NO | 24 | 2 | 75.6771 | 309.9695 | NO
[11 empty] | 2021-12-30 | 75.93% | 8.223% | 14.04% | 1.808% | 0% | 24 | 0 | 1.2809 | 15.7975 | NO | 24 | 0 | 52.0813 | 234.7945 | NO | 24 | 0 | 64.742 | 326.0243 | NO
[11 empty] | 2021-12-31 | 78.2% | 7.786% | 12.58% | 1.435% | 0% | 24 | 0 | 1.1695 | 15.3783 | NO | 24 | 0 | 37.1714 | 235.3297 | NO | 24 | 0 | 98.2477 | 326.6528 | NO

## A52B Boiler 7
|  | Concentrations in mg/m³ at reference conditions after subtracting uncertainty | [9 empty] | Daily means, excluding hours outside normal operating conditions
|  | 2021-10-01 |  |  | 2021-11-01 |  |  | 2021-12-01 |  |  | Date | Fuel mix |  |  |  |  | Particulate Matter concentration (mg/m³) after subtracting uncertainty |  |  |  |  | Sulphur dioxide concentration (mg/m³) after subtracting uncertainty |  |  |  |  | Oxides of nitrogen concentration (mg/m³) after subtracting uncertainty
|  | PM | SO2 | NOx | PM | SO2 | NOx | PM | SO2 | NOx |  | % BFG | % COG | % BOSg | % NG | % HFO | No.valid hours | No.hours OTNOC | Measured | Limit | Breach? | No.valid hours | No.hours OTNOC | Measured | Limit | Breach? | No.valid hours | No.hours OTNOC | Measured | Limit | Breach?
Daily means | Minimum | Not operating as per Derogation and as discussed with NRW |  |  | 0.78923 | 9.1425 | 32.7136 | 7.7144 | 6.7333 | 54.782 | 2021-10-01
| Maximum |  |  |  | 9.4493 | 25.8146 | 109.9414 | 10.1572 | 31.4797 | 142.8336 | 2021-10-02
| No. > Limit |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2021-10-03
Monthly mean |  |  |  |  | 5.9074 | 18.6898 | 72.7472 | 9.0276 | 19.2593 | 93.0674 | 2021-10-04
Monthly mean limit |  |  |  |  | 15.1792 | 217.5941 | 293.9774 | 14.405 | 211.4097 | 291.2887 | 2021-10-05
2021-10-06
2021-10-07
2021-10-08
2021-10-09
2021-10-10
2021-10-11
2021-10-12
2021-10-13
2021-10-14
2021-10-15
2021-10-16
2021-10-17
2021-10-18
2021-10-19
2021-10-20
2021-10-21
2021-10-22
2021-10-23
2021-10-24
2021-10-25
2021-10-26
2021-10-27
2021-10-28
2021-10-29
2021-10-30
2021-10-31
[11 empty] | 2021-11-01 | 49.51% | 11.24% | 2.304% | 23.6% | 13.35% | 24 | 12 | 0.88873 | 15.1898 | NO | 0 | 12 |  | 211.6121 | NO | 0 | 12 |  | 266.2686 | NO
[11 empty] | 2021-11-02 | 67.97% | 6.851% | 7.33% | 17.85% | 0% | 24 | 0 | 1.0557 | 13.3633 | NO | 0 | 0 |  | 208.814 | NO | 0 | 0 |  | 298.8218 | NO
[11 empty] | 2021-11-03 | 70.73% | 11.22% | 12.46% | 5.581% | 0% | 24 | 0 | 1.011 | 15.8889 | NO | 8 | 0 | 9.1425 | 241.3472 | NO | 8 | 0 | 32.7136 | 328.0591 | NO
[11 empty] | 2021-11-04 | 75.51% | 11.69% | 8.631% | 4.167% | 0% | 24 | 0 | 1.107 | 14.9977 | NO | 24 | 0 | 9.9093 | 243.6188 | NO | 24 | 0 | 41.1702 | 329.0087 | NO
[11 empty] | 2021-11-05 | 79.02% | 11.59% | 7.697% | 1.691% | 0% | 24 | 0 | 1.0518 | 14.9485 | NO | 24 | 0 | 17.0273 | 247.7385 | NO | 24 | 0 | 50.1177 | 334.1712 | NO
[11 empty] | 2021-11-06 | 74.75% | 9.235% | 14.3% | 1.722% | 0% | 24 | 0 | 0.78923 | 16.1097 | NO | 24 | 0 | 14.2454 | 243.9491 | NO | 24 | 0 | 38.7737 | 336.228 | NO
[11 empty] | 2021-11-07 | 67.28% | 8.044% | 21.57% | 3.106% | 0% | 24 | 0 | 0.92275 | 17.7407 | NO | 24 | 0 | 13.5715 | 239.7262 | NO | 24 | 0 | 46.2263 | 334.6235 | NO
[11 empty] | 2021-11-08 | 55.92% | 17.84% | 10.46% | 15.78% | 0% | 24 | 7 | 0.98372 | 16.8365 | NO | 24 | 7 | 14.1356 | 236.0799 | NO | 24 | 7 | 81.2399 | 302.4615 | NO
[11 empty] | 2021-11-09 | 64.02% | 19.01% | 6.277% | 10.69% | 0% | 24 | 1 | 1.3998 | 16.7058 | NO | 24 | 1 | 25.8146 | 247.9103 | NO | 24 | 1 | 84.6247 | 314.7491 | NO
[11 empty] | 2021-11-10 | 66.61% | 17.4% | 7.934% | 8.058% | 0% | 24 | 3 | 4.0728 | 16.1638 | NO | 24 | 3 | 23.3037 | 249.3339 | NO | 24 | 3 | 74.1729 | 320.8743 | NO
[11 empty] | 2021-11-11 | 71.53% | 11.99% | 13.29% | 3.182% | 0% | 24 | 0 | 8.7492 | 16.8557 | NO | 24 | 0 | 19.7719 | 247.7951 | NO | 24 | 0 | 60.3169 | 333.7594 | NO
[11 empty] | 2021-11-12 | 64.96% | 13.53% | 14.29% | 7.225% | 0% | 24 | 4 | 8.8767 | 17.2031 | NO | 24 | 4 | 15.7579 | 243.9645 | NO | 24 | 4 | 56.7944 | 324.9308 | NO
[11 empty] | 2021-11-13 | 79.84% | 10.1% | 9.163% | 0.8902% | 0% | 24 | 0 | 8.9224 | 15.3961 | NO | 24 | 0 | 21.9419 | 246.4275 | NO | 24 | 0 | 50.5059 | 336.7486 | NO
[11 empty] | 2021-11-14 | 73.37% | 9.283% | 15.17% | 2.174% | 0% | 24 | 0 | 8.4054 | 16.5309 | NO | 24 | 0 | 20.9509 | 243.5827 | NO | 24 | 0 | 54.4751 | 335.8715 | NO
[11 empty] | 2021-11-15 | 77.43% | 7.983% | 11.13% | 3.457% | 0% | 24 | 0 | 7.7655 | 15.5264 | NO | 24 | 0 | 16.8894 | 237.5421 | NO | 24 | 0 | 50.5537 | 331.7722 | NO
[11 empty] | 2021-11-16 | 75.04% | 12.75% | 9.453% | 2.757% | 0% | 24 | 0 | 8.3298 | 15.9147 | NO | 24 | 0 | 22.532 | 249.0763 | NO | 24 | 0 | 55.2301 | 332.7779 | NO
[11 empty] | 2021-11-17 | 80.42% | 9.399% | 9.165% | 1.017% | 0% | 24 | 0 | 7.1649 | 15.0349 | NO | 24 | 0 | 20.2077 | 244.4935 | NO | 24 | 0 | 68.2396 | 336.3536 | NO
[11 empty] | 2021-11-18 | 53.36% | 13.92% | 20.28% | 12.44% | 0% | 24 | 2 | 9.4493 | 16.1645 | NO | 24 | 2 | 20.4212 | 213.607 | NO | 24 | 2 | 109.9414 | 278.2836 | NO
[11 empty] | 2021-11-19 | 71.63% | 10.47% | 16.25% | 1.646% | 0% | 24 | 0 | 8.4572 | 17.1876 | NO | 24 | 0 | 21.9566 | 247.875 | NO | 24 | 0 | 86.6997 | 338.1181 | NO
[11 empty] | 2021-11-20 | 71.45% | 9.882% | 15.5% | 3.167% | 0% | 24 | 0 | 8.0957 | 16.8184 | NO | 24 | 0 | 23.8088 | 243.4008 | NO | 24 | 0 | 87.2784 | 334.1801 | NO
[11 empty] | 2021-11-21 | 72.28% | 8.477% | 14.58% | 4.66% | 0% | 24 | 0 | 8.3357 | 16.4639 | NO | 24 | 0 | 17.2266 | 238.2239 | NO | 24 | 0 | 84.6067 | 331.7378 | NO
[11 empty] | 2021-11-22 | 72.67% | 9.821% | 15.05% | 2.462% | 0% | 24 | 0 | 8.7673 | 16.6237 | NO | 24 | 0 | 18.3321 | 244.6841 | NO | 24 | 0 | 89.661 | 335.8468 | NO
[11 empty] | 2021-11-23 | 70.24% | 9.045% | 16.8% | 3.913% | 0% | 24 | 0 | 8.2297 | 16.8421 | NO | 24 | 0 | 16.5922 | 240.6128 | NO | 24 | 0 | 73.8838 | 333.1331 | NO
[11 empty] | 2021-11-24 | 74.3% | 10.73% | 12.66% | 2.315% | 0% | 24 | 0 | 8.6633 | 16.3556 | NO | 24 | 0 | 21.5248 | 246.5216 | NO | 24 | 0 | 87.6274 | 335.3969 | NO
[11 empty] | 2021-11-25 | 65.73% | 12.2% | 14.03% | 8.04% | 0% | 24 | 2 | 7.8842 | 16.6898 | NO | 24 | 2 | 19.6726 | 238.1412 | NO | 24 | 2 | 99.5308 | 320.5617 | NO
[11 empty] | 2021-11-26 | 68.12% | 9.927% | 10.1% | 11.86% | 0% | 24 | 1 | 7.6027 | 14.5988 | NO | 24 | 1 | 15.1109 | 223.7832 | NO | 24 | 1 | 83.7281 | 308.9624 | NO
[11 empty] | 2021-11-27 | 55.71% | 16.39% | 11.56% | 16.33% | 0% | 24 | 7 | 7.1803 | 16.7298 | NO | 24 | 7 | 19.0739 | 229.6763 | NO | 24 | 7 | 101.0925 | 298.128 | NO
[11 empty] | 2021-11-28 | 73.36% | 12.25% | 13.38% | 1.012% | 0% | 24 | 0 | 7.1215 | 16.493 | NO | 24 | 0 | 19.1003 | 250.2182 | NO | 24 | 0 | 82.7879 | 335.3134 | NO
[11 empty] | 2021-11-29 | 73.36% | 10.43% | 12.88% | 3.333% | 0% | 24 | 0 | 8.3622 | 15.6001 | NO | 24 | 0 | 19.3786 | 241.8087 | NO | 24 | 0 | 82.1733 | 329.8928 | NO
[11 empty] | 2021-11-30 | 71.17% | 11.32% | 11.37% | 6.139% | 0% | 24 | 0 | 7.8712 | 15.9336 | NO | 24 | 0 | 19.2957 | 239.0415 | NO | 24 | 0 | 97.4992 | 324.2207 | NO
[11 empty] | 2021-12-01 | 73.68% | 12.14% | 8.599% | 5.587% | 0% | 24 | 0 | 9.0413 | 15.6909 | NO | 24 | 0 | 21.1467 | 242.6987 | NO | 24 | 0 | 92.4128 | 326.5016 | NO
[11 empty] | 2021-12-02 | 70.26% | 16.61% | 5.442% | 7.683% | 0% | 24 | 0 | 8.4375 | 16.1834 | NO | 24 | 0 | 22.7755 | 246.9491 | NO | 24 | 0 | 111.3061 | 319.2008 | NO
[11 empty] | 2021-12-03 | 74.96% | 8.956% | 15.63% | 0.4582% | 0% | 24 | 0 | 7.7144 | 16.5371 | NO | 24 | 0 | 21.044 | 244.4973 | NO | 24 | 0 | 81.6867 | 337.442 | NO
[11 empty] | 2021-12-04 | 76.87% | 9.779% | 12.19% | 1.166% | 0% | 24 | 0 | 9.2822 | 15.7354 | NO | 24 | 0 | 19.6479 | 244.4651 | NO | 24 | 0 | 80.6632 | 335.1058 | NO
[11 empty] | 2021-12-05 | 71.62% | 13.52% | 13.19% | 1.669% | 0% | 24 | 0 | 9.2715 | 17.0505 | NO | 24 | 0 | 24.3957 | 252.5932 | NO | 24 | 0 | 91.5647 | 335.1009 | NO
[11 empty] | 2021-12-06 | 63.7% | 5.116% | 12.34% | 18.84% | 0% | 24 | 1 | 9.05 | 13.5697 | NO | 24 | 1 | 6.7333 | 199.5491 | NO | 24 | 1 | 85.9554 | 293.9828 | NO
[11 empty] | 2021-12-07 | 74.41% | 0.6397% | 12.16% | 12.8% | 0% | 24 | 0 | 8.0277 | 12.9596 | NO | 24 | 0 | 13.7521 | 201.4123 | NO | 24 | 0 | 54.782 | 306.7893 | NO
[11 empty] | 2021-12-08 | 73.46% | 1.307% | 11.82% | 13.41% | 0% | 24 | 0 | 9.3181 | 12.8816 | NO | 24 | 0 | 9.419 | 203.6578 | NO | 24 | 0 | 67.3259 | 308.0535 | NO
[11 empty] | 2021-12-09 | 76.91% | 2.322% | 8.138% | 12.63% | 0% | 24 | 0 | 9.7049 | 12.533 | NO | 24 | 0 | 10.5862 | 206.658 | NO | 24 | 0 | 77.3433 | 308.9448 | NO
[11 empty] | 2021-12-10 | 72.37% | 3.428% | 12.17% | 12.03% | 0% | 24 | 0 | 8.9331 | 13.6125 | NO | 24 | 0 | 10.6039 | 211.3141 | NO | 24 | 0 | 75.4669 | 311.9599 | NO
[11 empty] | 2021-12-11 | 73.95% | 4.556% | 10.81% | 10.68% | 0% | 24 | 0 | 9.3932 | 13.3668 | NO | 24 | 0 | 12.2984 | 216.1695 | NO | 24 | 0 | 72.6153 | 314.7831 | NO
[11 empty] | 2021-12-12 | 67.8% | 5.92% | 12.78% | 13.5% | 0% | 24 | 0 | 10.0909 | 14.3827 | NO | 24 | 0 | 15.9028 | 214.5962 | NO | 24 | 0 | 77.3072 | 309.3392 | NO
[11 empty] | 2021-12-13 | 71.35% | 1.777% | 10.35% | 16.52% | 0% | 24 | 0 | 9.1642 | 13.3267 | NO | 24 | 0 | 15.8701 | 198.4712 | NO | 24 | 0 | 86.6398 | 300.5668 | NO
[11 empty] | 2021-12-14 | 76.5% | 0.7038% | 12.83% | 9.959% | 0% | 24 | 0 | 8.7309 | 13.9457 | NO | 24 | 0 | 14.4397 | 208.7211 | NO | 24 | 0 | 84.9354 | 315.9598 | NO
[11 empty] | 2021-12-15 | 62.47% | 8.414% | 10.9% | 18.21% | 0% | 24 | 2 | 8.993 | 14.8315 | NO | 24 | 2 | 12.6977 | 209.5971 | NO | 24 | 2 | 102.4553 | 295.63 | NO
[11 empty] | 2021-12-16 | 71.38% | 9.719% | 12.84% | 6.068% | 0% | 24 | 0 | 7.9662 | 15.942 | NO | 24 | 0 | 22.1909 | 235.0108 | NO | 24 | 0 | 82.9779 | 324.3951 | NO
[11 empty] | 2021-12-17 | 77.53% | 10.91% | 7.755% | 3.802% | 0% | 24 | 0 | 9.8074 | 14.7236 | NO | 24 | 0 | 20.4114 | 242.286 | NO | 24 | 0 | 87.7123 | 329.4069 | NO
[11 empty] | 2021-12-18 | 71.94% | 13.35% | 12.2% | 2.51% | 0% | 24 | 0 | 8.3046 | 17.3232 | NO | 24 | 0 | 20.113 | 252.5113 | NO | 24 | 0 | 89.0936 | 335.7978 | NO
[11 empty] | 2021-12-19 | 63.31% | 16.16% | 14.05% | 6.487% | 0% | 24 | 2 | 9.3881 | 17.3126 | NO | 24 | 2 | 16.1093 | 251.1313 | NO | 24 | 2 | 107.0191 | 324.3886 | NO
[11 empty] | 2021-12-20 | 52.73% | 19.61% | 7.174% | 18.04% | 2.448% | 24 | 12 | 9.7779 | 15.5583 | NO | 24 | 12 | 12.4429 | 235.9625 | NO | 24 | 12 | 142.8336 | 292.945 | NO
[11 empty] | 2021-12-21 | 68.38% | 11.09% | 10.85% | 9.681% | 0% | 24 | 2 | 7.9103 | 15.5198 | NO | 24 | 2 | 20.5042 | 232.3144 | NO | 24 | 2 | 87.0522 | 316.5042 | NO
[11 empty] | 2021-12-22 | 67.92% | 12.13% | 12.56% | 7.381% | 0% | 24 | 4 | 8.2392 | 16.105 | NO | 24 | 4 | 19.8029 | 239.9251 | NO | 24 | 4 | 94.2099 | 323.0134 | NO
[11 empty] | 2021-12-23 | 73.53% | 13.05% | 6.928% | 6.492% | 0% | 24 | 2 | 9.1164 | 15.2827 | NO | 24 | 2 | 20.5196 | 241.6583 | NO | 24 | 2 | 115.2597 | 322.5973 | NO
[11 empty] | 2021-12-24 | 77.25% | 10.7% | 9.657% | 2.398% | 0% | 24 | 0 | 8.5315 | 15.67 | NO | 24 | 0 | 26.5311 | 244.9545 | NO | 24 | 0 | 104.4379 | 333.4791 | NO
[11 empty] | 2021-12-25 | 73.7% | 15.27% | 4.98% | 6.045% | 0% | 24 | 0 | 9.3358 | 14.7131 | NO | 24 | 0 | 29.4639 | 246.6953 | NO | 24 | 0 | 110.2822 | 322.8361 | NO
[11 empty] | 2021-12-26 | 70.56% | 14.61% | 9.665% | 5.163% | 0% | 24 | 0 | 9.6415 | 16.4045 | NO | 24 | 0 | 31.4797 | 248.7488 | NO | 24 | 0 | 98.5924 | 327.9438 | NO
[11 empty] | 2021-12-27 | 73.65% | 14.2% | 8.06% | 4.094% | 0% | 24 | 0 | 9.2137 | 15.7791 | NO | 24 | 0 | 27.532 | 250.2683 | NO | 24 | 0 | 100.4305 | 330.7131 | NO
[11 empty] | 2021-12-28 | 70.06% | 12.29% | 14.76% | 2.89% | 0% | 24 | 0 | 8.4232 | 16.8448 | NO | 24 | 0 | 21.5071 | 248.387 | NO | 24 | 0 | 96.6767 | 333.8361 | NO
[11 empty] | 2021-12-29 | 67.98% | 16.54% | 8.49% | 6.998% | 0% | 24 | 5 | 9.325 | 15.1952 | NO | 24 | 5 | 31.0934 | 247.4363 | NO | 24 | 5 | 117.6392 | 319.3469 | NO
[11 empty] | 2021-12-30 | 78.24% | 9.749% | 11.39% | 0.623% | 0% | 24 | 0 | 10.1572 | 15.7975 | NO | 24 | 0 | 23.5623 | 246.5504 | NO | 24 | 0 | 105.9315 | 338.0277 | NO
[11 empty] | 2021-12-31 | 81.7% | 8.166% | 9.788% | 0.3446% | 0% | 24 | 0 | 9.5662 | 15.3783 | NO | 24 | 0 | 22.4609 | 243.8822 | NO | 24 | 0 | 102.4801 | 338.3518 | NO