| Permit Number: | BP0044402 (PAN-004245) |
| --- | --- |
| Applicant name: | Dŵr Cymru Welsh Water (DCWW) |
| Site Address: | Crymych WwTW, Crymych, Pembrokeshire, SA41 3QX |
| Discharge Point NGR: | SN 18370 34760 |
| Respond by date: | 22/02/2019 (10 working days) |
| Permitting Officer: | Jason Copsey |

Brief Description of proposal:

DCWW have applied to vary the discharge permit for Crymych WwTW Storm Discharge as the WwTW has been given an ND1 driver – scheme to meet the requirements of the Water Framework Directive (WFD) No Deterioration for Ammonia. The scheme proposed to meet this driver includes a new inlet works and treatment process which will provide an increase in the Pass Forward Flow (PFF) from 12.19 litres per second (l/s) to 12.37 l/s which is 6xDWF. Since the works will treat flows to 6xDWF, it is proposed that the existing storm tanks are abandoned and the screened storm overflow will discharge directly to the watercourse. A storm spills assessment has been undertaken to assess the impact of this proposal which can be found in the solutions document supplied as part of the application here on the DMS. An application to vary the Crymych WwTW Final Effluent discharge permit BP0044401 as part of this scheme was issued on 25/04/2018.

Habitats Screening Report – Designations or protected species/habitats:

The habitats screening report can be found on the DMS here.

There are no protected species or habitats within screening distance of the discharge.

There are several SSSI’s and SAC’s within a 10km screening distance of the discharge.

As there is no hydrological connectivity between the storm discharge from Crymych WwTW and the designated sites picked up in the Habitats Screening Report a HRA Form 1 or Appendix 4 will not be completed for this application.

Risk Assessment Results (modelling or L1 Risk Assessment):

A spill analysis summary can be found on Page 7 of the Solutions Document found on the DMS here.

Miscellaneous:

NRM Responses:

Environment Management comments:

Officers name: 
Date:

Biodiversity comments:

N/A

Officers name:
Date:

Fisheries comments:

N/A

Officers name:
Date:

Conservation/Ecology Comments:

Officers name:
Date:

Internal Consultation Responses from other NRW Teams:

Water Quality Planning:

N/A

Officers name:

Date:

Geoscience Response:

N/A

Officers name:
Date:

Flood Risk Management:

N/A

Officers name:
Date:

| External Consultations sent to: | Yes/No |
| --- | --- |
| National Parks | No |
| Water Company regarding Drinking Water Protected Zone / SPZ1 | No |
| Environmental Heath | No |

Any Permitting Responses:

Date: