## READ ME
Special Area of Conservation Permit Review - Water Discharge Activities (DCWW) - Regulation 61 Notice Response Tool
This Excel file has been put together to enable DCWW to provide a structured response to the Regulation 61 Notice for the Special Area of Conservation Permit Review.
All of the information in the 'Reg61 Response Sheet' must be completed for each asset to enable NRW to complete the Regulator Initiated Variations, use the information below to complete the sheet:
Explanation & Key Information (Reg61 Response Sheet):
  Colour Key (Row 2):
- Headings in Blue contain identification information (e.g. Permit number) or miscellaneous information that shows where further information is required (e.g. other relevant NEP Drivers to be included in variation)
- Headings in Green contain information on the permit (e.g. Permitted DWF, weir setting)
- Headings in Yellow contain information required to be provided to complete the review or allow the permit to be drafted (e.g. new P limit, site plan)
  Discharge Type:
- Columns A-V are relevant to the Final Effluent permit
- Columns W-AE are relevant to the Storm permit
- Columns AF-AJ are relevant to the Emergency permit
- Storm and Emergency information should only be complete if the permits are to be consolidated into the Final Effluent permit, if there is not a Storm/Emergency discharge at the site or if DCWW do not want a permit consolidation the boxes should contain 'N/A'
  Other:
- If there is a consolidation, new Site Plans (Column Q) and Bespoke Conditions (Column R) should consider this and include the relevant information
- If another document is required (NEP Driver Permit information/New Site Plan), it should be named in the sheet as per the document. The submission format, timing and procedure for supplyingthis information should be agreed with NRW Permitting Service

## Reg61 Response Sheet
Final Effluent Permit | [20 empty] | Storm Permit | [9 empty] | Settled Storm | [9 empty] | UV Treatment |  |  |  |  | Emergency Permit
Site Name | Permit Number | Any other permits to be consolidated into the FE permit? ▪Storm = columns V - AF ▪Settled Storm = columns AG - AP ▪UV Pre and Post Treatment = columns AQ - AU ▪Emergency = columns AV - AZ | Other NEP Driver to be included in variation? | Permitted DWF (m³/d) | FE Permit in EPR Format? | Site address | Receiving Watercourse | FE dicharge point NGR | FE sample point | UWWTD inlet sample point | UWWTD outlet sample point | MCERTS flow meter | Current Permit Limits | Bespoke Conditions Required? ▪Limits of Specified Activity ▪Operating Techniques ▪Pre-Op/Improvement Conditions | New Site Plan Required? | Site Plan File Name (.jpg or .pdf) - to include any consolidated permits | Bespoke Condition File Name (.doc) - to include any consolidated permits | Proposed Total Phosphorus as P Limit | Proposed Total Aluminium as Al Limit | Information for Other NEP Variations? (.doc, .xlsx) | Permit Number | Storm Permit in EPR Format? | Storm sewage discharge point | Storm sewage effluent sample point | Storm sewage discharge EDM (AMP6) NGR | Overflow setting (l/s) or weir height (if reverse flow/both) (Table S3.3) | Storm storage volume (m³) (Table S3.3) | Online or Offline storage? (Table S3.3) | Maximum size of solid matter (Table S3.3) | Screen aperture size (mm) (Table S3.3) | Permit Number | Settled Storm Permit in EPR Format? | Settled Storm sewage discharge point | Settled Storm sewage effluent sample point | Settled Storm sewage discharge EDM (AMP6) NGR | Overflow setting (l/s) or weir height (if reverse flow/both) (Table S3.3) | Settled Storm storage volume (m³) (Table S3.3) | Online or Offline storage? (Table S3.3) | Maximum size of solid matter (Table S3.3) | Screen aperture size (mm) (Table S3.3) | Permit Number | UV Treatment Permit in EPR format | UV effluent discharge point | UV pre-treatment effluent sample point | UV post-treatment effluent sample point | Permit Number | Emergency Permit in EPR Format? | Sewage in emergency discharge point NGR | Sewage in emergency effluent sample point NGR | PKPSM File Name (.doc)
CARROG | CM0000501 | No | No | 49m³/d | Yes | Carrog Wastewater Treatment Works, Carrog, Corwen, LL21 9AU | River Dee | SJ 11740 43710 | SJ 11734 43796 | N/A | N/A | SJ 11734 43796 | LuT (95%ile) Limits: 42mg/l BOD, 47mg/l SS. | N/A | No | N/A | N/A | 5mg/l start date 2030. *Insufficient samples to accept backstop immediately (samples collected by 30/11/23). | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
BRYNEGLWYS | CM0032401 | No | No | 34m³/d | No | Bryneglwys Sewage Treatment Works, Llandegla, Bryneglwys, Wrexham, LL11 3AW | Afon Morwynion | SJ 14265 47265 | SJ 14265 47265 | N/A | N/A | N/A | LuT (95%ile) Limits: 75mg/l BOD, 150mg/l SS, 25mg/l NH3. | N/A | Yes | CM0032401 Site Plan | N/A | 5mg/l start date 2032. *Insufficient samples to accept backstop immediately (samples collected by 30/09/23). | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
FFAIRFACH | BH0065401 | Yes - Settled Storm (BN0194103) | Yes - U_MON3&4 | 847m³/d | No | Ffairfach Wastewater Treatment Works, Ffairfach, Near Llandeilo, Carmarthenshire, SA19 6PE | River Towy | SN 61641 21126 | SN 61717 21104 | SN 61717 21104 | SN 61717 21104 | SN 61717 21105 | LuT (95%ile) Limits: 35mg/l BOD, 55mg/l SS, 10mg/l NH3. Maximum Limits: 70mg/l BOD, 37mg/l NH3. | N/A | Yes | Permits_drawing1__BH0065401 | N/A | 5mg/l start date 2030. | N/A | U_MON3 4 Permitting Information | N/A (See Settled Storm) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | BN0194103 | Yes | SN 61639 21114 | SN 61792 21126 | SN 61792 21126 | 27l/s | 172m³ | Offline | No greater than 6 mm in more than 2 dimension | 6mm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
HENLLAN | BN0013701 | Yes - Storm (DB3297TS) | Yes - U_MON3&4 | 357m³/d | Yes | Henllan Wastewater Treatment Works, Pengallt Industrial Estate, Llandyfriog, Henllan, Ceredigion, SA44 5TE | Afon Teifi | SN 35355 40248 | SN 35402 40277 | N/A | N/A | SN 35399 40294 | LuT (95%ile) Limits: 30mg/l BOD, 45mg/l SS, 20mg/l NH3. | Limits of Specified Activity: Discharge of secondary treated sewage effluent via Outlet 1. The discharge derives from an agglomeration with a population equivalent of less than 2,000, discharging to freshwaters. | No | N/A | N/A | 5mg/l start date 2023. | N/A | U_MON3 4 Permitting Information | DB3297TS | Yes | SN 35355 40248 | SN 35429 40261 | SN 35429 40261 | 14l/s | N/A | N/A | No greater than 6 mm in more than 1 dimension | 6mm x 6mm mesh | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
DEVAUDEN | AA0001901 | No | No | 58m³/d | No | Devauden Sewage Treatment Works, Well Lane, Devauden, Chepstow, NP16 6NX | Tributary Pill Brook | ST 47852 98950 | ST 47969 98975 | N/A | N/A | ST 47967 98976 | LuT (95%ile) Limits: 22mg/l BOD, 60mg/l SS, 12mg/l NH3. | N/A | Yes | AA0001901 Site Plan | N/A | 5mg/l start date 2032. *Insufficient samples to accept backstop immediately (samples collected by 30/11/23). | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
PANDY MONMOUTHSHIRE | AH1002901 | Yes - Settled Storm (AN0391101) & Storm (AB3493FU) | Yes - U_MON3&4 | 176m³/d | No | Pandy Sewage Treatment Works, Pandy, Monmouthshire, NP7 8DR | River Honddu | SO 33518 22842 | SO 33555 22852 | N/A | N/A | SO 33541 22778 | LuT (95%ile) Limits: 40mg/l BOD, 60mg/l SS, 23mg/l NH3. Maximum Limits: 80mg/l BOD, 51mg/l NH3. | N/A | Yes | Permits_drawing_1_AH1002901 | N/A | 5mg/l start date 2030. | N/A | U_MON3 4 Permitting Information | AB3493FU | Yes | SO 33518 22842 | SO 33540 22730 | SO 33540 22730 | 5.4l/s | 50m³ | Offline | No greater than 10 mm in more than 2 dimension | 10mm Bar Screen | AN0391101 | Yes | SO 33518 22842 | SO 33533 22764 | SO 33533 22764 | 5.4l/s | 50m³ | Offline | No greater than 6 mm in more than 1 dimension | 6mm x 6mm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
LLANGURIG | AW1003601 | Yes - Storm & Emergency (AN0087501) | No | 36m³/d | No | Llangurig Sewage Treatment Works, Penybont Farm, A44, Llangurig, Llanidloes, SY18 6SG | River Wye | SN 90837 79668 | SN 90837 79668 | N/A | N/A | N/A | LuT (95%ile) Limits: 27mg/l BOD, 65mg/l SS. | N/A | Yes | AW1003601 Site Plan | N/A | 5mg/l start date 2032. *Insufficient samples to accept backstop immediately (samples collected by 30/09/23). | N/A | N/A | AN0087501 | Yes | SN 90888 79615 | SN 90947 79765 | SN 90947 79765 | 3.33l/s | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | AN0087501 | Yes | SN 90888 79615 | SN 90947 79765 | Not available currently with OPS
NEWBRIDGE-ON-WYE | AW1004401 | Yes - Storm (AB3497FZ) | Yes - U_MON3&4 | 280m³/d | No | Newbridge on Wye Sewage Treatment Works, Newbridge on Wye, Llandrindod Wells, Powys, LD1 6LH | River Wye | SO 01460 58122 | SO 01468 51823 | N/A | N/A | SO 01468 58121 | LuT (95%ile) Limits: 40mg/lg BOD, 60mg/l SS. Maximum Limits: 80mg/l BOD. pH value 6-9 (maximum range). | N/A | Yes | Permits_drawing1__AW1004401 | N/A | 5mg/l start date 2030. *Insufficient samples to accept backstop immediately (samples collected by 31/10/23). | N/A | U_MON3 4 Permitting Information | AB3497FZ | Yes | SO 01470 58120 | SO 01484 58132 | SO 01491 58155 | 12.68l/s | N/A | N/A | No greater than 6 mm in more than 1 dimension | 6mm x 6mm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
LLANDEWI YSTRADENNY - not a site we consider for RoP as the DWF is below 20m³/d | AW1002801 | No | No | 19.6m³/d | No | Llandewi Ystradenny Sewage Treatment Works, Llandewi Ystradenny, Powys | River Ithon | SO 10550 68171 | SO 10680 68250 | N/A | N/A | N/A | N/A - Descriptive. | N/A | N/A | N/A | N/A | No requirement | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
SENNYBRIDGE ARMY CAMP | AC0140301 | Yes - Storm (AN0246901) | Yes - U_MON3&4 | 451m³/d | No | Sennybridge Wastewater Treatment Works, Sennybridge Army Camp, Sennybridge, Brecon, LD3 8TS | River Usk | SN 92530 29450 | SN 92472 29482 | N/A | N/A | SN9247229442, SN9246229443 & SN9248929433 | LuT (95%ile) Limits: 40mg/l BOD, 60mg/l SS, 10mg/l NH3. pH value 6-9 (maximum range). | N/A | Yes | Permits_drawing_1_AC0140301 | N/A | 3.5mg/l start date 2030. | N/A | U_MON3 4 Permitting Information | AN0246901 | Yes | SN 92504 29398 | SN 92460 29406 | SN 92460 29406 | 12l/s | N/A | N/A | No greater than 6 mm in more than 1 dimension | 6mm COPA | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
CLYRO | AW1000901 | No | No | 33.6m³/d | Yes | Clyro Wastewater Treatment Works, Buttercup Meadow, Clyro, Hay-on-Wye, Powys, HR3 5JZ | Clyro Brook | SO 21702 43836 | SO 21635 43825 | N/A | N/A | SO 21650 43840 | LuT (95%ile) Limits: 38mg/l BOD, 60mg/l SS, 25mg/l NH3. | N/A | No | N/A | N/A | 5mg/l start date 2035. *Insufficient samples to accept backstop immediately (samples collected by 31/03/24). | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
CYNWYD | CM0149301 | Yes - Storm (CM0149302) | Yes - U_MON3&4 | 98.8m³/d | No | Cynwyd Sewage Treatment Works, Station Yard, Cynwyd, Corwen, LL21 0HY. | River Dee | SJ 05280 41130 | SJ 05330 41050 | N/A | N/A | SJ 05342 41066 | LuT (95%ile) Limits: 150mg/l BOD, 150mg/l SS. | N/A | Yes | Permits_drawing1__CM0149301 | N/A | 5mg/l start date 2032. *Insufficient samples to accept backstop immediately (samples collected by 31/12/23). | N/A | U_MON3 4 Permitting Information | CM0149302 | Yes | SJ 05265 41089 | SJ 05337 41045 | SJ 05337 41045 | 2.9l/s | N/A | N/A | No greater than 10 mm in more than 2 dimension | 10mm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
BEULAH | AW1000501 | No | No | 54m³/d | No | Beulah Sewage Treatment Works, Beulah, Powys, LD5 4UR. | River Cammarch | SN 92221 51039 | SN 92221 51039 | N/A | N/A | SN 92301 51119 | LuT (95%ile) Limits: 40mg/l BOD, 60mg/l SS, 5mg/l NH3. Maximum Limits: 80mg/l BOD, 20mg/l NH3. | N/A | Yes | AW1000501 Site Plan | N/A | 3mg/l start date 2030. | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
LLANYRE | AW1004001 | Yes - Settled Storm (AW1004002) | No | 80m³/d | Yes | Llanyre Wastewater Treatment Works, Off the A4081, Unnamed Rd, Llandrindod Wells, Powys, LD1 6DU. | River Ithon | SO 05260 62340 | SO 05207 62344 | N/A | N/A | SO 05120 62390 | N/A - Descriptive. | N/A | No | N/A | N/A | 5mg/l start date 2032. *Insufficient samples to accept backstop immediately (samples collected by 31/10/23). | N/A | N/A | N/A (See Settled Storm) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | AW1004002 | Yes | SO 05248 62334 | SO 05152 62377 | SO 05152 62377 | 2.8l/s | 25m³ | Offline | No greater than 12 mm in more than 2 dimension | 12mm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
LLECHRYD | BG0024901 | No | No | 138.3m³/d | No | Llechryd Sewage Treatment Works, Llechryd, Cardigan | Afon Teifi | SN 21244 43337 | SN 21244 43337 | N/A | N/A | SN 21173 43640 | LuT (95%ile) Limits: 30mg/l BOD, 40mg/l SS. | N/A | Yes | BG0024901 Site Plan | N/A | 5mg/l start date 2032. *Insufficient samples to accept backstop immediately (samples collected by 30/09/23). | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
LLANSPYDDID | AB0056601 | No | No | 28m³/d | No | Llanspyddid Sewage Treatment Works, Llanspyddid, Brecon, LD3 8PB | River Usk | SO 01086 28287 | SO 01086 28287 | N/A | N/A | N/A | N/A - Descriptive. | N/A | Yes | AB0056601 Site Plan | N/A | 5mg/l start date 2030. *Insufficient samples to accept backstop immediately (samples collected by 31/10/23). | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
LLANDDEW BRECON | AC0140701 | No | No | 21m³/d | No | Llanddew Sewage Treatment Works, Llanddew, Brecon, Powys, LD3 9ST | River Usk | SO 05111 30821 | SO 05124 30824 | N/A | N/A | N/A | LuT (95%ile) Limits: 96mg/l BOD, 150mg/l SS, 50mg/l NH3. | N/A | Yes | AC0140701 Site Plan | N/A | 4mg/l start date 2032. *Insufficient samples to accept backstop immediately (samples collected by 31/05/24). | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
CAIO | BN0042101 | No | No | 21.8m³/d | No | Caio Sewage Treatment Works, Llanwrda, Carmarthenshire | Afon Annell | SN 67469 39692 | SN 67469 39692 | N/A | N/A | N/A | LuT (95%ile) Limits: 20mg/l BOD, 60mg/l SS. | N/A | Yes | BN0042101 Site Plan | N/A | 5mg/l start date 2032. *Insufficient samples to accept backstop immediately (samples collected by 31/03/24). | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A