## READ ME
Special Area of Conservation Permit Review - Water Discharge Activities (DCWW) - Regulation 61 Notice Response Tool
This Excel file has been put together to enable DCWW to provide a structured response to the Regulation 61 Notice for the Special Area of Conservation Permit Review.
All of the information in the 'Reg61 Response Sheet' must be completed for each asset to enable NRW to complete the Regulator Initiated Variations, use the information below to complete the sheet:
Explanation & Key Information (Reg61 Response Sheet):
  Colour Key (Row 2):
- Headings in Blue contain identification information (e.g. Permit number) or miscellaneous information that shows where further information is required (e.g. other relevant NEP Drivers to be included in variation)
- Headings in Green contain information on the permit (e.g. Permitted DWF, weir setting)
- Headings in Yellow contain information required to be provided to complete the review or allow the permit to be drafted (e.g. new P limit, site plan)
  Discharge Type:
- Columns A-V are relevant to the Final Effluent permit
- Columns W-AE are relevant to the Storm permit
- Columns AF-AJ are relevant to the Emergency permit
- Storm and Emergency information should only be complete if the permits are to be consolidated into the Final Effluent permit, if there is not a Storm/Emergency discharge at the site or if DCWW do not want a permit consolidation the boxes should contain 'N/A'
  Other:
- If there is a consolidation, new Site Plans (Column Q) and Bespoke Conditions (Column R) should consider this and include the relevant information
- If another document is required (NEP Driver Permit information/New Site Plan), it should be named in the sheet as per the document. The submission format, timing and procedure for supplyingthis information should be agreed with NRW Permitting Service

## Reg61 Response Sheet
Final Effluent Permit | [20 empty] | Storm Permit | [9 empty] | Settled Storm | [9 empty] | UV Treatment |  |  |  |  | Emergency Permit
Site Name | Permit Number | Any other permits to be consolidated into the FE permit? ▪Storm = columns V - AF ▪Settled Storm = columns AG - AP ▪UV Pre and Post Treatment = columns AQ - AU ▪Emergency = columns AV - AZ | Other NEP Driver to be included in variation? | Permitted DWF (m³/d) | FE Permit in EPR Format? | Site address | Receiving Watercourse | FE dicharge point NGR | FE sample point | UWWTD inlet sample point | UWWTD outlet sample point | MCERTS flow meter | Current Permit Limits | Bespoke Conditions Required? ▪Limits of Specified Activity ▪Operating Techniques ▪Pre-Op/Improvement Conditions | New Site Plan Required? | Site Plan File Name (.jpg or .pdf) - to include any consolidated permits | Bespoke Condition File Name (.doc) - to include any consolidated permits | Proposed Total Phosphorus as P Limit | Proposed Total Aluminium as Al Limit | Information for Other NEP Variations? (.doc, .xlsx) | Permit Number | Storm Permit in EPR Format? | Storm sewage discharge point | Storm sewage effluent sample point | Storm sewage discharge EDM (AMP6) NGR | Overflow setting (l/s) or weir height (if reverse flow/both) (Table S3.3) | Storm storage volume (m³) (Table S3.3) | Online or Offline storage? (Table S3.3) | Maximum size of solid matter (Table S3.3) | Screen aperture size (mm) (Table S3.3) | Permit Number | Settled Storm Permit in EPR Format? | Settled Storm sewage discharge point | Settled Storm sewage effluent sample point | Settled Storm sewage discharge EDM (AMP6) NGR | Overflow setting (l/s) or weir height (if reverse flow/both) (Table S3.3) | Settled Storm storage volume (m³) (Table S3.3) | Online or Offline storage? (Table S3.3) | Maximum size of solid matter (Table S3.3) | Screen aperture size (mm) (Table S3.3) | Permit Number | UV Treatment Permit in EPR format | UV effluent discharge point | UV pre-treatment effluent sample point | UV post-treatment effluent sample point | Permit Number | Emergency Permit in EPR Format? | Sewage in emergency discharge point NGR | Sewage in emergency effluent sample point NGR | PSKPM File Name (.doc)
CEFN MAWR | CM0101301 | Yes - Settled Storm (CG0405901) | Yes - UMon3_4 for the SS permit (CG0405901) | 1594 | Yes | Cefn Mawr Wastewater Treatment Works, Heol Berwyn, Cefn Mawr, Wrexham, LL14 3NB | River Dee | SJ 27450 41700 | SJ 27450 41700 | SJ 27714 41645 | SJ 27450 41700 | SJ 27714 41645 | LuT (95%ile) Limits: 40mg/l BOD, 60mg/l SS, 20mg/l NH3. Maximum Limits: 80mg/l BOD, 48mg/l NH3. | N/A | No | N/A | N/A | N/A - 1mg/l - no change in permit already at 1mg/l | N/A | U_MON3_4 Permitting Information | N/A - (See Settled Storm) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | CG0405901 | Yes | SJ 27450 41700 | SJ 27704 41654 | SJ 27704 41654 | 48l/s | 350m³ | Offline | No greater than 6 mm in more than 1 dimension | 6mm x 6mm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
LLANDRINDOD WELLS STW PARK LANE | AW1002901 | Yes - Settled Storm (AN0357501) | Yes - UMon3_4 for the SS permit (AN0357501) | 1790 | Yes | Llandrindod Wells Wastewater Treatment Works Parl Lane, Llandrindod Wells, LD1 5NN | River Ithon | SO 04907 60500 | SO 04926 60496 | SO 05068 60536 | SO 04926 60496 | SO 04926 60496 | LuT (95%ile) Limits: 20mg/l BOD, 30mg/l SS, 7mg/l NH3. Maximum Limits: 56mg/l, 27mg/l NH3. | N/A | No | N/A | N/A | 0.8mg/l start date 31/03/2025 | N/A | U_MON3_4 Permitting Information | N/A - (See Settled Storm) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | AN0357501 | Yes | SO 04908 60457 | SO 04966 60542 | SO 04966 60542 | 55.2l/s | 398m³ | Offline | No greater than 6 mm in more than 1 dimension | 6mm x 6mm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
LLANOVER | AB0043401 | No | Yes - UMon3_4 | 86.6 | No | Llanover STW, Llanover, Abergavenny, NP7 9HY | River Usk | SO 31950 09360 | SO 31950 09360 | N/A | N/A | SO 31479 09145 | LuT (95%ile) Limits: 150mg/l BOD, 150mg/l SS, 50mg/l NH3. pH value 6-9 (maximum range). | N/A | Yes | AB0043401 Site Plan | N/A | 5mg/l start date 31/03/2030. *Insufficient samples to accept backstop immediately (samples collected by October 23) | N/A | U_MON3_4 Permitting Information | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GRESFORD | CM0040601 | No | Yes - UMon3_4 | 3590 | Yes | Gresford Wastewater Treatment Works, Gresford, Wrexham, LL12 0HT | River Alyn | SJ 34880 55780 | SJ 34884 55778 | SJ 34894 55604 | SJ 34884 55778 | SJ 34870 55599 | LuT (95%ile) Limits: 1st April - 30th October - 30mg/l BOD, 45mg/l SS, 7mg/l NH3. Maximum Limits: 64mg/l BOD, 27mg/l NH3. LuT: 31st October - 31st March - 50mg/l BOD, 75mg/l SS, 10mg/l NH3. Maximum Limits: 100mg/l BOD, 37mg/l NH3. No time period SS - 100mg/l. UWWTR: LuT: 25mg/l BOD, Max: 50mg/l BOD. | Operating Techniques - Asset Structural Description (ASD) | No | N/A | Use existing document for Operating Technique ASD. | N/A - 1mg/l - no change in permit already at 1mg/l | N/A | U_MON3_4 Permitting Information | N/A - (See Settled Storm) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | CM0040601 | Yes | SJ 34866 55530 | SJ 34866 55530 | SJ 34889 55577 | 112l/s | 643m³ | Offline | N/A | 12mm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
LLANDYSUL | BG0010201 | No | Yes - UMon3_4 | 689 | Yes | Llandysul Wastewater Treatment Works, Llandysul, Ceredigion, SA44 4RL | River Teifi | SN 41910 40290 | SN 41930 40230 | N/A | N/A | SN 41934 40192 | LuT (95%ile) Limits: 40mg/l BOD, 60mg/l SS. Maximum Limits: 80mg/l BOD. | N/A | No | N/A | N/A | 5mg/l start date 31/03/2027 | N/A | U_MON3_4 Permitting Information | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
TREGARON | BH0057801 | Yes - Settled Storm (BH0057901) | No | 520.4 | No | Tregaron Wastewater Treatment Works, Tregaron, Ceredigion, SY25 6HG | River Teifi | SN 67261 59165 | SN 67283 59277 | N/A | N/A | SN 67335 59325 | LuT (95%ile) Limits: 40mg/l BOD, 60mg/l SS, 5mg/l NH3. | N/A | Yes | Permits_drawing_1_BH0057801 | N/A | 2mg/l start date 31/03/2030 | N/A | No | N/A - (See Settled Storm) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | BH0057901 | Yes | SN 67261 59165 | SN 67335 59312 | SN 67335 59312 | 14 | 54 | Offline | No greater than 6 mm in more than 1 dimension | 6mm x 6mm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
LLANGOLLEN | CM0005401 | No | Yes - UMon3_4 (currently submitted on CM0005501) | 1834 | Yes | Llangollen Wastewater Treatment Works, Trevor Road, Llangollen, LL20 7UH | River Dee | SJ 23422 42348 | SJ 23413 42384 | SJ 23404 42429 | SJ 23413 42384 | SJ 23400 42410 | LuT (95%ile) Limits: 30mg/l BOD, 45mg/l SS, 17mg/l NH3 OR 25mg/l BOD. Maximum Limits: 64mg/l BOD, 90mg/l SS, 46mg/l NH3. pH value 6-9 (maximum range). UWWTR - 50mg/l BOD. | Operating Techniques - Pumping station key protection measures. Limits of Specified Activity - Discharge of sewage in emergency via Storm and EO Discharge Point - An emergency shall be defined as the period when the sewage pumping station is inoperative as a result of one or more of the following, which is not due to the act or default of the operator, its agents, representatives, officers, employees or servants; • electrical power failure; • mechanical breakdown of duty and standby pumps; • rising main failure; • blockage of the downstream sewer. | No | N/A | Use existing document for Operating Technique PS key Protection measures. | N/A - 1mg/l - no change in permit already at 1mg/l | N/A | U_MON3_4 Permitting Information | N/A - (See Settled Storm) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | CM0005401 | Yes | SJ 21847 42014 | SJ 21842 42053 | SJ 21842 42053 | 38.87l/s | 177 | Offline | No greater than 6 mm in more than 1 dimension | 6mm x 6mm | N/A | N/A | N/A | N/A | N/A | CM0005401 | Yes | SJ 21847 42014 | SJ 21842 42053 | Use existing PSKPM
HOPE | CM0075801 | Yes - Storm (MP3323XX) | Yes - UMon3_4 for Storm permit (MP3323XX) | 2237 | Yes | Hope Wastewater Treatment Works, Sarn Lane, Hope, Flintshire, LL12 9AE | River Alyn | SJ 30563 58092 | SJ 30487 58049 | SJ 30432 58041 | SJ 30487 58049 | SJ 30487 58049 | LuT (95%ile) Limits: 16mg/l BOD, 30 mg/l SS, 10mg/l NH3. Maximum Limits: 51mg/l BOD, 37mg/l NH3. UWWTR - 25mg/l BOD & 50mg/l BOD (composite). | N/A | No | N/A | N/A | N/A - 1mg/l - no change in permit already at 1mg/l | N/A | U_MON3_4 Permitting Information | MP3323XX | Yes | SJ 30560 58094 | SJ 30428 58014 | SJ 30428 58014 | 181.2l/s | N/A | N/A | No greater than 6 mm in more than 1 dimension | 6mm x 6mm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
PONTRHYDFENDIGAID | BN0040202 | No | Yes - UMon3_4 | 238.4 | Yes | Pontrhydfendigaid Wastewater Treatment Works, Pontrhydfendigaid, Ceredigion, SY25 6BB | River Teifi | SN 72782 66709 | SN 72788 66741 | N/A | N/A | SN 72779 66749 | LuT (95%ile) Limits: 20mg/l BOD, 30mg/l SS, 20mg/l NH3. | N/A | No | N/A | N/A | 1.8mg/l start date 2032. *Insufficient samples to accept backstop immediately (samples collected by July 23) | N/A | U_MON3_4 Permitting Information | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
TALYBONT | AD0001701 | Yes - Settled Storm (AD0001702) | Yes - UMon3_4 for SS permit (AD0001702) | 89 | No | Talybont Sewage Treatment Works, Talybont, Powys, LD3 7JE | River Caerfnell | SO1206923056 | SO 12043 22829 | N/A | N/A | SO 12044 22834 | LuT (95%ile) Limits: 40mg/l BOD, 60mg/l SS, 5mg/l NH3. Maximum Limits: 80mg/l BOD, 20mg/l NH3. pH value of 9.0 pH units or less than pH value of 6.0 pH units. | N/A | Yes | Permits_drawing_1_AD0001701 | N/A | 1mg/l start date 2030 | N/A | U_MON3_4 Permitting Information | N/A - (See Settled Storm) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | AD0001702 | Yes | SO 11975 22991 | SO 12039 22804 | SO 12039 22804 | 2.6l/s | 26.7m³ | Offline | No greater than 6 mm in more than 1 dimension | 6mm x 6mm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
RHAYADER | AW1005201 | Yes - Settled Storm (AW1005202) & Storm (AB3498CC) | Yes - UMon3_4 for SS permit (AW1005202) | 857 | No | Rhayader Wastewater Treatment Works, Rhayader, Powys, LD6 5BH | River Wye | SN 97830 67290 | SN 97760 67400 | SN 97900 67380 | SN 97760 67400 | SN 97880 67360 | LuT (95%ile) Limits: 40mg/l BOD, 60mg/l SS, 10mg/l NH3. Maximum Limits: 80mg/l BOD, 37mg/l NH3. | N/A | Yes | Permits_drawing_1_AW1005201 | N/A | 3mg/l start date 2025. *Insufficient samples to accept backstop immediately (samples collected by November 23) | N/A | U_MON3_4 Permitting Information | AB3498CC | Yes | SN 97789 67363 | SN 97914 67389 | SN 97914 67389 | 20.79 | N/A | N/A | No greater than 10 mm in more than 2 dimensions | 10mm | AW1005202 | Yes | SN 97870 67270 | SN 97872 67287 | SN 97872 6728 | 30l/s | 218m³ | Offline | No greater than 10 mm in more than 2 dimensions | 10mm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
OVERTON | CM0188601 | Yes - Settled Storm & Storm (CM0188602) | Yes - UMon3_4 for SS permit (CM0188602) | 257.2 | No | Overton Wastewater Treatment Works, land off the A539 (Pen-y-Llan/ High Street), Overton, Wrexham, LL13 0EG | River Dee | SJ 36625 41598 | SJ 37163 41493 | N/A | N/A | SJ 37189 41464 | LuT (95%ile) Limits: 40mg/l BOD, 60mg/l SS, 25mg/l NH3. | Limits of specified activity: Settled & Storm A1 & A2- Storm sewage is only discharged once the storm tank has been fully utilised. | Yes | Permits_drawing_1_CM0188601 | N/A | 5mg/l start date 2032. *Current samples show P concentration cannot meet backstop, investment is required. Cannot accept backstop immediately. | N/A | U_MON3_4 Permitting Information | CM0188602 | Yes | SJ 36625 41598 | SJ 37160 41490 | SJ 37160 41490 | 19l/s | N/A | N/A | No greater than 6 mm in more than 1 dimension | 6mm x 6mm | CM0188602 | Yes | SJ 36625 41598 | SJ 37196 41474 | SJ 37196 41474 | 7.97l/s | 57.4m³ | Offline | No greater than 6 mm in more than 1 dimension | 6mm x 6mm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
LLYSWEN | AW1004201 | Yes - Settled Storm (AN0390301) | Yes - UMon3_4 for SS permit (AN0390301) | 132 | No | Llyswen Sewage Treatment Works, Church Road, Llwyswen, Brecon, LD3 0UU | River Wye | SO 13369 38152 | SO 13557 38135 | N/A | N/A | SO 13565 38121 | LuT (95%ile) Limits: 40mg/l BOD, 60mg/l SS, 30mg/l NH3. Maximum Limits: 80mg/l BOD, 61mg/l NH3. | N/A | Yes | Permits_drawing_1_AW1004201 | N/A | 5mg/l start date 2032. *Insufficient samples to accept backstop immediately (samples collected by November 23) | N/A | U_MON3_4 Permitting Information | N/A - (See Settled Storm) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | AN0390301 | Yes | SO 13369 38152 | SO 13572 38124 | SO 13572 38124 | 4.2l/s | 31m³ | Offline | No greater than 6 mm in more than 1 dimension | 6mm x 6mm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
ABERLLYNFI THREE COCKS | AW1000301 | Yes - Storm & Emergency (AN0364001) | Yes - UMon3_4 for S&E permit (AN0364001) | 66 | No | Aberllynfi/ Three Cocks Sewage Treatment Works, Three Cocks, Brecon, Powys, LD3 0SN | Tregoyd Brook | SO 17310 37860 | SO 17325 37854 | N/A | N/A | SO 17519 37966 | LuT (95%ile) Limits: 94mg/l BOD, 90mg/l SS, 20mg/l NH3. | N/A | Yes | Permits_drawing1__AN0364001 | N/A | 3.5mg/l start date 2030. *Current samples show P concentration cannot meet backstop, investment is required. Cannot accept backstop immediately. | N/A | U_MON3_4 Permitting Information | AN0364001 | No | SO 17927 37873 | SO 17927 37873 | SO 17325 37854 | 7.1l/s | N/A | N/A | No greater than 6 mm in more than 1 dimension | 6mm x 6mm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | AN0364001 | No | SO 17297 37873 | SO 17297 37873 | AN0364001 PSKPM
MAES Y GROES | CM0071201 | No | No | 523 | No | Maes Y Groes Wastewater Treatment Works, Pantymwyn, Mold, CH7 5EP | Afon Alyn | SJ 19190 63490 | SJ 19190 63490 | N/A | N/A | SJ 19164 63478 | LuT (95%ile) Limits: 28mg/l BOD, 43mg/l SS. | N/A | Yes | CM0071201 Site Plan | N/A | 5mg/l start date 2030. *Insufficient samples to accept backstop immediately (samples collected by October 23) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
CROSSGATES | AW1001101 | Yes - Settled Storm (AN0226801) | Yes - UMon3_4 for SS permit (AN0226801) | 245.6 | No | Crossgates Sewage Treatment Works, Plas Y Ffynnon, Cambrian Way, Brecon, Powys, LD3 7HP | River Ithon | SO 08854 64657 | SO 08870 64690 | N/A | N/A | SO 08865 64683 | LuT (95%ile) Limits: 50mg/l BOD, 60mg/l SS. | N/A | Yes | Permits_drawing1__AW1001101 | N/A | 2mg/l start date 2032. *Insufficient samples to accept backstop immediately (samples collected by July 23) | N/A | U_MON3_4 Permitting Information | N/A - (See Settled Storm) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | AN0226801 | Yes | SO 08659 64232 | SO 08870 64690 | SO 08870 64690 | 5.7l/s | 57m³ | Offline | No greater than 6 mm in more than 1 dimension | 6mm x 6mm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
LLANWRTYD WELLS | AW1003901 | Yes - Storm (AW1003902) | Yes - UMon3_4 for S permit (AW1003902) | 382.1 | No | Llanwrtyd Wells Sewage Treatment Works, Llanwrtyd Wells, Powys, | River Irfon | SN 90030 46320 | SN 90030 46320 | N/A | N/A | SN 90016 46312 | LuT (95%ile) Limits: 40mg/l BOD, 60mg/l SS, 15mg/l NH3. Maximum Limits: 80mg/l BOD, 44mg/l NH3. | N/A | Yes | Permits_drawing_1_AW1003901 | N/A | 2mg/l start date 2027. | N/A | U_MON3_4 Permitting Information | AW1003902 | Yes | SN 90030 46320 | SN 89988 46383 | SN 89988 46383 | 9.5l/s | N/A | N/A | No greater than 6 mm in more than 1 dimension | 6mm x 6mm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
FIVE FORDS | CM0077801 | Yes - Settled Storm (CM0005702) | Yes - UMon3_4 for SS permit (CM0005702) | 27720 | Yes | Five Fords Wastewater Treatment Works, Cefn Road, Abenbury, Wrexham, LL13 0PA | River Dee | SJ 40900 47320 | SJ 36372 48297 | SJ 36059 48047 | SJ 36372 48297 | SJ 36372 48297 | LuT (95%ile) Limits: 50mg/l BOD, 60mg/l SS, 10mg/l NH3. Maximum Limits: 100mgl BOD, 100mg/l SS, 37mg/l NH3. UWWTR: 25mg/l BOD. Maximum: 50mg/l BOD. | N/A | No | N/A | N/A | 0.7mg/l start date 2030 | N/A | U_MON3_4 Permitting Information | N/A - (See Settled Storm) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | CM0005702 | Yes | SJ 36180 48340 | SJ 36074 48036 | SJ 36074 48036 | 806l/s | 5800m³ | Offline | No greater than 6 mm in more than 1 dimension | 6mm x 6mm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
PENYBONT NR.LLANDRINDOD WELLS | AN0115601 | No | No | 29 | No | Penybont Sewage Treatment Works, Plas Y Ffynnon, Cambrian Way, Brecon, Powys, LD3 7HP | River Ithon | SO 11630 63840 | SO 11630 63840 | N/A | N/A | N/A | N/A - Descriptive. | N/A | Yes | AN0115601 Site Plan | N/A | 5mg/l start date 2032. *Insufficient samples to accept backstop immediately (samples collected by November 23) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A